## 3rd Floor (2)
PAF AIR WAR COLLEGE, KARACHI | [6 empty] | DATED: 15/09/2022
BILL OF QUANTITIES FOR SUPPLY & INSTALLATION AIR CONDITIONING WORK (3RD FLOOR)
ITEM NO. | DESCRIPTION | QTY | UNIT | Rates |  | Amount |  | Total Amount
|  |  |  | Material | Labour | Material | Labour
AIR CONDITIONING WORK
1 | SUPPLY & INSTALLATION OF FAN COIL UNITS
1.1 | Supply & Installation of Chilled Water Ducted Type Fan Coil Units as per schedule and specification
a | Ducted Fan Coil Unit 2.5 TR | 4 | No |  | 8500 | 0 | 34000 | 34000 |  | 1.3 | 0 | 12350
b | Ducted Fan Coil Unit 2.0 TR | 1 | No |  | 8000 | 0 | 8000 | 8000 |  | 1.3 | 0 | 12350
c | Cassette Fan Coil Unit 1.0 TR | 3 | Nos. |  | 7500 | 0 | 22500 | 22500 |  | 1.3 | 0 | 12350
d | Cassette Fan Coil Unit 1.5 TR | 2 | Nos. |  | 7500 | 0 | 15000 | 15000 |  | 1.3 | 0 | 12350
e | Cassette Fan Coil Unit 1.0 TR | 1 | No |  | 7500 | 0 | 7500 | 7500 |  | 1.3 | 0 | 12350
2 | G.I. Duct & Allied Works
2.1 | Supply, fabrication, and installation of G.I. Duct work using prime quality sheet metal including hanger & supports and all tees, bends, reducers, elbows, turning vanes, and splitter etc. complete as specified in the specifications, shown on the layout drawing and standards drawing. Following Gauge chart shall be followed as per below mentioned sizes: *- Gauge 26 = Duct size upto 12" *- Gauge 24 = Duct size 13" to 30" *- Gauge 22 = Duct size 31" to 60" *- Gauge 20 = Duct size 61" to 90"
a | Supply & Installation of Duct | 18500 | Sq. Ft | 325 | 90 | 6012500 | 1665000 | 7677500 |  | 1.3 | 897 | 234
2.2 | Supply and installation of 1” thick, 24 kg/m3 density Glass Wool Insulation with 8 oz. Canvas cloth wrapping around duct with adhesive. All longitudinal and circumferential joints shall be sealed with 2” wide adhesive tape as specified in the specifications and shown on the drawing.
a | Supply & Isnt: Glass Wool Insulation on Ducts | 18500 | Sq. Ft | 180 | 60 | 3330000 | 1110000 | 4440000 |  | 1.3 | 312 | 148.2
2.3 | Supply & Installation of 1” thick, 24 kg/m3 density Sound Liner in supply ducts up 5’ from fan discharge with 100% surface applied with adhesive and mechanical fastness with washes 1.25 dia on the inner side of the duct at 12” centre to centre complete in all respect as specified in the specifications.
a | Sound Liner | 150 | Sq. Ft | 250 | 40 | 37500 | 6000 | 43500 |  | 1.3 | 616.2 | 78
2.4 | Supply & Installation of Flexible duct connector minimum 3" wide as shown in the drawings and directed by the engineer in charge.
a | Flexible Duct Connector | 50 | RFt | 400 | 60 | 20000 | 3000 | 23000 |  | 1.3 | 2600 | 780
2.5 | Duct Supports (Hanger, steel rods etc.) as per specs | 1 | Job | 225000 | 50000 | 225000 | 50000 | 275000 |  | 1.3 | 390000 | 39000
3 | Air Devices
3.1 | Supply & Installation of opposed blade Volume Control Dampers made from 16 SWG. G.I sheets as specified in the specifications, shown on the drawings.
a | VCDs | 75 | Sq. Ft | 3650 | 900 | 273750 | 67500 | 341250 |  | 1.3 | 8580 | 1872
3.2 | Supply & installation of Supply Air Diffusers / Return Air Grills powder coated complete as specified in the specifications, shown on the drawing.
a | Supply Air Diffusers | 75 | Sq. Ft | 3500 | 900 | 262500 | 67500 | 330000 |  | 1.3 | 9750 | 1560
b | Supply Air Diffusers with Dampers | 60 | Sq. Ft | 3850 | 900 | 231000 | 54000 | 285000 |  | 1.3 | 11050 | 1560
c | Return Air Diffusers / Grills | 125 | Sq. Ft | 3850 | 900 | 481250 | 112500 | 593750 |  | 1.3 | 9100 | 1560
4 | Supply, Installation of Seamless MS SCH 40 Pipes complete in all respect
4.1 | Supply & installing seamless Schedule 40 pipe including all tees, bend, reducers, hangers etc. complete as specified in the specifications and directed by the engineer incharge.
a | 3/4'' Dia | 200 | Rft | 400 | 140 | 80000 | 28000 | 108000 |  | 1.3 | 1040 | 234
b | 1'' Dia | 80 | Rft | 975 | 210 | 78000 | 16800 | 94800 |  | 1.3 | 1560 | 304.2
| 1-1/4'' Dia | 30 | Rft | 1110 | 230 | 33300 | 6900 | 40200 |  | 1.3 | 2080 | 390
c | Pipe Supports | 1 | Lot | 50000 | 10000 | 50000 | 10000 | 60000 |  | 1.3 | 110500 | 13000
5 | Pipe Insulation
5.1 | Supply & installing pre-formed glass wool insulation 64 Kg/m3 density factory applied vapour barrier. Complete and directed by the engineer incharge.
a | 3/4'' Dia | 200 | Rft | 270 | 80 | 54000 | 16000 | 70000 |  | 1.3 | 520 | 195
a | 1'' Dia | 80 | Rft | 460 | 90 | 36800 | 7200 | 44000 |  | 1.3 | 780 | 325
| 1-1/4'' Dia | 30 | Rft | 610 | 90 | 18300 | 2700 | 21000 |  | 1.3 | 1040 | 455
6 | VALVES WITH FITTING AND COMPLETE ACCESSORIES
6.1 | GATE VALVE
a | Gate Valve 3/4''Ø | 18 | NOS | 4100 | 1000 | 73800 | 18000 | 91800 |  | 1.3 | 24050 | 2340
b | Gate Valve 1''Ø | 15 | NOS | 6200 | 1000 | 93000 | 15000 | 108000 |  | 1.3 | 27300 | 3250
6.2 | BALANCING VALVES
a | Balancing Valve 3/4''Ø | 18 | NOS | 9300 | 1000 | 167400 | 18000 | 185400 |  | 1.3 | 16250 | 3120
b | Balancing Valve 1''Ø | 11 | NOS | 13000 | 1000 | 143000 | 11000 | 154000 |  | 1.3 | 18850 | 3900
6.3 | STRAINERS
a | Strainer 3/4' Dia | 6 | NOS | 3600 | 1000 | 21600 | 6000 | 27600 |  | 1.3 | 14950 | 2340
b | Strainer 1'' Dia | 5 | NOS | 5500 | 1000 | 27500 | 5000 | 32500 |  | 1.3 | 17550 | 2600
6.4 | 2-WAY MOTORIZED VALVE (0~100% Modulation)
a | 3/4" | 6 | NOS | 52000 | 3500 | 312000 | 21000 | 333000 |  | 1.3 | 117000 | 7800
b | 1" | 5 | NOS | 65000 | 3500 | 325000 | 17500 | 342500 |  | 1.3 | 143000 | 9750
7 | METER AND GAUGES
a | Temperature Gauge | 22 | NOS | 7500 | 1000 | 165000 | 22000 | 187000 |  | 1.3 | 16380 | 3120
b | Pressure Gauges with Gauge Cock & Outlet | 22 | NOS | 7300 | 1000 | 160600 | 22000 | 182600 |  | 1.3 | 19500 | 3120
8 | Drain Water System
8.1 | Supply, Installation, testing and commissioning of Condensate drain piping UPVC with 1/2" thick armaflex insulation or equivalent
a | 1-1/4" Dia | 350 | RFT | 425 | 60 | 148750 | 21000 | 169750 |  | 1.3 | 325 | 195
b | Drain Pipe Supports | 1 | Lot | 10000 | 50000 | 10000 | 50000 | 60000 |  | 1.3 | 23400 | 5200
9 | Balancing
| Air Balancing of the System with Reports | 1 | Job | 0 | 50000 | 0 | 50000 | 50000 |  | 1.3 | 0 | 84500
10 | Other
10.1 | Digital Decorative Themostate Controller (BMS Interfaceable) | 22 | No | 42000 | 2000 | 924000 | 44000 | 968000 |  | 1.3 | 45500 | 3900
10.2 | Control Wiring from Controller to sensor, motorized valve etc. (10 ~ 20' approximate) | 22 | Job | 5000 | 1500 | 110000 | 33000 | 143000 |  | 1.3 | 32500 | 6500
10.3 | Electrical Connections of Fan Coil Unit | 22 | Job | 6000 | 1000 | 132000 | 22000 | 154000 |  | 1.3 | 0 | 6500
10.4 | Painting of all equipment and piping ,supports etc | 1 | Job | 40000 | 15000 | 40000 | 15000 | 55000 |  | 1.3 | 0 | 97500
10.5 | Dismentling of Installation of Ceiling for Isntallating Duct to new build partition rooms for reception and meetings | 1 | Job | 0 | 75000 | 0 | 75000 | 75000 |  | 1.3 | 0 | 325000
10.6 | Charts & Tags | 1 | Job | 20000 | 5000 | 20000 | 5000 | 25000 |  | 1.3 | 0 | 65000
10.7 | Shop drawings | 1 | Job | 15000 | 5000 | 15000 | 5000 | 20000 |  | 1.3 | 0 | 65000
10.8 | As built Drawings 3 set and soft copy in CD | 1 | Job | 10000 | 7000 | 10000 | 7000 | 17000 |  | 1.3 | 0 | 65000
10.9 | Cost of testing, commissioning, balancing adjusting and handing over of the complete plant | 1 | Job | 0 | 25000 | 0 | 25000 | 25000 |  | 1.3 | 0 | 26000
| TOTAL COST | [6 empty] | 17940150 | 44950000
Note: 1. If required additional work or material except above then it will be charge additionally. 2. Electrical Wiring/DB/MCC is not included in the scope of wrok 3. BMS connectivity and cabling is not included in the scope work 4. Any other item didn't mentioned above will be cahgred additionally 5. Above mentioned quantities may vary as per the approved design of consultant | [8 empty] | 27009850
44950000
27009850
Note: Only Income tax included other taxes will be charged seperately as per Govt rules.