## App A2.2 - SUMMARY
OFFICE FITOUT - BILL OF QUANTITIES
Deutsche Bank Interiors, Karachi |  |  |  | 2022-04-11
ELECTRICAL & ALLIED WORKS (ADVANCE PACKAGE)
Ser # | Description | Material | Labor/Installation | Total Cost (Supply + Labor)
1 | ELECTRICAL & ALLIED WORKS
1.1 | WIRING / WIRING ACCESSORIES
1.2 | CABLE CONTAINMENT
1.3 | SWITCHES & SOCKETS
1.4 | LIGHTING FIXTURES
1.5 | EARTHING / GROUNDING SYSTEM
1.6 | OPENING / DISMANTLING
2 | MISCELLANEOUS
2.1 | AS-BUILT PACKAGE
SUMMARY COST INCLUDING GST (PKR)
Withholding Tax (10%)
Sindh Services Tax (13%)
GRAND TOTAL FOR ELECTRICAL AND ALLIED WORKS (PKR)

## App A2.2 - Electrical-BOQ
Deutsche Bank Interiors, Karachi | [9 empty] | 2022-04-11
OFFICE FITOUT - BILL OF QUANTITIES
ELECTRICAL & ALLIED WORKS (ADVANCE PACKAGE)
Ser # | Description | Unit | Qty | Model Make | Base Rate | Material |  | Labor/Installation |  | Total Cost (Supply + Labor) | Tenderer
[6 empty] | Supply Cost of Material (Unit) | Total Supply Cost | Labour/ Installation Cost (Unit) | Total Labor Cost |  | Remarks
1 | ELECTRICAL & ALLIED WORKS
1.1 | WIRING / WIRING ACCESSORIES
Supply, Installation, Testing and Commissioning of following items including all material, tools, labor & accessories required for completion of work as per description & drawings. Complete in all respects. Note: 1) The cost of wiring items shall includes Imported Fire Rated WAGO or equivalent Connectors and flexible G.I conduit with PVC Coating of appropriate size on each light point. 2) The circuit wire drop and busway plug / tap-off to light / power point riser shall be sufficient as per false ceiling levels and shall be in flexible GI conduit with PVC coating. 3) The wiring shall be done with PVC wires/cables 4) Megger Test of each circuit to be done by contractor. 5) Wiring for Occupancy Sensor shall be included in light wiring. 6) All Wiring to be LSZH with 450/750 volts to BS 6004
1 | Circuit wiring from DB to switch board including any wiring from switch board to switch board with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core PVC wires in 25mm dia PVC conduit and already laid cable tray as shown in drawings. | No. | 2
2 | Wiring for light point from switch board to first light point with phase 1.5 Sq.mm, common neutral 2.5 Sq.mm and common ECC 2.5 Sq.mm, in 25mm dia PVC conduit as shown on drawings. | No. | 10
a | Point to Point wiring (Including PIR) using the same wires & conduit size as mentioned in the above item. | No. | 4
3 | Wiring of 13A/15A Switch Socket units (RAW Power) from DB to first outlet including wiring within same technology box / adjacent power outlets in separate back boxes with following size of 1-core PVC wires in 25mm dia PVC conduits / cable tray under wall / floor as shown in the drawings.
a | 2 x 4 Sq.mm + ECC 1 x 4 Sq.mm | No. | 3
b | Outlet to Outlet wiring using the same wires & conduit size as mentioned in the above item. | No. | 4
4 | Wiring of 32A 3-Pin Industrial Socket for IT Racks from DB to Industrial Socket with 3 x 6 Sqmm Cu/PVC size of PVC wires in 25mm dia PVC conduit and already laid cable tray as shown on drawings. | No. | 18
1.2 | CABLE CONTAINMENT
1 | Supply & Installation of following sizes of PVC/UPVC/MS Conduits including all accessories such as bends, sockets, j-boxes, flexible conduits, metal saddles e.t.c for Main / Sub Main Power, Telephone & Data Cables, concealed / surface on wall as per design drawings. Provide Pull boxes where ever required.
a | 25mm dia PVC Conduit | Rm. | 100
b | 32mm dia PVC Conduit | Rm. | 1 | [6 empty] | Rate Only
c | 25mm dia Flexible GI Conduit with PVC Coating | Rm. | 50
d | 25mm dia GI Conduit For Fire Alarm | Rm. | 50
2 | Supply and Installation of following sizes of 12 SWG Hot Dipped Galvanized Perforated Cable Tray with 14 SWG Cover (4 feet covers) duly Painted after degreesing, derusting, phosphating and antirust primer complete in all respect with supporting hangers, brackets, elbows, tee & mounting accessories etc. Note: 1) Color Printed Tags to be provided at every 3 Meter Length. 2) U-shaped fischer plates to be used for joints. 3) Earth bonding to be done with every joint. 4) Color to be decided with consent of architect. 5) Imported mounting accessories to be used make mungo or fischer suitable to the site conditions.
a | 300mm x 50mm (Power & Lighting) (Floor Mounted) | Rm. | 300
b | 300mm x 50mm (Data) (Floor Mounted) | Rm. | 214
c | 150mm x 50mm (ELV) (Floor Mounted) | Rm. | 60
d | 150mm x 50mm (ISP) (Ceiling/Floor Mounted/Vertical Riser) | Rm. | 550
3 | Supply & Installation of 16 SWG Sheet Steel Back Boxes for installation of the following as per drawings and details including all accessories.
a | For installation of Light Switches. | No. | 4
b | For installation of 13A/15A Switch Socket. | No. | 7
1.3 | SWITCHES & SOCKETS
Supply & Installation of following 10 Amps switches or 10/13/15/20 Amps socket outlets recessed / surface on wall or as per design drawings. (Clipsal Pieno series for Switches & C-Vivace for Sockets or Equivalent)
1 | One Gang Switch Unit | No. | 1
2 | Three Gang Switch Unit | No. | 3
3 | 13A, International Switch Socket unit | No. | 7
4 | 15A, Round 3 pin Switch Socket unit | No. | 1 | [6 empty] | Rate Only
5 | 32A 3-Pin (Single Phase) Industrial Socket with Plug for IT Racks | No. | 18
6 | 80A 5-Pin (Three Phase) Industrial Socket with Plug for UPS | No. | 2
1.4 | LIGHTING FIXTURES
Supply, Installation, Testing & Commissioning of the following lighting fixtures complete with driver and specified lamps, installation and hanging accessories upto 1 meter length for all pendant lights as per drawings and specificaion complete in all respect. (Refer Drawing Light Fixture Schedule) Note: 1) Power factor of all light fixture shall not be less than 0.9. 2) Efficacy >100lm/W and CRI > 90. 3) All down light shall have COB ship. 4) Fixture must be made of die-cast aluminum with aluminum heat sink. 5) All light fixture shall be finalized after taking approval from architect/consultant 6) Minimum 3 year warranty required from date of successful commissioning of light and driver both.
1 | L3- Linear LED 36 watt Surface - IP-65 | No. | 14
1.5 | EARTHING / GROUNDING SYSTEM
Supply, installation, testing and commissioning of following imported items for Earthing / Grounding System for lightning protection and grounding of other systems including all material, boring, labor, tools, transportation, all accessories etc. Complete in all respects as per drawing and specification with detailed test reports.
1 | Earth Connectivity through Jumpers on Raised Floors at a distance of every 2 Sqm. | Job | 1
2 | Earth Connecting Point (ECP) or Equipotential bar made with 300 mm wide, 50 mm high and 8 mm thick tin plated Copper, as shown in drawings. Bar shall be provided with holes suitable for installation of 4 No. 95 sqmm bare copper conductor. ECP shall be enclosed in 300mm x 100mm x 100mm size of powder coated metal enclosure with front accessible cover. | No. | 4
3 | Supply, installation, testing & commissioning of following size of single core PVC cables in appropriate size of exposed / concelled conduit from ECP to several equipments as per details given below, including all material, labor, tools, transportation, accessories etc. Complete in all respects with detailed test reports.
4 | 1C 16 Sqmm Cu/PVC in 25mm dia PVC Conduit | Rm. | 200
1.6 | OPENING / DISMANTLING
1 | Core Cutting: The contarctor will do the core cutting (metal slab) within TR to connect to TER below; 3No.s 50mm for IT, 1No. 75mm for ELV, 1No. 100mm for Power. | Job | 1 | [8 empty] | 0
2 | Wall Cutting: The contarctor will do the walls openings at basement level (parking floor) of 200mm x 100mm for the cable tray to enter into the vertical shaft as well as at respective floors where it will enter DB premises. | Job | 1 | [8 empty] | 0
Fire stopping
3 | Supply and installation of fire stopping system complete in all respect as per drawings, specifications and upon instruction of Consultant and Project Manager | Job | 1
2 | MISCELLANEOUS
2.1 | AS-BUILT PACKAGE
1 | Preparation of as-built drawings and documents of all electrical and allied works after final approval from the consultant/client. Note: 1) Submission of as-built drawings 2 sets after work completion of each floor and 3 sets & soft copy of complete electrical works after final commissioning of project. Approval of final bills are subject to completion of as built drawings. 2) Documents including the Operation and Maintenance Manuals. 3) Testing Reports and Measurement Sheets. 4) Warranty certificates for products. | Job | 1
TOTAL COST OF ELECTRICAL & ALLIED WORKS
Note
Any statutory approvals required to be taken by the Contractor.

## BLANK BOQ (hidden)
UNILEVER PAKISTAN LTD
3RD FLOOR
Ser # | Description | Unit | Qty | Rate | Amount
1 | CIVIL WORK
1.1 | BLOCK MASONRY
Cement concrete block masonry set in 1:4 cement
mortar with 1:4:5 or 1:3:6 machine made block minimum 800 psi
(approved by the Architect) including racking out joints curing, etc.,
complete as per specifications and relevant drawings
| 6" thick (External) | Sft | 5665
| 4" thick (Internal) | Sft | 500
| 3" Thick brick cladding ( Lobby Feature Wall) | Sft | 200
1.2 | PLASTER
Plaster 0.75" thick 1:4 cement plaster to internal
walls, columns, beams, slabs, lintels, steps, etc., including making
chamfered shape edges or rounding off corners at junctions including
curing, etc., complete as per specifications and relevant drawings.
a | Internal Walls | Sft | 8000
b | External periphery walls | Sft | 6700
1.3 | DRY WALL PARTITION WALL
a | 100 mm MDF partition on 75 mm x 75mm partal wood framing @600 mm x 600mm c.c (approx),in ducco finish,treated with approved antitermite slagnum & zahbia primer on both ends of MDF , shall ensure the sample to be approved before purchase of material. The approved sample shall always be at site as detailed in the General Condition of Contract. | Sft | 7000
b | GLASS WALL PARTITION (Translucent Glass film)
| 12 mm thick imported tempared glass fixed, Champaign color aluminium U- channel along with the wall at top and bottom and polishing of exposed edges,with 3M Electro cut 314 Brand frosted film complete in all respects and as directed by the Architect. | Sft | 3100
1.4 | PAINT
Low VOC acrylic emulsion by JOTUN paint on walls of approved quality and shade including rubbing, filling and primer coat., complete in all respects.
a | Internal Fair Faced Textured paint (includes walls and ceiling) | Sft | 5000
b | Internal Walls | Sft | 18500
External Weathred shield
c | 3 coats, external weathered shield by JOTUN, ICI, Nelson paint complete in all respects of approved quality and shade including rubbing, filling and primer coat. | Sft | 6700
1.5 | FLOORING & SPECIAL FINISHES
1.5.1 | PORCELAIN TILES IN OFFICE SPACES
Porcelain tile of 12"x24" full body approved quality.Shade pattern set in 1:4 cement mortar including preparing proper base of 1:2:4 concrete mortar all as per specification and drawing complete in all respect. (MML Product supplied by Benitoz or Equivalent; color & size to be approved by the Architect, price will be Rs. 3000 / sqm)
a | Flooring | Sft | 1000
1.5.2 | PORCELAIN TILES IN WET AREA TILES
Porcelain tile of 12"x24" full body approved quality.Shade pattern set in 1:4 cement mortar including preparing proper base of 1:2:4 concrete mortar all as per specification and drawing complete in all respect. (MML Product supplied by Benitoz or Equivalent; color & size to be approved by the Architect, price will be Rs. 3000 / sqm)
a | Floor | Sft | 1350
b | Wall | Sft | 4500
1.5.3 | CORRIDOR TILES
Porcelain tile of Fiandre Marmi MaximumTravertino size 5'x10' full body approved quality.Shade pattern set in 1:4 cement mortar including preparing proper base of 1:2:4 concrete mortar all as per specification and drawing complete in all respect. (Fiandre Product supplied by Benitoz or Equivalent; color & size to be approved by the Architect, price will be Rs. 13000 / sqm)
a | Floor | Sft | 15750
1.5.4 | GRANITE COUNTER TOP
Granite counter top , including all beds and anchoring, finished as below: (with basin hole cutting and special finishes complete as per drawing ) The Granite will be installed on a GI frame with red oxide coating and the finished with black spray paint. Rs. 800 / sqft
b | Polished finish on Counter Tops | Sft | 260
1.5.5 | GRANITE STEPS
i | Granite to be installed on the Steps using dry bond methodology . Dry bond to be used is Ressichem T210 or Millwala's Tifix
ii | Grouting. Water proof grouting color to be specified by the Architect.
Included in the laying of the Granite will be preparation of floor using cement mix to achieve perfect alignment a required of the floor for the application of tiles. Rs. 800 / sqft
iii | 3" Flame torch finish on Staircase Tread 5'-0" | No | 17
iv | Polish finish on Staircase Riser | No | 21
1.6 | SPECIAL FINISHES
a | Branding and Display (refer to attachment) | Sft | 765
b | Green wall (refer to attachment) baseprice Rs. 2500 SQFT | Sft | 350
c | Ceramic wall cladding (refer to attachment) | Sft | 265
b | Internal Ceiling | Sft | 26000
1.7 | ALUMINUM WINDOW
EXTERNAL WINDOWS
Aluminum Windows using imported section and high quality hardware; that must be airtight with minimum infiltration and exfiltration properties. The Aluminum section will be powder coated, color to be approved by Architect.
(Double-Glazed assembly with U-value of 1.4 W/Sqm.K in 6mm Low-E Exterior Glass + 12mm Air Gap (with or without Argon filling) + 6mm local clear Internal Glass)
| Imported Aluminum windows of W1 size 6'-0" x 4'-6" on front façade. | No. | 7
| Imported Aluminum windows of W2 size 14'-0" x 4'-6" on front façade (Board Room) . | No. | 1
TOTAL COST OF CIVIL WORK
2 | INTERIOR FINISHES WORK
2.1 | CARPET FLOOR
| Carpet as specified by Architect (For spec find the attachment) SQFT Rs. 325 | Sft | 20000
2.2 | VINYL FLOORING
Seamless vinyl flooring by Tarkett or equivalent. Thinkness 4.5mm. (50 mm x 50 mm tile) Inteface level set collection availabe from pak carpets or equivalent. SQFT Rs .265
| Color and size as approved by the Architect. | Sft | 550
2.3 | RUBBER FLOORING
| (Gym Area) 8.2 MM Thickness (For spec find the attachment) | Sft | 150
2.3 | FALSE CEILING
a | CEMENT BOARD CEILING
| Cement Board false ceiling at edges allaround the rooms and corridors to as make-up space to ensure metal pan ceilings are not cut and are used as full tiles. (Rs:110) | Sft | 27500
b | STEEL MESH CEILING IN VITALITY ZONE (Hexazonal MS frame rapped with steel mesh) | Sft | 1600
c | ALUMINUM CEILING ( High-grade pre-coated aluminum alloy ) 0.5mm~1.0mm thinckness | Sft | 1250
2.4 | MDF CLADDING (2" thick partal wood frame rapped around 1/2" thick one side MDF sheet).
| Providing MDF cladding on all exposed columns. | Sft | 7000
2.8 | JOINERY
1.5" thick solid core commercial ply veneer flush door shutters (Formite 7195 - Baluchistan Laminates) SWG G.I 16 gauage door frames 2" x 7" so lignum painted 2"x5/8", approved quality of oxidized brass hinges, brass screw, tower bolts, imported locks top of the line quick set hydraulic door closer (brand-New Star Japanese) Wherever needed aluminum push plates on both sides door stopper and other hardware of brass including iron hold fasts, complete in all respects as per drawings and as directed by the Architect.
| Size 3'-0" X 7'-0" | No | 6
| Size 2'-6" X 7'-0" | No | 9
2.9 | METAL SCREEN
| Laser cut perforated ( High Strength Low Alloy HSLA steel ) corten metal sheet. | Sft | 950
2.7 | Metal framing joinery work for the perforated partition and S.S pipes feature. | Sft | 300
2.9 | SKIRTING
a | PVC skirting of 2" thick in dark grey color. | Rft | 3500
TOTAL COST OF INTERIOR FINISHES WORK
3 | IMPORTED PARTITION WALLS & DOOR
3.1 | WOODEN PARTITION | Sft | 5500
3.2 | 6 plus 6mm LAMINATED TEMPERED GLASS PARTITION | Sft | 2500
3.3 | 10mm TEMPERED GLASS DOOR IN PARTITION | No | 30
3.4 | WOODEN DOOR IN PARTITION | No | 2
TOTAL COST OF PARTITION WALL & DOORS
SUMMARY
1 | CIVIL WORK
2 | INTERIOR FINISHES WORK
3 | PARTITION WALLS & DOORS
TOTAL COST