## VAV (15th)
Deutsche Bank
Karachi |  |  |  | REV#01
Date: 11-05-2022
SCHEDULE OF VAV BOXES FOR 15th FLOOR
TAG NO | QTY | SPACES SERVED | MIN SUPPLY AIR | MAX SUPPLY AIR
| Nos. |  | CFM | CFM
VAV-01 | 1 | Support Staff | 110 | 155
VAV-02 | 1 | Mail Room | 148.5 | 205
VAV-03 | 1 | Teller Office | 170.5 | 270
VAV-04 | 1 | Medium Meeting Room | 264 | 365
VAV-05 | 1 | Reception Lobby | 467.5 | 470
VAV-06 | 1 | Small Meeting Room | 225 | 500
VAV-07 | 1 | Group Audit | 255 | 565
VAV-08 | 1 | Faith Room | 195 | 585
VAV-09 | 5 | GRE + CSO_6 | 454.52 | 796
VAV-10 | 1 | TDI (CTM)-5 | 510 | 915
VAV-11 | 5 | GRE + CSO_6 | 577.8 | 1170
VAV-12 | 1 | Break Out | 1275 | 1650
Total | 20
Notes :
(i) All VAV & CAV Boxes should have factory fitted controllers
(ii) Control wiring will be done from controller to VAV/CAV by supplier.
(iii) All VAV Boxes must be equipped with Thermostat and digital display.
(iv) Pressure Sensor required for all VAVs & CAVs
(v) Standalone BMS interfacable central controller with control wiring to be provided and installed by the supplier.
(vi) Supplier to provide complete submittal with all the necessary information for consultant approval.

## CAV (15th)
Deutsche Bank
Karachi |  |  | REV#01
Date: 11-05-2022
SCHEDULE OF CAV BOXES FOR 15th FLOOR
TAG NO | QTY | SPACES SERVED | SUPPLY AIR
| Nos. |  | CFM
CAV-01 | 1 | FM Store | 125
CAV-02 | 1 | IT Store | 160
CAV-03 | 1 | Vault | 215
CAV-04 | 1 | File Storage | 405
CAV-05 | 1 | Breakout | 600
Total | 5
Notes :
(i) All VAV & CAV Boxes should have factory fitted controllers
(ii) Control wiring will be done from controller to VAV/CAV by supplier.
(iii) All VAV Boxes must be equipped with Thermostat and digital display.
(iv) Pressure Sensor required for all VAVs & CAVs
(v) Standalone BMS interfacable central controller with control wiring to be provided and installed by the supplier.
(vi) Supplier to provide complete submittal with all the necessary information for consultant approval.

## VAV (16th)
Deutsche Bank
Karachi |  |  |  | REV#01
Date: 11-05-2022
SCHEDULE OF VAV BOXES FOR 16th FLOOR
TAG NO | QTY | SPACES SERVED | MIN SUPPLY AIR | MAX SUPPLY AIR
| Nos. |  | CFM | CFM
VAV-01 | 1 | Compliance_4 | 315 | 365
VAV-02 | 1 | Large Meeting Room | 302.5 | 410
VAV-03 | 1 | COO Office | 307.5 | 550
VAV-04 | 2 | PA / Waiting, HR Office | 300 | 575
VAV-05 | 1 | CCO Office | 435 | 1000
VAV-06 | 1 | Treasury IB_6 | 450 | 1235
VAV-07 | 1 | CFO Office | 787.5 | 1390
VAV-08 | 1 | CLM_8 & Corp Bank_12 | 1350 | 1625
Total | 9
Notes :
(i) All VAV & CAV Boxes should have factory fitted controllers
(ii) Control wiring will be done from controller to VAV/CAV by supplier.
(iii) All VAV Boxes must be equipped with Thermostat and digital display.
(iv) Pressure Sensor required for all VAVs & CAVs
(v) Standalone BMS interfacable central controller with control wiring to be provided and installed by the supplier.
(vi) Supplier to provide complete submittal with all the necessary information for consultant approval.

## CAV (16th)
Deutsche Bank
Karachi |  |  | REV#01
Date: 11-05-2022
SCHEDULE OF CAV BOXES FOR 16th FLOOR
TAG NO | QTY | SPACES SERVED | SUPPLY AIR
| Nos. |  | CFM
CAV-01 | 2 | Breakout | 170
CAV-02 | 1 | Corridor Right / Left | 1090
Total | 3
Notes :
(i) All VAV & CAV Boxes should have factory fitted controllers
(ii) Control wiring will be done from controller to VAV/CAV by supplier.
(iii) All VAV Boxes must be equipped with Thermostat and digital display.
(iv) Pressure Sensor required for all VAVs & CAVs
(v) Standalone BMS interfacable central controller with control wiring to be provided and installed by the supplier.
(vi) Supplier to provide complete submittal with all the necessary information for consultant approval.

## AHU Sheet (hidden)
PROJECT: REHMAN MEDICAL COLLEGE (RMC)
LOCATION: PESHAWAR
DESIGN PARAMETRES : DB = 100˚F, WB = 83˚F
COOLING LOAD SHEET WITHOUT HRV:
FLOOR | AHU # | Space | Total Area (Sq.Ft) | Calculated Cooling Tonnage (TR) | Calculated Heating Load (MBH) | Sq.Ft/ton | Total Cooling Load (BTU/HR) | Sensible Heat Ratio | Total Sensible Load (BTU/HR) | Total Supply Air CFM | Total Fresh Air CFM |  | Total Return Air CFM | CFM/Sq.Ft
FIFTH FLOOR | AHU-03 | Office | 468 | 2 | 18.4 | 234 | 24000 | 0.884 | 21216 | 445 | 20 | VAV-06 | 425 | 0.95085 | VAV-05
|  | Seminar Not Exp 1 | 830 | 5 | 17.7 | 166 | 60000 | 0.577 | 34620 | 1135 | 590 | VAV-19 | 545 | 1.3675 | VAV-08
|  | Seminar Not Exp 2 | 830 | 5 | 17.7 | 166 | 60000 | 0.577 | 34620 | 1135 | 590 | VAV-19 | 545 | 1.3675 | VAV-08
|  | Seminar 1 | 475 | 2.8 | 7.5 | 169.6429 | 33600 | 0.578 | 19420.8 | 612 | 329 | VAV-10 | 283 | 1.2884 | VAV-02
|  | Seminar 2 | 475 | 2.8 | 7.5 | 169.6429 | 33600 | 0.578 | 19420.8 | 612 | 329 | VAV-10 | 283 | 1.2884 | VAV-02
|  | Seminar 3 | 475 | 2.8 | 7.5 | 169.6429 | 33600 | 0.578 | 19420.8 | 612 | 329 | VAV-10 | 283 | 1.2884 | VAV-02
|  | Seminar 4 | 475 | 2.8 | 7.5 | 169.6429 | 33600 | 0.578 | 19420.8 | 612 | 329 | VAV-10 | 283 | 1.2884 | VAV-02
|  | Skill Lab 1 | 200 | 1.1 | 11.2 | 181.8182 | 13200 | 0.786 | 10375.2 | 450 | 85 | VAV-06 | 365 | 2.25 | VAV-04
|  | Skill Lab 2 | 200 | 1.1 | 11.2 | 181.8182 | 13200 | 0.786 | 10375.2 | 450 | 85 | VAV-06 | 365 | 2.25 | VAV-04
|  | Skill Lab 3 | 200 | 1.1 | 11.2 | 181.8182 | 13200 | 0.786 | 10375.2 | 450 | 85 | VAV-06 | 365 | 2.25 | VAV-04
|  | Passage | 1850 | 5.2827 | - | 350.2008 | 63392.2018 | 0.837 | 53059.2729 | 2253.0963 | 403.0963 |  | 1850 | 1.2179
|  | Total | 6478 | 31.7827 | 117.4 | 203.8217 | 381392.2018 |  | 252324.0729 | 8766.0963 | 3174.0963 |  | 5592 | 1.3532
| AHU-04 | Passage | 1570 | 4.4831 | - | 350.2008 | 53797.7064 | 0.837 | 45028.6803 | 1912.0872 | 342.0872 |  | 1570 | 1.2179
|  | Pathology & Dental Lab | 1175 | 4 | 19.8 | 293.75 | 48000 | 0.678 | 32544 | 1250 | 470 | VAV-20 | 780 | 1.0638 | VAV-13
|  | Seminar Exp 3 | 852 | 6.1163 | 23.6 | 139.3 | 73395.5492 | 0.642 | 47119.9426 | 1540 | 590 | VAV-23 | 950 | 1.81 | VAV-16
|  | Seminar Exp 4 | 910 | 6.5327 | 23.6 | 139.3 | 78391.9598 | 0.642 | 50327.6382 | 1647.1 | 627.9 | VAV-24 | 1019.2 | 1.81 | VAV-16
|  | Seminar Exp 5 | 910 | 6.5327 | 23.6 | 139.3 | 78391.9598 | 0.642 | 50327.6382 | 1647.1 | 627.9 | VAV-24 | 1019.2 | 1.81 | VAV-16
|  | Seminar 5 | 475 | 2.8 | 7.5 | 169.6429 | 33600 | 0.578 | 19420.8 | 612 | 329 | VAV-10 | 283 | 1.2884 | VAV-02
|  | Skill Lab 4 | 200 | 1.1 | 11.2 | 181.8182 | 13200 | 0.786 | 10375.2 | 450 | 85 | VAV-06 | 365 | 2.25 | VAV-04
|  | Total | 6092 | 31.5648 | 109.3 | 193 | 378777.1752 |  | 255143.8992 | 9058.2872 | 3071.8872 |  | 5986.4 | 1.4869
| AHU-02 | Passage | 800 | 2.2844 | - | 350.2008 | 27412.844 | 0.837 | 22944.5505 | 974.3119 | 174.3119 |  | 800 | 1.2179
|  | Seminar Exp 1 | 735 | 5.2764 | 23.6 | 139.3 | 63316.5829 | 0.642 | 40649.2462 | 1330.35 | 507.15 | VAV-21 | 823.2 | 1.81 | VAV-13
|  | Seminar Exp 2 | 788 | 5.6569 | 23.6 | 139.3 | 67882.2685 | 0.642 | 43580.4164 | 1426.28 | 543.72 | VAV-22 | 882.56 | 1.81 | VAV-15
|  | Junior Faculty | 1235 | 6.3 | 37.7 | 196.0317 | 75600 | 0.614 | 46418.4 | 1800 | 450 | VAV-25 | 1350 | 1.4575 | VAV-21
|  | Lecture Theatre 02 | 1235 | 5.6 | 17.9 | 220.5357 | 67200 | 0.58 | 38976 | 1260 | 675 | VAV-20 | 585 | 1.0202 | VAV-09
|  | Student's Affair | 170 | 0.8 | 8.8 | 212.5 | 9600 | 0.871 | 8361.6 | 370 | 30 | VAV-04 | 340 | 2.1765 | VAV-03
|  | Principal Office | 170 | 0.9 | 9.6 | 188.8889 | 10800 | 0.86 | 9288 | 400 | 35 | VAV-04 | 365 | 2.3529 | VAV-04
|  | Seminar 6 | 627 | 3.7771 | 17.7 | 166 | 45325.3012 | 0.577 | 26152.6988 | 808.83 | 601.92 | VAV-13 | 545 | 1.29 | VAV-08
|  | Assistant Professor | 145 | 1.2 | 6 | 120.8333 | 14400 | 0.924 | 13305.6 | 540 | 25 | VAV-08 | 515 | 3.7241 | VAV-07
|  | AsistanT Professor 1 | 145 | 0.7 | 8.1 | 207.1429 | 8400 | 0.869 | 7299.6 | 330 | 25 | VAV-03 | 305 | 2.2759 | VAV-02
|  | AsistanT Professor 2 | 145 | 0.7 | 8.1 | 207.1429 | 8400 | 0.869 | 7299.6 | 330 | 25 | VAV-03 | 305 | 2.2759 | VAV-02
|  | Subtotal | 6195 | 33.1947 | 161.1 | 186.6259 | 398336.9966 |  | 264275.7119 | 9569.7719 | 3092.1019 |  | 6815.76 | 1.5448
| AHU-01 | Passage | 4500 | 12.8498 | - | 350.2008 | 154197.2477 | 0.837 | 129063.0963 | 5480.5046 | 980.5046 |  | 4500 | 1.2179
|  | Lecture Theatre 01 | 1130 | 8.6 | 38.6 | 131.3953 | 103200 | 0.704 | 72652.8 | 2580 | 670 | VAV-30 | 1910 | 2.2832 | VAV-26
|  | Board Room | 320 | 1.6 | 7.1 | 200 | 19200 | 0.753 | 14457.6 | 530 | 90 | VAV-08 | 440 | 1.6562 | VAV-06
|  | Anatomy Museum | 595 | 3.5 | 17 | 170 | 42000 | 0.769 | 32298 | 1270 | 215 | VAV-20 | 1055 | 2.1345 | VAV-17
|  | Reception | 96 | 0.4 | 4 | 240 | 4800 | 0.843 | 4046.4 | 180 | 15 |  | 165 | 1.875
|  | Subtotal | 6641 | 26.9498 | 66.7 | 246.4214 | 323397.2477 |  | 252517.8963 | 10040.5046 | 1970.5046 |  | 8070 | 1.5119
SIXTH FLOOR | AHU-03 | Anatomy Lab | 294 | 1.1 | 4.7 | 267.2727 | 13200 | 0.667 | 8804.4 | 300 | 130 | VAV-02 | 170 | 1.0204 | VAV-01
|  | Asistant Associates Lecturers | 510 | 2 | 18.2 | 255 | 24000 | 0.841 | 20184 | 820 | 140 | VAV-13 | 680 | 1.6078 | VAV-11
|  | Board Room | 615 | 2.5 | 11.3 | 246 | 30000 | 0.658 | 19740 | 700 | 190 | VAV-11 | 510 | 1.1382 | VAV-07
|  | Class Rm 1 Not Exp | 966 | 4.6 | 25.2 | 210 | 55200 | 0.665 | 36708 | 1320 | 425 | VAV-21 | 895 | 1.3665 | VAV-15
|  | Class Rm 2 Not Exp | 966 | 4.6 | 25.2 | 210 | 55200 | 0.665 | 36708 | 1320 | 425 | VAV-21 | 895 | 1.3665 | VAV-15
|  | Demo For CRS | 1110 | 5.2857 | 25.2 | 210 | 63428.5714 | 0.665 | 47322 | 1516.7702 | 488.4 | VAV-23 | 1028.3702 | 1.3665 | VAV-16
|  | Faculty Office 2 | 260 | 1.3 | 12.2 | 200 | 15600 | 0.694 | 10826.4 | 480 | 55 | VAV-07 | 425 | 1.8462 | VAV-05
|  | Passage | 1850 | 5.4948 | - | 336.6795 | 63392.2018 | 0.837 | 53059.2729 | 2323.1078 | 403.0963 |  | 1920.0115 | 1.2557
|  | Subtotal | 6571 | 26.8806 | 122 | 244.4518 | 320020.7733 |  | 233352.0729 | 8779.878 | 2256.4963 |  | 6523.3817 | 1.3362
| AHU-04 | Class Room 3 Exp | 1040 | 5.5 | 25.1 | 189.0909 | 66000 | 0.717 | 47322 | 1520 | 430 | VAV-23 | 1090 | 1.4615 | VAV-18
|  | Class Room 4 Exp | 1040 | 5.5 | 25.1 | 189.0909 | 66000 | 0.717 | 47322 | 1520 | 430 | VAV-23 | 1090 | 1.4615 | VAV-18
|  | Class Room 5 Exp | 1040 | 5.5 | 25.1 | 189.0909 | 66000 | 0.717 | 47322 | 1520 | 430 | VAV-23 | 1090 | 1.4615 | VAV-18
|  | Class Room 6 Exp | 1040 | 5.5 | 25.1 | 189.0909 | 66000 | 0.717 | 36708 | 1520 | 430 | VAV-23 | 1090 | 1.4615 | VAV-18
|  | Faculty Office 1 | 260 | 1.3 | 12.2 | 200 | 15600 | 0.694 | 10826.4 | 480 | 55 | VAV-07 | 425 | 1.8462 | VAV-05
|  | Passage | 1570 | 4.6632 | - | 336.6795 | 53797.7064 | 0.837 | 45028.6803 | 1912.0872 | 342.0872 |  | 1570 | 1.2557
|  | Subtotal | 5990 | 27.9632 | 112.6 | 214.2102 | 333397.7064 |  | 234529.0803 | 8472.0872 | 2117.0872 |  | 6355 | 1.4144
| AHU-01 | Cafeteria | 595 | 4.2 | 12.5 | 141.6667 | 50400 | 0.46 | 23184 | 770 | 380 | VAV-12 | 390 | 1.2941 | VAV-04
|  | IT Lab | 1470 | 6 | 29.7 | 245 | 72000 | 0.696 | 50112 | 1985 | 630 | VAV-27 | 1355 | 1.3503 | VAV-21
|  | Kine Lab | 665 | 3.6 | 26.2 | 184.7222 | 43200 | 0.782 | 33782.4 | 1330 | 290 | VAV-21 | 1040 | 2 | VAV-17
|  | Library | 1235 | 6 | 35.1 | 205.8333 | 72000 | 0.818 | 58896 | 2445 | 315 | VAV-30 | 2130 | 1.9798 | VAV-28
|  | Physiology Lab | 300 | 1.7 | 9.5 | 176.4706 | 20400 | 0.787 | 16054.8 | 600 | 130 | VAV-10 | 470 | 2 | VAV-06
|  | Principal Office | 170 | 1.1 | 9.6 | 154.5455 | 13200 | 0.801 | 10573.2 | 465 | 40 | VAV-06 | 425 | 2.7353 | VAV-05
|  | Passage | 800 | 2.3761 | - | 336.6795 | 28513.7615 | 0.717 | 20444.367 | 1004.5872 | 174.3119 |  | 830.2752 | 1.2557
|  | Subtotal | 5235 | 24.9761 | 122.6 | 209.6 | 299713.7615 |  | 213046.767 | 8599.5872 | 1959.3119 |  | 6640.2752 | 1.6427
| AHU-02 | Faculty Lounge | 385 | 1.9 | 13.4 | 202.6316 | 22800 | 0.768 | 17510.4 | 760 | 65 | VAV-12 | 695 | 1.974 | VAV-11
|  | Female Lounge | 360 | 1.9 | 13.4 | 202.6316 | 22800 | 0.768 | 17510.4 | 760 | 57.6 | VAV-12 | 695 | 1.974 | VAV-11
|  | Seminar | 920 | 9.2 | 32.3 | 100 | 110400 | 0.72 | 79488 | 2200 | 530 | VAV-29 | 1670 | 2.3913 | VAV-24
|  | Reception | 85 | 0.5 | 1.1 | 170 | 6000 | 0.693 | 4158 | 150 | 30 |  | 120 | 1.7647
|  | Student's Affair | 85 | 0.7 | 8.2 | 121.4286 | 8400 | 0.8 | 6720 | 315 | 30 | VAV-02 | 285 | 3.7059 | VAV-02
|  | Male Lounge | 360 | 1.9 | 13.4 | 202.6316 | 22800 | 0.768 | 17510.4 | 760 | 65 | VAV-12 | 695 | 1.974 | VAV-11
|  | Passage | 4500 | 13.3658 | - | 336.6795 | 154197.2477 | 0.837 | 129063.0963 | 5650.8028 | 980.5046 |  | 4670.2982 | 1.2557
|  | Subtotal | 6695 | 29.4658 | 81.8 | 227.2124 | 347397.2477 |  | 271960.2963 | 10595.8028 | 1758.1046 |  | 8830.2982 | 1.5826
250-300
300-340
340-370
350-400
2200
2580

## Summit Bank(CAV) (hidden)
PROJECT: JS Tower
LOCATION: Karachi
Date:26-01-2018
SCHEDULE OF CAV BOXES
TAG NO | QTY | SPACES SERVED | SUPPLY AIR | ELECTRICAL CHARACTERISTICS | ELECTRICAL LOAD | ELECTRICAL LOAD (total) | MAX. NC LEVEL
| Nos. |  | CFM |  | kW | kW | NC
20F-CAV-01 | 1 | lobby | 275 | 1 Ph + N + E | 0.1 | 0.1 | 35
20F-CAV-02 | 1 | entrance | 530 | 1 Ph + N + E | 0.1 | 0.1
20F-CAV-03 | 1 | bank offices | 760 | 1 Ph + N + E | 0.15 | 0.15
20F-CAV-04 | 1 | lobby | 1030 | 1 Ph + N + E | 0.15 | 0.15
20F-CAV-05 | 2 | entrance | 1350 | 1 Ph + N + E | 0.15 | 0.3
21F-CAV-01 | 1 | librarian ofice | 1690 | 1 Ph + N + E | 0.15 | 0.15
Total | 7 |  |  |  |  | 0.95
Note :
All CAV Boxes should have factory fitted controllers
Control wiring should be provided from controller to CAV
Electrical power to be provided by electrical consultant