## 15F
Deutsche Bank
Karachi |  |  | REV: 01
15th Floor |  |  | Date: 11-05-2022
SCHEDULE OF VENTILATION FANS
Description | Unit | TAF-01 (1-2) | TAF-01 (2-2)
Quantity | No. | 1 | 1
Location |  | 15th Floor | 15th Floor
Spaces Served |  | Above Support Staff False Ceiling | Above Mail Room False Ceiling
Supply Air Quantity | CFM | 130 | 190
External Static Pressure | Inch WC | Standard | Standard
Max Fan Blower Revolution | RPM | 1450 | 1450
Duty |  | Transfer Air | Transfer Air
Max.Sound Level at 1 m | dB | 45 | 45
Configuration |  | Wall Mounted Propeller Type | Wall Mounted Propeller Type
Construction |  | Front Dischage & Rear Intake | Front Dischage & Rear Intake
Max.Fan Outlet Velocity | FPM | 1600 | 1600
Motor Protection |  | Standard | Standard
Max Motor Revolution | RPM | 1450 | 1450
Drive |  | Direct Drive | Direct Drive
Electrical Characteristic |  | 220~240V /1Ph/ 50 Hz | 220~240V /1Ph/ 50 Hz
Accessories |  | Speed Regulator | Speed Regulator
Remarks
Notes:
A- Motor power input to be provided by the Manufacturer / Supplier along with data sheet.
B- Computer selection of each model fan to be provided by the suppliers for Consultant approval along with fan dimensions.
SWSI Centrifugal Fan constructed in welded steel with Backward Curve Wheel. coated with non stick Teflon coating were as fan shall be painted with , Stainless Steel Shaft, Belt
SWSI Centrifugal Belt driven Up blast Fan with Backward Curve Wheel.
Fan Housing and Wheel shall be Constructed of not less than 2.0mm thickness (14 Gauge) Galvanized Steel Sheet with continuous Welded Joints.
Fan Wheel Must be Statically and Dynamically Balanced
Fan Housing supports are constructed of structural steel with formed flanges.
Drive frame is welded steel which supports the shaft and bearings and reinforcement for the housing.

## 16F
Deutsche Bank
Karachi |  |  | REV: 01
16th Floor |  |  | Date: 11-05-2022
SCHEDULE OF VENTILATION FANS
Description | Unit | TAF-01 | TAF-02
Quantity | No. | 1 | 1
Location |  | 16th Floor | 16th Floor
Spaces Served |  | Above Small Meeting Room False Ceiling | Above Large Meeting Room False Ceiling
Supply Air Quantity | CFM | 145 | 335
External Static Pressure | Inch WC | Standard | Standard
Max Fan Blower Revolution | RPM | 1450 | 1450
Duty |  | Transfer Air | Transfer Air
Max.Sound Level at 1 m | dB | 45 | 45
Configuration |  | Wall Mounted Propeller Type | Wall Mounted Propeller Type
Construction |  | Front Dischage & Rear Intake | Front Dischage & Rear Intake
Max.Fan Outlet Velocity | FPM | 1600 | 1600
Motor Protection |  | Standard | Standard
Max Motor Revolution | RPM | 1450 | 1450
Drive |  | Direct Drive | Direct Drive
Electrical Characteristic |  | 220~240V /1Ph/ 50 Hz | 220~240V /1Ph/ 50 Hz
Accessories |  | Speed Regulator | Speed Regulator
Remarks
Notes:
A- Motor power input to be provided by the Manufacturer / Supplier along with data sheet.
B- Computer selection of each model fan to be provided by the suppliers for Consultant approval along with fan dimensions.
SWSI Centrifugal Fan constructed in welded steel with Backward Curve Wheel. coated with non stick Teflon coating were as fan shall be painted with , Stainless Steel Shaft, Belt
SWSI Centrifugal Belt driven Up blast Fan with Backward Curve Wheel.
Fan Housing and Wheel shall be Constructed of not less than 2.0mm thickness (14 Gauge) Galvanized Steel Sheet with continuous Welded Joints.
Fan Wheel Must be Statically and Dynamically Balanced
Fan Housing supports are constructed of structural steel with formed flanges.
Drive frame is welded steel which supports the shaft and bearings and reinforcement for the housing.

## Make-up air unit (hidden)
Marquee at Islamabad Club
Islamabad |  |  |  | Dated: 06-06-2016
SCHEDULE OF MAKEUP AIR UNITS
Description | Unit | MUA-01 | MUA-02 | MUA-03
Quantity | No. | 1 | 1 | 1
Location |  | Roof | Roof | Roof
Spaces Served |  | Sweets and Baking | Lower ground Kitchen and servery | Ground floor Kitchen area
Heating Capacity | Btu/hr | 235700 | 165700 | 929900
Supply Air Quantity | CFM | 6400 | 4500 | 25250 | 235699.2 | 165726 | 929907
External Static Pressure | Inch WC | 1 | 1 | 1.5
Fan Blower Revolution | RPM | 960 | 960 | 960
Duty |  | Treated Fresh Air Unit | Treated Fresh Air Unit | Treated Fresh Air Unit
Max.Sound Level at 1 meter | dB | 55 - 60 | 55 - 60 | 55 - 60
Configuration |  | Fan with Direct Gas Heating Section | Fan with Direct Gas Heating Section | Fan with Direct Gas Heating Section
Construction |  | Front Dischage & Rear Intake | Front Dischage & Rear Intake | Front Dischage & Rear Intake
Max.Fan Outlet Velocity | FPM | 1600 | 1600 | 1600
Motor Protection |  | Class-F Insulation IP-55 Panel | Class-F Insulation IP-55 Panel | Class-F Insulation IP-55 Panel
Motor Revolution | RPM | 1450 | 1450 | 1450
Drive |  | Belt Drive with Variable Pitch Motor Pulley | Belt Drive with Variable Pitch Motor Pulley | Belt Drive with Variable Pitch Motor Pulley
Electrical Characteristic |  | 380~440V /3Ph/ 50 Hz | 380~440V /3Ph/ 50 Hz | 380~440V /3Ph/ 50 Hz
Accessories
Remarks |  | Weather Proof Canopy along with Fan | Weather Proof Canopy along with Fan | Weather Proof Canopy along with Fan
A. Unit Type:
1. B.D. = Belt Driven
2. D.D. = Direct Driven
A- Motor power input to be provided by the manufacturer / Supplier along with data sheet.
B- Computer selection of each model Fan to be provided by the suppliers for Consultant approval along with fan
dimensions.
C- Fans to be installed at Roof, should have weather proof construction.
SWSI Centrifugal Fan constructed in welded steel with Backward Curve Wheel. coated with non stick Teflon coating were as fan shall be painted with , Stainless Steel Shaft, Belt
SWSI Centrifugal Belt driven Up blast Fan with Backward Curve Wheel.
Fan Housing and Wheel shall be Constructed of not less than 2.0mm thickness (14 Gauge) Galvanized Steel Sheet with continuous Welded Joints.
Fan Wheel Must be Statically and Dynamically Balanced
Fan Housing supports are constructed of structural steel with formed flanges.
Drive frame is welded steel which supports the shaft and bearings and reinforcement for the housing.