## Table 1
Bill of Quantities
Fire Suppression Services
Amreli Steel Limited | [7 empty] | Rev.01
10th Floor, Dolmen Sky Tower, Karachi | [7 empty] | Date: 02-11-2022
S.No. | Description | Unit |  | Material |  | Labour |  | Total
|  |  | Qty | Rate | Amount | Rate | Amount | Amount
| SECTION-01 FIRE FIGHTING SERVICES | Rft. | 350
Supply, installation, testing & commissioning of fire suppression services including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1.1 | MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
i. | Dia 1" (Threaded fitting)
ii. | Dia 1-1/4" (Threaded fitting) | Rft. | 30
iii. | Dia 1-1/2" (Threaded fitting) | Rft. | 70
iv. | Dia 2" (Threaded fitting) | Rft. | 70
v. | Dia. 2-1/2" (Welded joints fitting) | Rft. | 20
vi. | Dia. 3" (Welded joints fitting) | Rft. | 50
1.2 | Sprinkler Heads | Nos. | 46
i. | Sprinkler Upright type quick response K = 5.6 (Opening Temperature 57ºC)
1.3 | Fire extinguishers with fixing accessories. | Nos. | 2
i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas)
ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 2
iii. | Type Class K FX-5 (6 Litre Wet chemical fire extinguisher). | Nos. | 1
Cost of Fire Suppression Services Rs.
| SECTION-02 NOVEC SYSYEM | Kg. | 10
2.1 | CLEAN AGENT (FK-5-1-12 Stored In Cylinder - Ul Listed / Fm Approved)
Supply & installation of clean agent in engineered cylinders of FSS with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
a. | Clean Agent (FK-5-1-12, Fluoroketone)
b. | Engineered cylinder with head valve, top plug adapter, siphon tube, pressure gauge, brackets and all other items, complete in all respect. | Nos. | 2
2.2 | Supply & installation of MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Rft. | 40
i. | Dia 1/2" (Threaded fitting)
2.3 | SPRINKLER HEADS | Nos. | 2
Supply & installation of nozzles with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
Brass Discharge Nozzle - 360 Degrees discharge pattern
i. | Dia 1/2"
2.4 | INPUT & OUTPUT DEVICES | Nos. | 1
Supply & installation of input and output devices for the clean agent suppression system (integrated with BMS) with wiring, controls & fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant
i. | Entinguishing Control Panel for the clean agent fire suppression system
ii. | Manual Abort / Emergency Cut Off Switch | Nos. | 2
iii. | Manual Release Switch - Single Action | Nos. | 2
iv. | Horn / Strobe | Nos. | 1
v. | Alarm Bell | Nos. | 1
2.5 | ACTUATION DEVICES | Nos. | 2
Supply & installation of actuation devices with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
i. | Solenoid Actuator for the specified cylinder size
ii. | Manual Control Head for manual actuation of cylinder with safety pull pin | Nos. | 2
iii. | Pressure Switch to indicated system discharge with an external manual reset button | Nos. | 2
iv. | Low Pressure Switch to monitor the pressure within the cylinder | Nos. | 2
2.6 | WIRING | Job. | 1
i. | Supply & installation of wiring of 2C, 1.5 Sq.mm fire resistant shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia MS conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respects ready to operate as per drawings, specification, instruction of consultant.
2.7 | Making of Shop drawings on Auto CAD 2018 with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects as per instruction of consultant. | Job. | 1
2.8 | Painting, identification and tagging to the installations and equipments, complete in all respects as per instruction of consultant. | Job. | 1
2.9 | Flushing of entire fire pipe work according to (NFPA-13), complete in all respects as per instruction of consultant. | Job. | 1
2.1 | Testing and commissioning of entire fire fighting and clean agent for fire suppression system complete in all respects as per instruction of consultant. | Job. | 1
Cost of Novec System Rs.
Cost of Fire Suppression Services Rs.
Cost of Novec System Rs.
Total Cost of Fire Suppression Services Rs.