## Summary
S.# | DESCRIPTION | SUPPLY (Rs.) | INSTALLATION (Rs.) | TOTAL (Rs.)
1 | SECTION - A FIRE ALARM SYSTEM
2 | SECTION - B PUBLIC ADDRESS SYSTEM
3 | SECTION - C ACCESS CONTROL SYSTEM
4 | SECTION - D CCTV SYSTEM
| Total Amount (Rs.) | 0 | 0 | 0
GST
PST
Grand Total
Notes: ● Contractor is advised to inform missing items (if any) in BOQ at time of submitting this tender. No escalation will be considered at time of execution of work. ● Owner can supply any material of Contractor scope at any stage and its cost will be completely deleted from Contractor scope without any kind of adjustment. ● Contractor should mark the selected brands and vendors in approved manufacturer list with submission of Tender Documents. ● Owner / Consultant have all the rights to select any brand / vendor from provided approved manufacturer list, Contractor shall not finalize any brand / vendor without written approval from consultant / owner. ● Upon completion of 1st fix electrical works, the fit-out contractor should request for first fix inspection by the Fit-Out Team, before closing the false ceiling through ● At the time of 2nd fix Main Distribution Board will be connected up and the wiring will be tested through Megger Test in front of the Fit-Out Team. The report of the same will be duly signed by the Occupant’s Contractor/Project Manager and the Fit-Out Team. Megger Test with KC number punched along with valid calibration certificate of megger test must be submitted. ● Fit-Out contractor to submit Electrical As-Built drawings and other relevant documents immediately after completion of works.
SECTION - G VOICE & DATA COMMUNICATION SYSTEM
Total Amount (Rs.) Sec - G (CARRIED FORWARD TO SUMMARY)
SECTION - H CCTV SYSTEM (IP BASED)
Total Amount (Rs.) Sec - H (CARRIED FORWARD TO SUMMARY)
SECTION - I FIRE ALARM SYSTEM
Fire Repeater Panel along with termination of all Control / Signal cables complete in all aspects. Panel to have all loops marked in distinguishable colors with individual LED's
Total Amount (Rs.) Sec - I (CARRIED FORWARD TO SUMMARY)
SECTION - J INTELLIGENT LIGHTING CONTROL SYSTEM
Total Amount (Rs.) Sec - J (CARRIED FORWARD TO SUMMARY)
SECTION - K PUBLIC ADDRESS SYSTEM
60W - 2 Channel Power Amplifier (For Office) operating at 220V, AC suitable for rack mounting incorporates two audio line level inputs: a Music input and a priority call input. A built-in relay switches the amplifier from the music input of priority call input.
Total Amount (Rs.) Sec - K (CARRIED FORWARD TO SUMMARY)
SECTION - L IP ACCESS CONTROL SYSTEM
|  | 1 | No
|  | 10 | No
|  | 10 | No
|  | 10 | No
|  | 20 | No
6 |  | 8 | No
7 |  | 1 | Job
8
Total Amount (Rs.) Sec - L (CARRIED FORWARD TO SUMMARY)
SECTION - M SHOP DRAWINGS / AS-BUILT DRAWINGS
Total Amount (Rs.) Sec - M (CARRIED FORWARD TO SUMMARY)
SECTION - N PERSONAL PROTECTIVE EQUIPMENTS
Total Amount (Rs.) Sec - N (CARRIED FORWARD TO SUMMARY)

## BOQ
S.# | DESCRIPTION | QTY | UNIT | SUPPLY |  | INSTALLATION |  | TOTAL (Rs.) | Brand | Lead Time | Remarks
|  |  |  | RATE (Rs.) | AMOUNT (Rs.) | RATE (Rs.) | AMOUNT (Rs.)
SECTION - A FIRE ALARM SYSTEM
Supply, Installation, Testing and Commissioning of following items for Addressable Fire Alarm System comprising of following equipments including all accessories required for the completion of the system in all respects. Cables shall be Fire retardant, Low Smoke, Zero Halogen and must comply BS 6387 standard
1 | Addressable Fire Alarm Control Panel of 4-loop having maximum 250 devices per loop. The FACP shall be self powered with built in 12V batteries for 24 Hrs backup with charging unit. It can be programmed using Windows based software for peripheral devices like display unit, printers etc. NOTE: 1) The Panel should have GSM Module to send alters to alteast 3 persons of Client choice. 2) The Panel should have dry contacts for ZCU fault and alarm status. 3) The Panel should be integrated with Building FA System. 4) The Panel should be integrated with Access Control System. 5) The Panel should be able to integrate with BACnet BMS system without any additional item cost. | 1 | No.
2 | Fire Repeater Panel Loop Powered along with termination of all Control / Signal cables complete in all aspects. Panel to have all loops marked in distinguishable colors with individual LED's | 4 | No.
3 | Addressable Smoke Detectors incorporating an LED indication located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 76 | No.
4 | Addressable Multi Detectors incorporating an LED indication located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 15 | No.
5 | Addressable Break Glass Type Manual Call Point having a built in short circuit isolator and built in microprocessor to ensure a response time of max 1 second. It also incorporates an indication LED, flashed after pressing the button to acknowledge the activation and a key operation facility for testing purposes. | 16 | No.
6 | Addressable Type Indoor Loop Powered electronic sounder with flasher and minimum sound out put 89 dB at 1 meter with frequencies for variety of sounds as required. Souder shall be loop wired and loop signaled, built in short circuit isolator, configured via software. | 16 | No.
7 | Environmental Monitoring Sensor with Controller Single combo temperature and humidity sensor, field replaceable sensor module with RJ-45 connector. Environmental Specifications: Temperature: 20-25 Celcius Humidity Level: 40% and 60% | 5 | No. |  | Rate Only |  | Rate Only | Rate Only
8 | I/O Relay for connectivity with diferent systems | 12 | No.
9 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job.
10 | Allow for any other item required for completion of system not covered in BOQ or specifications / drawings in accordance with the same standards and brands shown and approved by consultant. All such items shall be covered in this item but complete description, item rates, quantity required and brands shall be mentioned separately and to be attached with the BOQ. | 1 | Job.
Note: 1) The given quantities are slightly higher then those on drawings, this includes spare and contingencies as well. 2) Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY)
SECTION - B PUBLIC ADDRESS SYSTEM
Supply, Installation, testing & commissioning of following items for Public Address System as described below including all accessories. Complete with mounting brackets, wiring, adapters etc.
1 | 240W - 2 Channel Power Amplifier with Voice Evacuation Manager (For Office) operating at 220V, AC suitable for rack mounting incorporates two audio line level inputs: a Music input and a priority call input. A built-in relay switches the amplifier from the music input of priority call input. | 2 | No.
2 | 6W Recessed type Speakers intended for high quality speech and music reproduction with sealed enclosure protective against moisture and dust. The speaker shall have output power adjustments for full, half and quarter power outputs, including back boxes if required. | 60 | No.
3 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job.
4 | Allow for any other item required for completion of system not covered in BOQ or specifications / drawings in accordance with the same standards and brands shown and approved by consultant. All such items shall be covered in this item but complete description, item rates, quantity required and brands shall be mentioned separately and to be attached with the BOQ. | 1 | Job.
Note: - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. - The Bidder shall provide the complete Technical Literature for the system offered.
Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY)
SECTION - C ACCESS CONTROL SYSTEM
Supply, Installation testing and Commisioning of following items for IP Access Control System (with features of Bio Metric,Face Recognization & RFID for authorization as well as attendance) as described below including all accessories. Complete with mounting brackets, wiring, adapters etc.
1 | Proximity Door Access Controller suitable for 4 door / 4 readers for door access (connecting to readers at upto 100m), monitoring, store at least 10,000 events, provided with power supply unit with battery back-up for at-least 24 hours. Built-in interfacing with TCP / IP switch for LAN/WAN networking and telephone dialer. | 14 | No
2 | Proximity Card Reader 125KHz, (for outside door) reading range 6", operating at low voltage DC supply, with mounting base suitable for interior and exterior environment with dual color LED and speaker for comprehensive audible feed back to user. | 42 | No
3 | Power Supply Units for push buttons complete in all respects. | 15 | No
4 | Proximity Cards ISO credit card standard size and thickness, thin, flexible polyvinyl chloride laminated, passive type, easy printable on both sides( the final number of cards shall be confirmed by the end users). HID Corporate 1000 (iclass). | 600 | No
5 | Touch type Push Button (Exit Switch) suitable for installation on BS standard size back box connected to door controller for access. | 15 | No
6 | Break Glass Unit for Emergency override for the Reader. | 12 | No
7 | Facial Recognition Time Attendance System Face Capacity 5000 Fingerprint Capacity 10000 Password/Cards 15000 OS:Linux CPU : 1.2GHZ RAM : 512MB DDR3L ROM : 4GB EMMC SCREEN : 5' LAN/WIFI/QR-Code with Application Software | 5 | No |  | Rate Only |  | Rate Only | Rate Only
8 | Door Contact | 30 | No
9 | Alarm with Sounder (For emergency Doors) | 3 | No
10 | Magnetic Lock (Single Door) with holder and fixing accessories. | 25 | Nos.
11 | Magnetic Lock (Double Door) with holder and fixing accessories. | 5 | Nos.
12 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
13 | Allow for any other item required for completion of system not covered in BOQ or specifications / drawings in accordance with the same standards and brands shown and approved by consultant. All such items shall be covered in this item but complete description, item rates, quantity required and brands shall be mentioned separately and to be attached with the BOQ. | 1 | Job
Note: - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. - The Bidder shall provide the complete Technical Literature for the system offered.
Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY)
SECTION - D CCTV SYSTEM (IP BASED)
Supply, Installation, Testing & Commissioning of following items for CCTV System (IP Based) including but not limited to the description given here under including all power and communication accessories, housings, mounting brackets, suspension rods etc. required for completion of the system.
1 | Surface/Recessed 2MP Ceiling mounted Mini Dome fixed type PoE I.P camera with day and night feature with 1080p resolution 1280 x 1024 @ 25/30fps pixels with live and recording quality of minimum 15 fps, Varifocal Lens 3.3-12mm, along with all mounting accessories complete in all respect. | 48 | No.
2 | Network Video Recorder (NVR) with 24 channel Video input. The NVR shall be equipped with LAN / WAN facility. NVR should have minimum 30 days storage capacity on 12 frame per second with 60 TB HDD or higher if required to cater 100% cameras, RW CD Drive. Complete with all connecting cords and accessories including SFP modules. | 2 | No.
3 | 12 Port PoE Switch to be installed in Comm. Room in racks with all mounting accessories. | 6 | No.
4 | 32" LED Color Screen to be installed in control Room in racks with all connecting cords and mounting stands. | 2 | No.
5 | Work stations (Core i7 Ultra Slim Desktop PC with Genuine Windows 10 Professional 64bit processor, 16GB ram, 4TB HDD, 4GB Graphics Card & DVD Writer) | 1 | No.
6 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
7 | Allow for any other item required for completion of system not covered in BOQ or specifications / drawings in accordance with the same standards and brands shown and approved by consultant. All such items shall be covered in this item but complete description, item rates, quantity required and brands shall be mentioned separately and to be attached with the BOQ. | 1 | Job
Note: 1) The supplier to confirm the storage requirement as per number of cameras, pixel resolutions, video compression and number of recording days. 2) The Bidder shall provide the complete Technical Literature for the system offered. 3) The given quantities are slightly higher then those on drawings. 4) All the IT Equipements shall be verified by the Client IT. Team before procurement
Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY)