## OPTION 1
SECTION II: BILL OF QUANTITIES FOR MECHANICAL WORKS (Engineer's Estimates)
BOQ No. | Description | Qty | Unit | Material Unit Rate | Material Cost | Installation Unit Rate | Installation Cost | Total Cost
All Air Conditioning, Mechanical Ventilation Works shall be completed, tested and commissioned as per drawings,specifications, ready to operate and as per the instruction of Client/Consultant.
1 | Unloading, rigging, lifting, placement at respective location, installation, testing and commissioning of DX split type air conditioning units (Owner Supplied) of different capacities (as per mentioned in schedule) complete in all respects, ready to operate. Including supply of supports, brackets, flexible duct connection, rubber isolator, flashing, gas charging, control wiring & power wiring (connection) in G.I. for external / PVC for internal from outdoor unit to indoor unit complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant.
a | Split Indoor / Outdoor Units
i | GF-FS-CENTRAL HALL/GF-CU-CENTRAL HALL | 8 | No. | 8000 | 64000 | 8000 | 64000 | 128000
2 | Supply, installation, testing and commissioning of refrigerant pipes (liquid + gas) with hangers and supports including 19mm thick expended rubber foam insulation, PVC tape wrapping + control wiring from indoor to outdoor including Gas charging if required and installation of branch distributor (supplied with units) complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant.
i | REF PIPE LIQUID | 220 | Rft | 900 | 198000 | 200 | 44000 | 242000
ii | REF PIPE GAS | 220 | Rft | 1380 | 303600 | 200 | 44000 | 347600
3 | Supply, Installation & Commissioning of U-PVC piping condensate drain including all cutting, fixing fitting, laying, cleaning and making good with 20mm thick Pre-moulded closed cell pipe insulation of 25-30kg/cum density, mean K value 0.035 , Fire class O as per BS-467 (Fire spread of flame) and propagation FSI<25 & SDI<30, as per ASTM E84, for drain water piping . The insulation material shall have water absorption less than 0.06% after 24 hours as per ASTM c209:1998. The joints shall be properly sealed with manufacturer recommended solution and tape on circumferential joints and on longitudinal joints. The insulation to be continuous as per good installation practice. The insulation shall be with Alupet foil protection. Rigid polymeric Cellular foam inserts of density 170-330 kg/m3, compression strength 20 kg/cm2 shall be used for pipe hangers and supports. complete in all respect as per drawings and specifications.
i | 3/4" Diameter | 50 | RFT | 450 | 22500 | 100 | 5000 | 27500
4 | MISCELLANEOUS
i | Supply, Installation & commissioning of brass tags for Equipment and system including all accessories complete in all respect. | 1 | Job | 5000 | 5000 | 5000 | 5000 | 10000
ii | Supply, Installation & commissioning of foundation for pipes and equipment including all noise and Vibration controller as per drawings and specifications. | 1 | Job | 60000 | 60000 | 20000 | 20000 | 80000
iii | Supply, Installation & commissioning of hangers and supports for pipes, ducts and equipment including all noise and Vibration controller roller type and others as per drawings and specifications. | 1 | Job | 38000 | 38000 | 15000 | 15000 | 53000
iv | Civil Work wall cutting, core cutting, cheiseling etc. as per drawings and as per instructions of Client / Consultant. | 1 | Job | 20000 | 20000 | 30000 | 30000 | 50000
v | Painting on equipment / Hangers, Supports, Pipe etc as per specifications. | 1 | Job | 10000 | 10000 | 10000 | 10000 | 20000
5 | Drawings
i | Shop Drawings and As-built Drawings as per specifications. | 1 | Job | 5000 | 5000 | 5000 | 5000 | 10000
6 | Testing & Commissioning
i | HVAC System. | 1 | Job | 0 | 0 | 30000 | 30000 | 30000
7 | Sundries
i | Supply, installtion and commissioning of items Listed or not listed in BOQ but required. (Contractor to specify the list of missing items if there is any.) | 1 | Job | 0 | 0 |  | 0 | 0
7 | MISCELLANEOUS Work
1 | Supply of Freon Cylinder for commissioning of units. | 1 | Nos | 67200 | 67200 | 0 | 0 | 67200
Grand Total for HVAC Works |  |  |  |  | 793300 |  | 272000 | 1065300