## Grand Summary
VISA FIT OUT PROJECT
10th FLOOR UNIT # 4, DOLMEN SKY TOWER - A, CLIFTON KARACHI.
RUNNING BILL NO 2
SR.NO. | DESCRIPTION |  | AMOUNT PAK Rs.
1 | ACMV WORKS | Rs. | 312640
2 | FSS WORKS | Rs. | 53800
| Total Work: Rs. |  | 366440

## HVAC
VISA FIT OUT PROJECT
10th FLOOR UNIT # 4, DOLMEN SKY TOWER - A, CLIFTON KARACHI.
ACMV WORKS - BILL OF QUANTITIES/ENGINEER'S ESTIMATE
Sr. No. | Description | Bill of Quantities |  |  |  | Running Bill No 1 |  | Running Bill No 2 |  | Running Bill No 3
|  | Unit | Qty | Rate | Amount Rs. | Billed Qty | Billed Amount | Billed Qty | Billed Amount | Billed Qty | Billed Amount
ACMV WORKS
1 | AC UNITS:
1.1 | Supply, installation, testing and commissioning of of ducted type fan coil unit & water cooled package unit complete in all respects, ready to operate including supply and installation of all accessories, lindaptor supports, hanger steel base, vibration isolators, including interconnecting power & control wiring (terminal connection) with inlet & outlet water pipe connections, drain connection, flexible rubber duct connection / connector etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
1.1 | DFCU-01 | No. | 1 | 0 | 0 |  |  |  | 0 |  | 0
1.2 | WCPU-01 | No. | 1 | 0 | 0 |  |  |  | 0 |  | 0
2 | VALVES & ACCESSORIES
2 | Supply & installation of valves & accessories for DFCU & WCPU with supports, hangers, flanges, gas kits, nut & bolts where it required, etc. complete in all respects as per specifications, drawings and as per instructions of consultant.
For DFCU:
2.1 | Ball Valve
a | 25mm dia | Nos. | 4 | 6500 | 26000 | 2 | 13000 |  | 0 |  | 0
2.2 | Strainers
a | 25mm dia | No. | 1 | 5900 | 5900 | 1 | 5900 |  | 0 |  | 0
2.3 | Balancing Valve (with self sealing measuring nipples)
a | 25mm dia | No. | 1 | 14500 | 14500 | 1 | 14500 |  | 0 |  | 0
2.4 | 2-Way Motorized Valve with Actuator (0-100% modulating)
a | 25mm dia | No. | 1 | 69000 | 69000 |  | 0 | 1 | 69000 |  | 0
2.5 | Digital Decorative Thermostat Controller (BMS Interfacable) with Duct Mounted Sensor | No. | 1 | 69500 | 69500 | 1 | 69500 |  | 0 |  | 0
2.6 | Control wiring from controller to sensors, motorized valve and Power wiring up to 5 meter radius | Job. | 1 | 65000 | 65000 | 1 | 65000 |  | 0 |  | 0
For WCPU:
2.1 | Ball Valve
a | 25mm dia | Nos. | 4 | 5800 | 23200 | 4 | 23200 |  | 0 |  | 0
[7 empty] | 0 |  | 0 |  | 0
2.2 | Strainers | [5 empty] | 0 |  | 0 |  | 0
a | 25mm dia | No. | 1 | 6900 | 6900 | 1 | 6900 |  | 0 |  | 0
[7 empty] | 0 |  | 0 |  | 0
2.3 | Balancing Valve (with self sealing measuring nipples) | [5 empty] | 0 |  | 0 |  | 0
a | 25mm dia | No. | 1 | 15000 | 15000 | 1 | 15000 |  | 0 |  | 0
[7 empty] | 0 |  | 0 |  | 0
2.4 | Flexible Pipe Connector | [5 empty] | 0 |  | 0 |  | 0
a | 25mm dia | Nos. | 2 | 7000 | 14000 | 2 | 14000 |  | 0 |  | 0
[7 empty] | 0 |  | 0 |  | 0
2.5 | 2-Way Motorized Valve with Actuator (0-100% modulating) | [5 empty] | 0 |  | 0 |  | 0
a | 25mm dia | No. | 1 | 165000 | 165000 | 1 | 165000 |  | 0 |  | 0
[7 empty] | 0 |  | 0 |  | 0
2.6 | Flow Switch | No. | 1 | 15000 | 15000 | 1 | 15000 |  | 0 |  | 0
[7 empty] | 0 |  | 0 |  | 0
2.7 | Digital Decorative Thermostat Controller (BMS Interfacable) with Duct Mounted Sensor | No. | 1 | 69500 | 69500 | 1 | 69500 |  | 0 |  | 0
[7 empty] | 0 |  | 0 |  | 0
2.8 | Control wiring from controller to sensors, motorized valve and Power wiring up to 5 meter radius | Job. | 1 | 38000 | 38000 | 1 | 38000 |  | 0 |  | 0
3 | VFD FOR EXISTING AHUs
3 | Supply, installation, testing and commissioning of Variable Frequency Drive (VFD) with controls complete in all respects as per specifications, drawings and as per instructions of consultant.
3.1 | VFD-01 (2.5 kw approx) | Nos. | 2 | 165000 | 330000 |  | 0 | 2 | 330000 |  | 0
4 | M.S PIPE:
4 | Supply & installation of SCH-40 M.S.(As per ASME & API standard, Heavy Quality with standard SCH 40 wall thickness) pipes & fitting for chilled & cooling water circulation system complete with bends, tees, unions, sockets, specials, lindaptor support, hangers & anchors, M.S. angle, U channel, roller support, bolts, rods, clamps, concrete fasteners etc as required to complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
4.1 | 25mm dia | Rm | 50 | 2600 | 130000 | 32 | 83200 | 7.9 | 20540 |  | 0
5 | PIPE INSULATION:
5 | Supply & installation of Pre Formed Polystyrene (Thermopore) insulation (32 kg/m3 density) for chilled water pipes only, bends, tees, unions, sockets, valves and on specials protected with Kraft paper, wrapped with 8oz Canvas cloth than paint with anti fungus paint etc, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
5.1 | 25mm dia | Rm | 25 | 1600 | 40000 |  | 0 | 18.3 | 29280 |  | 0
6 | VAV / CAV BOXES:
6 | Supply & installation of Pre Formed Polystyrene (Thermopore) insulation (32 kg/m3 density) for chilled water pipes only, bends, tees, unions, sockets, valves and on specials protected with Kraft paper, wrapped with 8oz Canvas cloth than paint with anti fungus paint etc, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
6.1 | VAV-01 | No. | 1 | 91000 | 91000 | 1 | 91000 |  | 0 |  | 0
6.2 | VAV-02 | No. | 1 | 107000 | 107000 | 1 | 107000 |  | 0 |  | 0
6.3 | VAV-03 | No. | 1 | 113000 | 113000 | 1 | 113000 |  | 0 |  | 0
6.4 | VAV-04 | No. | 1 | 118000 | 118000 | 1 | 118000 |  | 0 |  | 0
6.5 | VAV-05 | No. | 1 | 150000 | 150000 | 1 | 150000 |  | 0 |  | 0
6.6 | VAV-06 | No. | 1 | 150000 | 150000 | 1 | 150000 |  | 0 |  | 0
6.7 | CAV-01 | No. | 1 | 175000 | 175000 | 1 | 175000 |  | 0 |  | 0
6.8 | CAV-02 | No. | 1 | 175000 | 175000 | 1 | 175000 |  | 0 |  | 0
6.9 | CAV-03 | Nos. | 2 | 250000 | 500000 | 2 | 500000 |  | 0 |  | 0
6.1 | CAV-04 | No. | 1 | 400000 | 400000 | 1 | 400000 |  | 0 |  | 0
6.11 | CAV-05 | No. | 1 | 950000 | 950000 | 1 | 950000 |  | 0 |  | 0
6.12 | CAV-06 | No. | 1 | 950000 | 950000 | 1 | 950000 |  | 0 |  | 0
7 | VENTILATION FANS:
7 | Supply & installation of fans with accessories including supply & installation of vibration isolator, electrical / power wiring upto 5 meter + connection, flexible duct connection / connector, lindaptor type support & hangers etc, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
7.1 | TAF-01 | No. | 1 | 25000 | 25000 |  | 0 |  | 0 |  | 0
7.2 | RAF-01 | No. | 1 | 1380000 | 1380000 | 1 | 1380000 |  | 0 |  | 0
8 | G.I DUCT:
8 | Supply, fabrication & installation of machine made G.I sheet metal duct different sections supply, return, fresh & exhaust air including plenums, splitter dampers, guide vanes, flexible duct connector / connection, access door, transformation, plenums chambers, wooden frame, lindaptor type anchors supports & hangers etc, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqm | 430 | 5000 | 2150000 | 186.28 | 931400 | 103.98 | 519900 | 2.34 | 11700
9 | DUCT INSULATION:
9 | Supply & installation of adhesive 20mm thick rubber foam (XLPE) insulation with aluminum foil over supply & return duct, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqm | 410 | 5900 | 2419000 | 186.28 | 1099052 | 103.98 | 613482 | 2.34 | 13806
10 | S.S CLADDING:
10 | Supply, fabrication & installation of 26 SWG gauge SS-304 cladding (non false ceiling area only), complete in all respects ready to operate as per specification, drawings and as per instruction, approval of consultant. | Sqm | 65 | 13000 | 845000 |  | 0 | 118.5 | 1540500 | 19.58 | 254540
11 | SOUND LINER:
11 | Supply & installation of acoustical duct sound liner (adhesive 12mm thick) in supply air & return air duct etc, complete in all respects ready to operate as per drawings, specification and as per instruction of consultant. | Sqm | 30 | 4000 | 120000 |  | 0 | 41.5 | 166000 |  | 0
12 | AIR DEVICES
12 | Supply & installation of aluminum fabricated, powder coated grills, diffusers and registers etc for supply, return, exhaust & fresh air of different sizes (Grade A) wooden frame, lindaptor supports and other accessories etc, complete in all respects ready to operate as per drawings, specification and as per instruction of consultant.
12.1 | Supply & Return Air Register / Diffuser with Damper
a | 150mm x 150mm | Nos. | 2 | 3500 | 7000 |  | 0 | 3 | 10500 |  | 0
b | 450mm x 450mm | Nos. | 11 | 11500 | 126500 |  | 0 | 11 | 126500 |  | 0
c | 650mm x 250mm | Nos. | 3 | 8900 | 26700 |  | 0 | 3 | 26700 |  | 0
[9 empty] | 0 |  | 0
12.2 | S.S Wire Mesh with G.I Frame | [7 empty] | 0 |  | 0
a | 300mm x 150mm | Nos. | 2 | 5000 | 10000 |  | 0 |  | 0 |  | 0
b | 550mm x 150mm | No. | 1 | 4500 | 4500 |  | 0 |  | 0 |  | 0
c | 550mm x 200mm | No. | 1 | 7500 | 7500 |  | 0 |  | 0 |  | 0
a | 600mm x 150mm | No. | 1 | 12000 | 12000 |  | 0 |  | 0 |  | 0
b | 700mm x 200mm | No. | 1 | 13500 | 13500 |  | 0 |  | 0 |  | 0
c | 900mm x 350mm | Nos. | 2 | 18000 | 36000 |  | 0 | 1 | 18000 |  | 0
[9 empty] | 0 |  | 0
12.3 | Supply & Return Air Linear Slots 6,000 Series | [7 empty] | 0 |  | 0
a | 2 Slots of 20mm | Rm | 40 | 3790 | 151600 |  | 0 | 74 | 280460 | 8.6 | 32594
[7 empty] | 0 |  | 0 |  | 0
12.4 | Supply & Return Air Linear Bar Grill 4,000 Series | [5 empty] | 0 |  | 0 |  | 0
a | 65mm width | Rm | 10 | 4500 | 45000 |  | 0 | 8.4 | 37800 |  | 0
[7 empty] | 0 |  | 0 |  | 0
12.5 | Exhasut Air Disc Valve | [5 empty] | 0 |  | 0 |  | 0
a | 150mm dia | Nos. | 8 | 3500 | 28000 |  | 0 | 8 | 28000 |  | 0
b | 200mm dia | No. | 1 | 4200 | 4200 |  | 0 | 1 | 4200 |  | 0
13 | FLEXIBLE DUCT:
13 | Supply & installation of flexible duct including hangers, jubilee clamp complete in all respects as per specification, drawings & as per instruction of consultant.
13.1 | 150mm dia | Rm | 45 | 1800 | 81000 |  | 0 | 46 | 82800 |  | 0
14 | BUTTERFLY DAMPER:
14 | Supply & installation of butterfly damper for above flexible duct with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of consultant.
14.1 | 150mm dia | Nos. | 38 | 3200 | 121600 |  | 0 | 38 | 121600 |  | 0
15 | BACK DRAFT DAMPER:
15 | Supply and installation of Back Draft Damper framing in 16 SWG G.I sheet & auto gravity shutter in 26 SWG sheet, with gas kits, nut botls etc, complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant. | [7 empty] | 0 |  | 0
15.1 | 450mm x 250mm | Nos. | 2 | 7000 | 14000 |  | 0 | 2 | 14000 |  | 0
16 | VOLUME CONTROL DAMPER:
16 | Supply & installation of Volume Control Damper in 16 SWG G.I sheet metal with gas kits, nut bolts, etc, complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant.
16.1 | 550mm x 100mm | Nos. | 5 | 2500 | 12500 |  | 0 |  | 0 |  | 0
16.2 | 550mm x 150mm | No. | 1 | 5000 | 5000 |  | 0 |  | 0 |  | 0
16.3 | 600mm x 150mm | No. | 1 | 4500 | 4500 |  | 0 |  | 0 |  | 0
16.4 | 300mm x 150mm | No. | 1 | 2500 | 2500 |  | 0 |  | 0 |  | 0
16.5 | 900mm x 350mm | No. | 1 | 13000 | 13000 |  | 0 |  | 0 |  | 0
16.6 | 550mm x 200mm | No. | 1 | 6000 | 6000 |  | 0 |  | 0 |  | 0
16.7 | 900mm x 350mm | No. | 1 | 14000 | 14000 |  | 0 |  | 0 |  | 0
17 | DRAIN PIPE:
17 | Supply & installation of uPVC make class D SCH-40 pipe with 10mm thick expanded rubber foam insulation, PVC tape wrapping for condensate drain including lindaptor type support hangers, excavation, cutting, chiseling and making good complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
17.1 | 25mm dia | Rm | 20 | 990 | 19800 |  | 0 | 15 | 14850 |  | 0
18 | PAINTING & IDENTIFICATION:
18 | Painting & Identification work on chilled water pipes & exhaust duct, supports, hangers etc, complete in all respects with one coat of ICI make Red lead oxide primer & two coats of ICI make enamel paint etc, complete in all respects as per instruction of consultant. | Job. | 1 | 25000 | 25000 | 1 | 25000 |  | 0 |  | 0
19 | TESTING & BALANCING:
19 | Testing, balancing and commissioning of water & air side of the system (from independent agency) complete in all respects including flow measurement & balancing, temp, pressure, electrical data of related equipment etc, complete in all respects as per instruction of consultant. | Job. | 1 | 50000 | 50000 |  | 0 | 1 | 50000 |  | 0
20 | SHOP & AS BUILT DRAWING:
20 | Making of Shop drawings on Auto CAD 2016 with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment as per instruction of Consultant. | Job. | 1 | 25000 | 25000 | 1 | 25000 |  | 0 |  | 0
21 | SAFETY ITEMS
21 | Provision of PPEs for all M&P Contractor workforce with following while doing execution / construction: Cotton Dangree / Coverall color: Brown (Base price: 1600 Rs ) QTY = 15 nos. (min) Steel toe Shoes Jaguar / Color: Black (Base price: 1800 Rs ) QTY = 15 nos. (min) Safety Helmet Economical with "chin strap" / Color: Blue / White / Red (Base price: 500 Rs ) QTY = 15 nos. (min) | Job. | 1 |  | 0 |  | 0 |  | 0 |  | 0
| Grand Total Amount Rs. | [5 empty] | 7937152 |  | 4104112 |  | 312640

## Fire
VISA FIT OUT PROJECT
10th FLOOR UNIT # 4, DOLMEN SKY TOWER - A, CLIFTON KARACHI.
FIRE SUPPRESSION SERVICES - BILL OF QUANTITIES/ENGINEER'S ESTIMATE
Sr. No. | Description | Bill of Quantities |  |  |  | Running Bill No 1 |  | Running Bill No 2 |  | Running Bill No 3
|  | Unit | Qty | Rate | Amount Rs. | Billed Qty | Billed Amount | Billed Qty | Billed Amount | Billed Qty | Billed Amount
FSS WORKS
1 | MS PIPES:
1.1 | MS Sch-40 seamless pipes including all specials fittings UL listed & FM approved, threaded, welded joints, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, supports and hangers, sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
1.1 | Dia 25 mm (Threaded fitting) | Rm. | 110 | 2750 | 302500 | 110.3 | 303325 | 39.2 | 107800 |  | 0
1.2 | Dia 32 mm (Threaded fitting) | Rm. | 20 | 3500 | 70000 | 19.6 | 68600 |  | 0 |  | 0
1.3 | Dia 40 mm (Threaded fitting) | Rm. | 20 | 3990 | 79800 | 12.5 | 49875 | 3.7 | 14763 |  | 0
1.4 | Dia 50 mm (Threaded fitting) | Rm. | 30 | 5390 | 161700 | 19 | 102410 |  | 0 |  | 0
1.5 | Dia 65 mm (Welded joints fitting) | Rm. | 6 | 8094 | 48564 | 14.9 | 120600.6 |  | 0 |  | 0
1.6 | Dia 75 mm (Welded joints fitting) | Rm. | 15 | 10400 | 156000 | 18.3 | 190320 |  | 0 |  | 0
0
0
2 | SPRINKLER HEADS | [9 empty] | 0
[9 empty] | 0 |  | 0
2.1 | Sprinkler Upright type standard response K = 5.6 (Opening Temperature 68ºC) | Nos. | 2 | 2800 | 5600 | 11 | 30800 |  | 0 |  | 0
0
2.2 | Sprinkler Pendent type (concealed with face / Cover plate) K = 5.6 (Opening Temperature 57ºC) | Nos. | 49 | 2200 | 107800 | 53 | 116600 | 1 | 2200 |  | 0
0
[9 empty] | 0 |  | 0
3 | FIRE EXTINGUISHERS WITH FIXING ACCESSORIES | [9 empty] | 0
0
3.1 | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 2 | 17000 | 34000 |  | 0 |  | 0 | 2 | 34000
0
3.2 | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 2 | 9900 | 19800 |  | 0 |  | 0 | 2 | 19800
0
0
4 | GATE VALVES | [9 empty] | 0
4 | Isolation Gate valve with matching flanges. | [9 empty] | 0
4.1 | Size. 75 mm | No. | 1 | 35000 | 35000 |  | 0 |  | 0 |  | 0
[9 empty] | 0 |  | 0
[9 empty] | 0 |  | 0
5 | FIRE STOP MATERIAL: | [7 empty] | 0 |  | 0
5 | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1 | 75000 | 75000 | 1 | 75000 |  | 0 |  | 0
[9 empty] | 0 |  | 0
[9 empty] | 0 |  | 0
6 | NOVEC 1230: | [7 empty] | 0 |  | 0
6 | Supply & installation of MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant. | [7 empty] | 0 |  | 0
6.1 | Dia. 20 mm ( Threaded fitting ) | Rm. | 6 | 1470 | 8820 |  | 0 |  | 0 |  | 0
[9 empty] | 0 |  | 0
[9 empty] | 0 |  | 0
7 | CLEAN AGENT (FK-5-1-12 Stored In Cylinder - Ul Listed / Fm Approved) : | [7 empty] | 0 |  | 0
7 | Supply & installation of clean agent in engineered cylinders of FSS with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant. | [7 empty] | 0 |  | 0
7.1 | Clean Agent (FK-5-1-12, Fluoroketone) | KG. | 32 | 0 | 0 |  | 0 |  | 0 |  | 0
[9 empty] | 0 |  | 0
7.2 | Engineered cylinder with head valve, top plug adapter, siphon tube, pressure gauge, brackets and all other items, complete in all respect. | No. | 1 | 0 | 0 |  | 0 |  |  |  | 0
0
0
8 | SPRINKLER HEADS | [9 empty] | 0
8 | Supply & installation of nozzles with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant. | [7 empty] | 0 |  | 0
0
8.1 | Brass Discharge Nozzle - 360 Degrees discharge pattern | [9 empty] | 0
a | Size. 19 mm dia | No. | 1 | 0 | 0 |  | 0 |  | 0 |  | 0
0
[9 empty] | 0 |  | 0
9 | INPUT & OUTPUT DEVICES: | [9 empty] | 0
9 | Supply & installation of input and output devices for the clean agent suppression system (integrated with BMS) with wiring, controls & fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant | [9 empty] | 0
9.1 | Entinguishing Control Panel for the clean agent fire suppression system | No. | 1 | 0 | 0 |  | 0 |  |  |  | 0
9.2 | Photoelectric Smoke Detector | Nos. | 2 | 0 | 0 |  | 0 |  |  |  | 0
9.3 | 2 Wire Detector Base | Nos. | 2 | 0 | 0 |  | 0 |  |  |  | 0
9.4 | Manual Abort / Emergency Cut Off Switch | No. | 1 | 0 | 0 |  | 0 |  | 0 |  | 0
9.5 | Manual Release Switch - Single Action | No. | 1 | 0 | 0 |  | 0 |  |  |  | 0
9.6 | Horn / Strobe | No. | 1 | 0 | 0 |  | 0 |  |  |  | 0
9.7 | Alarm Bell | No. | 1 | 0 | 0 |  | 0 |  |  |  | 0
0
|  |  |  | Total - 09 | 0
[9 empty] | 0 |  | 0
10 | ACTUATION DEVICES: | [7 empty] | 0 |  | 0
10 | Supply & installation of actuation devices with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant. | [7 empty] | 0 |  | 0
10.1 | Solenoid Actuator for the specified cylinder size. | No. | 1 | 0 | 0 |  | 0 |  | 0 |  | 0
10.2 | Manual Control Head for manual actuation of cylinder with safety pull pin. | No. | 1 | 0 | 0 |  | 0 |  | 0 |  | 0
10.3 | Pressure Switch to indicated system discharge with an external manual reset button | No. | 1 | 0 | 0 |  | 0 |  | 0 |  | 0
10.4 | Low Pressure Switch to monitor the pressure within the cylinder. | No. | 1 | 0 | 0 |  | 0 |  | 0 |  | 0
[7 empty] | 0 |  | 0 |  | 0
[9 empty] | 0 |  | 0
11 | WIRING : | [7 empty] | 0 |  | 0
11 | Supply & installation of wiring of 2C, 1.5 Sq.mm fire resistant shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia G.I conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Job. | 1 | 0 | 0 |  | 0 |  | 0 |  | 0
0
0
12 | SHOP & AS BUILT DRAWING: | [9 empty] | 0
12 | Making of Shop drawings on Auto CAD 2018 and latest version with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects as per instruction of consultant. | Job. | 1 | 25000 | 25000 | 1 | 25000 |  | 0 |  | 0
[9 empty] | 0 |  | 0
0
13 | PAINTING & IDENTIFICATION: | [9 empty] | 0
13 | Painting, identification and tagging to the installations and equipments, complete in all respects as per instruction of consultant. | Job. | 1 | 25000 | 25000 | 1 | 25000 |  | 0 |  | 0
0
0
14 | FLUSHING: | [9 empty] | 0
14 | Flushing of entire fire pipe work according to (NFPA-13), complete in all respects as per instruction of consultant. | Job. | 1 | 25000 | 25000 | 1 | 25000 |  | 0 |  | 0
0
0
15 | TESTING & COMMISSIONING: | [9 empty] | 0
15 | Testing and commissioning of entire clean agent fire suppression system complete in all respects as per instruction of consultant. | Job. | 1 | 150000 | 150000 | 1 | 150000 |  | 0 |  | 0
0
0
| Grand Total Amount Rs. | [5 empty] | 1282530.6 |  | 124763 |  | 53800