## HVAC
Technical Submittal Register of HVAC
Sr.# | Description | BOQ No. | Submittal No. | Proposed date of submittal as per work schedule | Submission Date at AAA Site Office | Approval Date | Received at AAA site office | LOAM | Authorized Dealer | Submitted Brand | Sample | Status | Remarks
1 | Supports for HVAC ducting & Piping works |  | NICVD-HVAC-01 |  | 2024-10-07 | 2024-10-22 | 2024-10-24 | Norm | Unique Tools and Mill Store | NORM | Submitted | Approved
2 | Copper Piping For VRF System |  | NICVD-HVAC-02 |  | 2024-10-07 | 2024-10-22 | 2024-10-24 | Mueller USA | Crescent Corporation | Mueller | Submitted | Approved |  | Approved | 14
3 | Insulation for Copper Piping |  | NICVD-HVAC-03 |  | 2024-10-07 | 2024-10-22 | 2024-10-24 | Aeroflaex,Thailand | Katys | Aeroflex | Submitted | Approved |  | Not Submitted | 4
4 | UPVC Pipe & Fitting for Drain piping |  | NICVD-HVAC-04 |  | 2024-10-07 | 2024-10-22 | 2024-10-24 | AGM/KSA | Malik Corporation | AGM | Submitted | Approved |  | Resubmit | 1
5 | Insulation for UPVC Condensate Drain Piping |  | NICVD-HVAC-05 |  | 2024-10-07 | 2024-10-22 | 2024-10-24 | Superloan,Malaysia | Iqbal Sons | Superloan | Submitted | Approved
6 | G.I Sheet for Duct Works - Supply Air Duct & Exhaust Air Duct |  | NICVD-HVAC-06 |  | 2024-10-07 | 2024-10-22 | 2024-10-29 | International Steel Limited | Lokhandawala | International Steel Limited | Awaited | Approved | Provide Sample 12''x12'' size of each gauge with weight | Under Review | 0
7 | XLPE Insulation For Duct Works |  | NICVD-HVAC-07 |  | 2024-10-07 | 2024-10-22 | 2024-10-29 | AEROFOAM | Global Technologies | AEROFOAM | Submitted | Approved |  | Total | 19
8 | Duct Sound Linear - Thickness: 12 MM |  | NICVD-HVAC-08 |  | 2024-10-07 | 2024-10-22 | 2024-10-29 | Thermobreak |  | Thermobreak | Submitted | Approved
9 | Flexible Duct |  | NICVD-HVAC-09 |  | 2024-10-07 | 2024-10-22 | 2024-10-29 | Aero Duct,UAE Duct Mate,USA AFS,AFS | MM Steel Corporation Iqbal Sons Fakhri Brothers | Flexiva |  | Resubmit | Flexible Duct No Required for project
10 | Centrifugal Inline, Wall Mounted & Tube Axial |  | NICVD-HVAC-10 |  | directly submitted to contractor | 2024-11-20 | 2024-11-29 | Sodeca | Khursheed Engineering | Sodeca |  | Approved | Sodeca "Spain" is approved . RPM values exceeding the limit. Max alloowed 1600 RPM in the highlidhted fans.Weather proof canopy / cabnet required on RFEAF-01
11 | Centrifugal Inline, Wall Mounted & Tube Axial |  | NICVD-HVAC-10 (R1) |  | directly submitted to contractor | 2024-11-20 | 2024-11-29 | Sodeca | Khursheed Engineering | Sodeca |  | Approved | Fire rated motor and eweather proof canopy required Internal wiring and cabble fire resistent required
12 | Isolation Valves | [6 empty] | Emerson China | Crescent Corporation |  |  | Not Submitted | Requisition on Requisition form is pending
13 | aluminumfabricatedpowder coated exhaust & fresh Air louvers |  | NICVD-HVAC-12/13/14/15) |  | 2025-01-17 | 2025-01-25 |  | AIR GUIDE | AIR GUIDE |  |  | Approved
14 | Grills, Diffusers and Registers for supply air, return air, exhaust air&freshair |  | NICVD-HVAC-12/13/14/15) |  | 2025-01-17 | 2025-01-25 |  | AIR GUIDE | AIR GUIDE |  |  | Approved | Requisition on Requisition form is pending
15 | VolumeControl Damper in16SWG G.I | [6 empty] | AIR GUIDE STEEL CRAFT SHAN INDUSTRIES ENGATECH E.A.P AIR DEVICIES | M/S. AIR GUIDE M/S. STEEL CRAFT M/s. SHAN INDUSTIES M/S. ENGATECH INTERNATIONAL M/S. ENGINEERING AIR PRODUCTS |  |  | Not Submitted | VCD No Required for project
16 | Fire Damper | [6 empty] | AIR GUIDE STEEL CRAFT SHAN INDUSTRIES ENGATECH E.A.P AIR DEVICIES | M/S. AIR GUIDE M/S. STEEL CRAFT M/s. SHAN INDUSTIES M/S. ENGATECH INTERNATIONAL M/S. ENGINEERING AIR PRODUCTS |  |  | Not Submitted | FD No Required for project
17 | Motorized Damper | [6 empty] | AIR GUIDE STEEL CRAFT SHAN INDUSTRIES ENGATECH E.A.P AIR DEVICIES | M/S. AIR GUIDE M/S. STEEL CRAFT M/s. SHAN INDUSTIES M/S. ENGATECH INTERNATIONAL M/S. ENGINEERING AIR PRODUCTS |  |  | Not Submitted | MD No Required for project
OFM Items
1 | VRF/VRV air conditioning units withmultiple indoor evaporative units and Y Joints | 1-1.9 |  | 2024-11-10 |  |  |  | Gree,China Haier,China | DWP Technologies Haier | DWP | Not required | Approved | Requisition on Requisition form is pending
2 | single split units | 2.1-2.5 |  | 2024-11-10 |  |  |  | Gree,China Haier,China | DWP Technologies Haier | DWP | Not required | Approved | Requisition on Requisition form is pending