## Grand Summary
S.# | DESCRIPTION | SUPPLY (Rs.) | INSTALLATION (Rs.) | AMOUNT (Rs.)
1 | BOQ - 17TH FLOOR
2 | BOQ - 18TH FLOOR
3 | BOQ - 19TH FLOOR
Sub-Total (Rs.)
GST and SST taxes
Grand Total
Note: ● Contractor is advised to inform missing items (if any) in BOQ at time of submitting this tender. No escalation will be considered at time of execution of work. ● Owner can supply any material of Contractor scope at any stage and its cost will be completely deleted from Contractor scope without any kind of adjustment. ● Contractor should mark the selected brands and vendors in approved manufacturer list with submission of Tender Documents. ● Owner / Consultant have all the rights to select any brand / vendor from provided approved manufacturer list, Contractor shall not finalize any brand / vendor without written approval from consultant / owner.

## Sum-17F
S.# | DESCRIPTION | SUPPLY (Rs.) | INSTALLATION (Rs.) | AMOUNT (Rs.)
1 | SECTION - A FIRE SUPPRESSION SYSTEM
2 | SECTION - B ADDRESSABLE FIRE ALARM SYSTEM
3 | SECTION - C CCTV SYSTEM
4 | SECTION - D PUBLIC ADDRESS SYSTEM
Total Amount (Rs.)

## BoQ-17F
S.# | DESCRIPTION | BOQ QTY | UNIT | Verified QTY | SUPPLY |  | INSTALLATION |  | AMOUNT (Rs.) | Lead Time | Brand | Remarks
[5 empty] | RATE (Rs.) | AMOUNT (Rs.) | RATE (Rs.) | AMOUNT (Rs.)
SECTION - A FIRE SUPPRESSION SYSTEM
Supply, Installation, Testing & Commissioning of Fire Suppression System comprising of following equipments including all accessories required for the completion of the system in all respects
1 | FK 5-1-12 - 32Kg 5112 -(500 PSI)-HP SERIES ENGINEERED 75 LB. - S.S. RED COLOR CYL. ASSEMBLY FILLING RANGE 16.4(36) TO 34.4(76) KG 1-1/2" S.S .VALVE ASSEMBLY C/W TOP CAP ADAPTER, PRESSURE GAUGE W/GUARD, PRESSURE SWITCH GUARD & CYL. MOUNTING BRACKET Flow-Calc-New - Hydraulic Flow Calc for New Piping 1No. Caution Label-"When alarm sounds…" 1No. Caution Label-"Do not enter / Vacate Room…" 1No. Caution Label-"Operation of Manual Pull…" 1No. | 1 | Set
2 | Discharge Hose | 1 | No.
3 | Combined Fire & Extinguishing Control Panel with Battery Backup Features: Integral PSU (2.0 Amp), 4 x 20 LCD Display, Extinguishing Delay Timer (0-60 seconds), Flooding Time Programming, Optional 8 Way Relay, Alarm/Fault log (100 Events), Optional 8 Way Relay Output. | 1 | No.
4 | Conventional Smoke Detector with Base. | 4 | No.
5 | Conventional Fire Alarm Sounder with Flasher | 1 | No.
6 | Abort Switch | 1 | No.
7 | MS Sch-40 piping with fitting accessories, paint works and pressure testing of piping works | 1 | Job
8 | Programming, Testing & Commissioning of the complete system as per client's requirements with training sessions of maintenance personnel's along with consultant. | 1 | Job
Note: - Contractor shall provide complete technical literature for the quoted equipment for approval of Consultant before procurement. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY)
SECTION - B FIRE ALARM SYSTEM
Supply, Installation, Testing and Commissioning of following items for Addressable Fire Alarm System comprising of following equipments including all accessories required for the completion of the system in all respects. Cables shall be Fire retardant, Low Smoke, Zero Halogen and must comply BS 6387 standard Note: Thread rods cannot be installed directly to the ceiling. Any conduit required to be hanged shall be clamped with the Iron Girder using Type TR60. (Refer Details).
1 | Addressable Fire Alarm Control Panel of 4-loop having maximum 250 devices per loop. The FACP shall be self powered with built in 12V batteries for 24 Hrs backup with charging unit. It can be programmed using Windows based software for peripheral devices like display unit, printers etc. NOTE: 1) The Panel should have GSM Module to send alters to alteast 3 persons of Client choice. 2) The Panel should have dry contacts for ZCU fault and alarm status. 3) The Panel should be integrated with Building FA System. 4) The Panel should be integrated with Access Control System. 5) The Panel should be able to integrate with BACnet BMS system without any additional item cost. | 1 | No.
2 | Addressable Smoke Detectors incorporating an LED indication located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 74 | No.
3 | Addressable Multi Detectors incorporating an LED indication located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 4 | No.
4 | Addressable resetable Type Manual Call Point having a built in short circuit isolator and built in microprocessor to ensure a response time of max 1 second. It also incorporates an indication LED, flashed after pressing the button to acknowledge the activation and a key operation facility for testing purposes. | 8 | No.
5 | Addressable Type Indoor Loop Powered electronic sounder with flasher and minimum sound out put 89 dB at 1 meter with frequencies for variety of sounds as required. Souder shall be loop wired and loop signaled, built in short circuit isolator, configured via software. | 9 | No.
6 | I/O Relay for connectivity with diferent systems | 4 | No.
7 | Sounder Module with Battery Bank for integration with Building Fire Alarm System | 2 | No.
8 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job.
Note: 1) Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY)
SECTION - C CCTV SYSTEM (IP BASED)
Supply, Installation, Testing & Commissioning of following items for CCTV System (IP Based) including but not limited to the description given here under including all power and communication accessories, housings, mounting brackets, suspension rods etc. required for completion of the system. Note: Thread rods cannot be installed directly to the ceiling. Any conduit required to be hanged shall be clamped with the Iron Girder using Type TR60. (Refer Details).
1 | Surface/Recessed 2MP Ceiling mounted Mini Dome fixed type PoE I.P camera with day and night feature with 1080p resolution 1280 x 1024 @ 25/30fps pixels with live and recording quality of minimum 15 fps, Varifocal Lens 3.3-12mm, along with all mounting accessories complete in all respect. | 12 | No.
2 | Network Video Recorder (NVR) with 16 channel Video input. The NVR shall be equipped with LAN / WAN facility. NVR should have minimum 30 days storage capacity on 12 frame per second with 60 TB HDD or higher if required to cater 100% cameras, RW CD Drive. Complete with all connecting cords and accessories including SFP modules. | 1 | No.
3 | 12 Port PoE Switch to be installed in Comm. Room in racks with all mounting accessories. | 1 | No.
4 | 32" LED Color Screen to be installed in control Room in racks with all connecting cords and mounting stands. | 1 | No.
5 | Work stations (Core i7 Ultra Slim Desktop PC with Genuine Windows 10 Professional 64bit processor, 16GB ram, 4TB HDD, 4GB Graphics Card & DVD Writer) | 1 | No.
6 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
Note: 1) The supplier to confirm the storage requirement as per number of cameras, pixel resolutions, video compression and number of recording days. 2) The Bidder shall provide the complete Technical Literature for the system offered. 3) The given quantities are slightly higher then those on drawings. 4) All the IT Equipements shall be verified by the Client IT. Team before procurement
Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY)
SECTION - D PUBLIC ADDRESS SYSTEM
Supply, Installation, testing & commissioning of following items for Public Address System as described below including all accessories. Complete with mounting brackets, wiring, adapters etc.
1 | 300W - 2 Channel Power Amplifier with Voice Evacuation Manager operating at 220V, AC suitable for rack mounting incorporates two audio line level inputs: a Music input and a priority call input. A built-in relay switches the amplifier from the music input of priority call input. | 1 | No.
2 | 6W Recessed Ceiling Speakers with Fire Rated (EN-54) back boxes intended for high quality speech and music reproduction with sealed enclosure protective against moisture and dust. The speaker shall have output power adjustments for full, half and quarter power outputs, including back boxes if required. | 23 | No.
3 | Table Mounted Gooseneck Microphone | 1 | No.
4 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job.
Note: - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. - The Bidder shall provide the complete Technical Literature for the system offered.
Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY)

## Sum-18F
S.# | DESCRIPTION | SUPPLY (Rs.) | INSTALLATION (Rs.) | AMOUNT (Rs.)
1 | SECTION - A FIRE SUPPRESSION SYSTEM
2 | SECTION - B ADDRESSABLE FIRE ALARM SYSTEM
3 | SECTION - C CCTV SYSTEM
4 | SECTION - D PUBLIC ADDRESS SYSTEM
Total Amount (Rs.)

## BoQ-18F
S.# | DESCRIPTION | QTY | UNIT | Verified QTY | SUPPLY |  | INSTALLATION |  | AMOUNT (Rs.)
[5 empty] | RATE (Rs.) | AMOUNT (Rs.) | RATE (Rs.) | AMOUNT (Rs.)
SECTION - A FIRE SUPPRESSION SYSTEM
Supply, Installation, Testing & Commissioning of Fire Suppression System comprising of following equipments including all accessories required for the completion of the system in all respects
1 | FK 5-1-12 - 32Kg 5112 -(500 PSI)-HP SERIES ENGINEERED 75 LB. - S.S. RED COLOR CYL. ASSEMBLY FILLING RANGE 16.4(36) TO 34.4(76) KG 1-1/2" S.S .VALVE ASSEMBLY C/W TOP CAP ADAPTER, PRESSURE GAUGE W/GUARD, PRESSURE SWITCH GUARD & CYL. MOUNTING BRACKET Flow-Calc-New - Hydraulic Flow Calc for New Piping 1No. Caution Label-"When alarm sounds…" 1No. Caution Label-"Do not enter / Vacate Room…" 1No. Caution Label-"Operation of Manual Pull…" 1No. | 1 | Set
2 | Discharge Hose | 1 | No.
3 | Combined Fire & Extinguishing Control Panel with Battery Backup Features: Integral PSU (2.0 Amp), 4 x 20 LCD Display, Extinguishing Delay Timer (0-60 seconds), Flooding Time Programming, Optional 8 Way Relay, Alarm/Fault log (100 Events), Optional 8 Way Relay Output. | 1 | No.
4 | Conventional Smoke Detector with Base. | 4 | No.
5 | Conventional Fire Alarm Sounder with Flasher | 1 | No.
6 | Abort Switch | 1 | No.
7 | MS Sch-40 piping with fitting accessories, paint works and pressure testing of piping works | 1 | Job
8 | Programming, Testing & Commissioning of the complete system as per client's requirements with training sessions of maintenance personnel's along with consultant. | 1 | Job
Note: - Contractor shall provide complete technical literature for the quoted equipment for approval of Consultant before procurement. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY)
SECTION - B FIRE ALARM SYSTEM
Supply, Installation, Testing and Commissioning of following items for Addressable Fire Alarm System comprising of following equipments including all accessories required for the completion of the system in all respects. Cables shall be Fire retardant, Low Smoke, Zero Halogen and must comply BS 6387 standard Note: Thread rods cannot be installed directly to the ceiling. Any conduit required to be hanged shall be clamped with the Iron Girder using Type TR60. (Refer Details).
1 | Fire Repeater Panel Loop Powered along with termination of all Control / Signal cables complete in all aspects. Panel to have all loops marked in distinguishable colors with individual LED's | 1 | No.
2 | Addressable Smoke Detectors incorporating an LED indication located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 65 | No.
3 | Addressable Multi Detectors incorporating an LED indication located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 3 | No.
4 | Addressable resetable Type Manual Call Point having a built in short circuit isolator and built in microprocessor to ensure a response time of max 1 second. It also incorporates an indication LED, flashed after pressing the button to acknowledge the activation and a key operation facility for testing purposes. | 6 | No.
5 | Addressable Type Indoor Loop Powered electronic sounder with flasher and minimum sound out put 89 dB at 1 meter with frequencies for variety of sounds as required. Souder shall be loop wired and loop signaled, built in short circuit isolator, configured via software. | 7 | No.
6 | I/O Relay for connectivity with diferent systems | 4 | No.
7 | Sounder Module with Battery Bank for integration with Building Fire Alarm System | 2 | No.
8 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job.
Note: 1) Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY)
SECTION - C CCTV SYSTEM (IP BASED)
Supply, Installation, Testing & Commissioning of following items for CCTV System (IP Based) including but not limited to the description given here under including all power and communication accessories, housings, mounting brackets, suspension rods etc. required for completion of the system. Note: Thread rods cannot be installed directly to the ceiling. Any conduit required to be hanged shall be clamped with the Iron Girder using Type TR60. (Refer Details).
1 | Surface/Recessed 2MP Ceiling mounted Mini Dome fixed type PoE I.P camera with day and night feature with 1080p resolution 1280 x 1024 @ 25/30fps pixels with live and recording quality of minimum 15 fps, Varifocal Lens 3.3-12mm, along with all mounting accessories complete in all respect. | 12 | No.
2 | Network Video Recorder (NVR) with 16 channel Video input. The NVR shall be equipped with LAN / WAN facility. NVR should have minimum 30 days storage capacity on 12 frame per second with 60 TB HDD or higher if required to cater 100% cameras, RW CD Drive. Complete with all connecting cords and accessories including SFP modules. | 1 | No.
3 | 12 Port PoE Switch to be installed in Comm. Room in racks with all mounting accessories. | 1 | No.
4 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
Note: 1) The supplier to confirm the storage requirement as per number of cameras, pixel resolutions, video compression and number of recording days. 2) The Bidder shall provide the complete Technical Literature for the system offered. 3) The given quantities are slightly higher then those on drawings. 4) All the IT Equipements shall be verified by the Client IT. Team before procurement
Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY)
SECTION - D PUBLIC ADDRESS SYSTEM
Supply, Installation, testing & commissioning of following items for Public Address System as described below including all accessories. Complete with mounting brackets, wiring, adapters etc.
1 | 6W Recessed Ceiling Speakers with Fire Rated (EN-54) back boxes intended for high quality speech and music reproduction with sealed enclosure protective against moisture and dust. The speaker shall have output power adjustments for full, half and quarter power outputs, including back boxes if required. | 21 | No.
2 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job.
Note: - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. - The Bidder shall provide the complete Technical Literature for the system offered.
Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY)

## Sum-19F
S.# | DESCRIPTION | SUPPLY (Rs.) | INSTALLATION (Rs.) | AMOUNT (Rs.)
1 | SECTION - A FIRE SUPPRESSION SYSTEM
2 | SECTION - B ADDRESSABLE FIRE ALARM SYSTEM
3 | SECTION - C CCTV SYSTEM
4 | SECTION - D PUBLIC ADDRESS SYSTEM
Total Amount (Rs.)

## BoQ-19F
S.# | DESCRIPTION | QTY | UNIT | Verified QTY | SUPPLY |  | INSTALLATION |  | AMOUNT (Rs.)
[5 empty] | RATE (Rs.) | AMOUNT (Rs.) | RATE (Rs.) | AMOUNT (Rs.)
SECTION - A FIRE SUPPRESSION SYSTEM
Supply, Installation, Testing & Commissioning of Fire Suppression System comprising of following equipments including all accessories required for the completion of the system in all respects
1 | FK 5-1-12 - 32Kg 5112 -(500 PSI)-HP SERIES ENGINEERED 75 LB. - S.S. RED COLOR CYL. ASSEMBLY FILLING RANGE 16.4(36) TO 34.4(76) KG 1-1/2" S.S .VALVE ASSEMBLY C/W TOP CAP ADAPTER, PRESSURE GAUGE W/GUARD, PRESSURE SWITCH GUARD & CYL. MOUNTING BRACKET Flow-Calc-New - Hydraulic Flow Calc for New Piping 1No. Caution Label-"When alarm sounds…" 1No. Caution Label-"Do not enter / Vacate Room…" 1No. Caution Label-"Operation of Manual Pull…" 1No. | 1 | Set
2 | Discharge Hose | 1 | No.
3 | Combined Fire & Extinguishing Control Panel with Battery Backup Features: Integral PSU (2.0 Amp), 4 x 20 LCD Display, Extinguishing Delay Timer (0-60 seconds), Flooding Time Programming, Optional 8 Way Relay, Alarm/Fault log (100 Events), Optional 8 Way Relay Output. | 1 | No.
4 | Conventional Smoke Detector with Base. | 4 | No.
5 | Conventional Fire Alarm Sounder with Flasher | 1 | No.
6 | Abort Switch | 1 | No.
7 | MS Sch-40 piping with fitting accessories, paint works and pressure testing of piping works | 1 | Job
8 | Programming, Testing & Commissioning of the complete system as per client's requirements with training sessions of maintenance personnel's along with consultant. | 1 | Job
Note: - Contractor shall provide complete technical literature for the quoted equipment for approval of Consultant before procurement. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY)
SECTION - B FIRE ALARM SYSTEM
Supply, Installation, Testing and Commissioning of following items for Addressable Fire Alarm System comprising of following equipments including all accessories required for the completion of the system in all respects. Cables shall be Fire retardant, Low Smoke, Zero Halogen and must comply BS 6387 standard Note: Thread rods cannot be installed directly to the ceiling. Any conduit required to be hanged shall be clamped with the Iron Girder using Type TR60. (Refer Details).
1 | Loop card module in existing fire alarm panel installed at 25th floor to integrate devices at 19th floor. | 1 | No.
2 | Fire Repeater Panel Loop Powered along with termination of all Control / Signal cables complete in all aspects. Panel to have all loops marked in distinguishable colors with individual LED's | 1 | No.
3 | Addressable Smoke Detectors incorporating an LED indication located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 59 | No.
4 | Addressable Multi Detectors incorporating an LED indication located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 1 | No.
5 | Addressable resetable Type Manual Call Point having a built in short circuit isolator and built in microprocessor to ensure a response time of max 1 second. It also incorporates an indication LED, flashed after pressing the button to acknowledge the activation and a key operation facility for testing purposes. | 8 | No.
6 | Addressable Type Indoor Loop Powered electronic sounder with flasher and minimum sound out put 89 dB at 1 meter with frequencies for variety of sounds as required. Souder shall be loop wired and loop signaled, built in short circuit isolator, configured via software. | 9 | No.
7 | I/O Relay for connectivity with diferent systems | 4 | No.
8 | Sounder Module with Battery Bank for integration with Building Fire Alarm System | 2 | No.
9 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job.
Note: 1) Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY)
SECTION - C CCTV SYSTEM (IP BASED)
Supply, Installation, Testing & Commissioning of following items for CCTV System (IP Based) including but not limited to the description given here under including all power and communication accessories, housings, mounting brackets, suspension rods etc. required for completion of the system. Note: Thread rods cannot be installed directly to the ceiling. Any conduit required to be hanged shall be clamped with the Iron Girder using Type TR60. (Refer Details).
1 | Surface/Recessed 2MP Ceiling mounted Mini Dome fixed type PoE I.P camera with day and night feature with 1080p resolution 1280 x 1024 @ 25/30fps pixels with live and recording quality of minimum 15 fps, Varifocal Lens 3.3-12mm, along with all mounting accessories complete in all respect. | 12 | No.
2 | Network Video Recorder (NVR) with 16 channel Video input. The NVR shall be equipped with LAN / WAN facility. NVR should have minimum 30 days storage capacity on 12 frame per second with 60 TB HDD or higher if required to cater 100% cameras, RW CD Drive. Complete with all connecting cords and accessories including SFP modules. | 1 | No.
3 | 12 Port PoE Switch to be installed in Comm. Room in racks with all mounting accessories. | 1 | No.
4 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
5 | Allow for any other item required for completion of system not covered in BOQ or specifications / drawings in accordance with the same standards and brands shown and approved by consultant. All such items shall be covered in this item but complete description, item rates, quantity required and brands shall be mentioned separately and to be attached with the BOQ. | 1 | Job
Note: 1) The supplier to confirm the storage requirement as per number of cameras, pixel resolutions, video compression and number of recording days. 2) The Bidder shall provide the complete Technical Literature for the system offered. 3) The given quantities are slightly higher then those on drawings. 4) All the IT Equipements shall be verified by the Client IT. Team before procurement
Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY)
SECTION - D PUBLIC ADDRESS SYSTEM
Supply, Installation, testing & commissioning of following items for Public Address System as described below including all accessories. Complete with mounting brackets, wiring, adapters etc.
1 | 200W - 2 Channel Power Amplifier to be integrated with existing evacuation manager at 25th floor, operating at 220V, AC suitable for rack mounting incorporates two audio line level inputs: a Music input and a priority call input. A built-in relay switches the amplifier from the music input of priority call input. | 1 | No.
2 | 6W Recessed type Speakers intended for high quality speech and music reproduction with sealed enclosure protective against moisture and dust. The speaker shall have output power adjustments for full, half and quarter power outputs, including back boxes if required. | 24 | No.
3 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job.
Note: - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. - The Bidder shall provide the complete Technical Literature for the system offered.
Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY)