## Summary
M/S Bank Al-Falah Limited
Head Office I.I Chundriger Road Karachi
Overhauling, Repairing & Replacement |  |  |  | 2024-03-06
of Air Handling Units
RUNNING BILL NO 1
S.No | Description | Material Amount | Labour Amount | Total Amount
1 | Air Handling Unit - 3rd Floor (A/B) | 1319000 | 338000 | 1657000
2 | Chillers (Rooftop Plantroom) | 10390000 | 1790000 | 12180000
3 | Cooling Towers (Rooftop) | 15647000 | 1513000 | 17160000
| SubTotal Amount | 27356000 | 3641000 | 30997000
| Discount 05% | 1367800 | 182050 | 1549850
| Total Amount after Discount | 25988200 | 3458950 | 29447150
| Claimed 30% | 7796460 | 1037685 | 8834145
| SST 13% | 0 | 134899.05 | 134899.05
| Total After SST | 7796460 | 1172584.05 | 8969044.05
For Pioneer Services
PIONEER SERVICES

## Air Handling Unit
BOQ OF OVERHAULING, AND REPAIRING OF AIR HANDLING UNITS (AHU) 3rd Floor (A/B) BA BUILDING KARACHI
S.NO | DESCRIPTION | Qty | Unit | Material Rate | Labour Rate | Material Amount | Labour Amount | Total Amount
1 | Removal of existing isolator including supply and installation of new newpron isolators according AHU unit weight. | 1 | Job | 50000 | 10000 | 50000 | 10000 | 60000
2 | Metal structure of AHU such as M.s channel foundation floor columns and other supports rusted part to be replaced with new and paint primer 2 coat and epoxy 2 coat complete in all respect. | 1 | job | 65000 | 25000 | 65000 | 25000 | 90000
3 | Overhauling of AHU motor ball bearing replaced with new (Make SKF) including setting of motor foundation repaired if required and fix belt guard properly. | 1 | job | 65000 | 25000 | 65000 | 25000 | 90000
4 | AHU blower repaire or replaced including balancing of blower and shaft polish and alignment, replace pillow block bearing with new (make SKF) including provide grease niple for lubrication. (And test with grease gun). | 1 | job | 130000 | 30000 | 130000 | 30000 | 160000
5 | Supply and installation of Water proof light for enternal area AHU of approx 40 watt. | 1 | job | 20000 | 3000 | 20000 | 3000 | 23000
6 | AHU Chilled water coil channel frame around the coil clean with rust and dust and vanished with epoxy paint as required | 1 | job | 25000 | 15000 | 25000 | 15000 | 40000
7 | Descaling of AHU chilled water coil complete in all respect | 1 | job | 35000 | 15000 | 35000 | 15000 | 50000
8 | AHU Blower including louvor and blower housing paint with 2 coat primer & 2 coat epoxy complete in all respect. | 1 | job | 30000 | 10000 | 30000 | 10000 | 40000
9 | Removal of existing insulation from inside the AHU including supply and installation of aluminum faced EPDM foam insulation complete in all respect. | 1 | job | 340000 | 50000 | 340000 | 50000 | 390000
10 | Supply and installation of flexible duct connector in AHU room including replaced fiber glass insulation in AHU room including supply and installation of canvas cloth with anti fungus paint . | 1 | job | 95000 | 25000 | 95000 | 25000 | 120000
11 | Cleaning / paint AHU from outer area with primer and finished with oil paint. | 1 | job | 90000 | 30000 | 90000 | 30000 | 120000
12 | Cleaning / descalling of chilled water line, Gate valve Globe valve, strainer motorized valve complete in all respect. | 1 | job | 20000 | 15000 | 20000 | 15000 | 35000
13 | Removal of existing Gate valve including supply and isntallation of Gate valve as per AHU line size (make HATTERSLEY OR GALA) with flanges, nut bolt gasket, insulation, fabric, anti fungus paint complete in all respect. | 2 | Nos | 67000 | 10000 | 134000 | 20000 | 154000
14 | Chilled water supply / return line damaged insulation repleced with new including AHU room all chilled water line fix new canvas cloth and anti fungus paint complete in all respect. | 1 | job | 45000 | 15000 | 45000 | 15000 | 60000
15 | AHU exisitng V-belt replaced with new (Make: Continental) | 3 | Set | 15000 | 5000 | 45000 | 15000 | 60000
16 | Supply & installation of filter frame & aluminum filter complete in all respect. | 1 | job | 80000 | 20000 | 80000 | 20000 | 100000
17 | Door hinges & lock replaced with new if required | 1 | job | 10000 | 5000 | 10000 | 5000 | 15000
18 | Exisitng condensate Drain pipe replaced with new UPVC 1.5'' dia including U-trap and insulation complete in all respect. | 1 | job | 10000 | 5000 | 10000 | 5000 | 15000
19 | Supply of SS Nut, Bolts, Washers, Screws & Rivits | 1 | job | 30000 | 5000 | 30000 | 5000 | 35000
Sub Total Amount Rs | [5 empty] | 1319000 | 338000 | 1657000
Discount 5% | [5 empty] | 65950 | 16900 | 82850
Total After Discount | [5 empty] | 1253050 | 321100 | 1574150
Add SST 13% | [5 empty] | 0 | 41743 | 41743
Total After Discount | [5 empty] | 1253050 | 362843 | 1615893

## Fresh Air Unit
5TH FLOOR FRESH AIR UNIT
S.NO | DESCRIPTION | Qty | Unit | Per Unit Amount | Total Amount
1 | Evaporator Coil descaling internal and external | 1 | Job | 50000 | 50000
2 | globe valve,moterized valve & strainer descalling of chilled water line | 1 | job | 40000 | 40000
3 | Gate valve 2.5''old valve removing and new valve installation make HATTERSLEY OR GALA with flenges EPS thermocol insulation,fabric,anti fungus paint with almunium cladding . | 2 | Nos | 55000 | 110000
4 | Replacement of motor bearing, Make SKF & motor foundation & belt guard safety cover | 1 | job | 80000 | 80000
5 | AHU belt replacement make continental | 1 | job | 25000 | 25000
6 | Chilled water line supply & return aslo anti fungus paint & another paint with EPS thermocol insulation. | 1 | job | 50000 | 50000
7 | Drain pipe UPVC size 1.5'' | 1 | job | 20000 | 20000
8 | FAHU room oil base mate finish NIPPON paint. | 1 | job | 70000 | 70000
9 | supply & installation of complete filter frame,bag filter & alluminium air filter | 1 | job | 155000 | 155000
10 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 50000 | 50000
Sub Total Amount Rs |  |  |  |  | 650000
Discount 5% |  |  |  |  | 32500
Total After Discount |  |  |  |  | 617500

## Fan Coil Unit (Elevator n BMS)
FAN COIL UNITS OF ELEVATOR & BMS ROOM - 5TH FLOOR (TOTAL 04 NOS)
S.NO | DESCRIPTION | Qty | Unit | Per Unit Amount | Total Amount
1 | Evaporator Coil descaling internal and external with epoxy paint. | 4 | Nos | 15000 | 60000
2 | supply & installation of alluminium air filter | 8 | Nos | 15000 | 120000
3 | Replacement of motor bearing, Make SKF | 8 | Nos | 15000 | 120000
4 | Chilled water line supply & return also anti fungus paint & another paint with EPS thermocol insulation. | 4 | job | 15000 | 60000
5 | BMS room oil base mate finish NIPPON paint. | 1 | job | 90000 | 90000
6 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 40000 | 40000
Sub Total Amount Rs |  |  |  |  | 490000
Discount 5% |  |  |  |  | 24500
Total After Discount |  |  |  |  | 465500

## Chillers
BOQ OF REPAIRING AND REPLACEMENT AND MAINTENANCE WORKS OF CHILLERS AND COOLING TOWERS OVERHAULING OF BA BUILDING KARACHI
S.NO | DESCRIPTION | Qty | Unit | Material Rate | Labour Rate | Material Amount | Labour Amount | Total Amount
CHILLERS (ROOFTOP PLANT ROOM)
1 | 03 Chillers, 06Nos circuit of Botzer Compressors, Existing Oil removed and supply and re-fill up new Oil (BSE170) Germany 210 Ltr including repaired of leakages, replacement of dryer core & dryer, top-up Freon complete in respect. | 6 | Nos | 1195000 | 215000 | 7170000 | 1290000 | 8460000
2 | Chiller / compressor foundation & heat exchanger cleaning from duct & rust and painting 2 coat of primer and 2 coat of epoxy. | 6 | Nos | 20000 | 5000 | 120000 | 30000 | 150000
3 | Providing and installation of Stainer 12" dia for main Condenssor water with flange, nut bolt, gaskte etc complete in all respect Make HATTERSLEY OR GALA | 0 | Nos | 0 | 0 | 0 | 0 | 0
4 | Removal of existing 8" dia gate valve including supply / installation of 8" dia Gate valve with related fittings inluding insulation and cladding. make HATTERSLEY OR GALA | 2 | Nos | 250000 | 30000 | 500000 | 60000 | 560000
5 | Primary / Secondary Chilled and condenser water pumps ball bearings (Make: SKF) Mechanical Seal (Jhon Crane) Pump shaft coupler (imported) replace with new including related work complete in all respect | 10 | Nos | 215000 | 30000 | 2150000 | 300000 | 2450000
6 | Supply and installation of Automatic Air Vent Brass 1" with related fittings for chilled water system make HATTERSLEY | 4 | Nos | 15000 | 5000 | 60000 | 20000 | 80000
7 | Supply and installation of booster pumps (a set of two pumps) for cooling tower and chilled water system with 2Hp motor and VFD drive and related material | 0 | Set |  | 0 | 0 | 0 | 0
8 | Existing Booster Pump Overhauling (Optional) | 2 | Job | 30000 | 5000 | 60000 | 10000 | 70000
9 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | Job | 50000 | 10000 | 50000 | 10000 | 60000
10 | Water cooled Chillers Conddenssor descaling with chemical and brushing complete in all respect. | 6 | Nos | 40000 | 10000 | 240000 | 60000 | 300000
11 | Cleaning and descaling of Condenssor water header 12" dia with related material complete in all respect (04 Nos Header) | 1 | Job | 40000 | 10000 | 40000 | 10000 | 50000
Sub Total Amount Rs | [5 empty] | 10390000 | 1790000 | 12180000
Discount 5% | [5 empty] | 519500 | 89500 | 609000
Total After Discount | [5 empty] | 9870500 | 1700500 | 11571000
Add SST 13% | [5 empty] | 0 | 221065 | 221065
Total After Discount | [5 empty] | 9870500 | 1921565 | 11792065

## Cooling Towers
S.NO | DESCRIPTION | Qty | Unit | Material Rate | Labour Rate | Material Amount | Labour Amount | Total Amount
COOLING TOWERS (ROOFTOP)
1 | Dismantle of cooling tower structure frame and other metal accessories removed & galvanized hot dipped (90-110 Micron) and re-installed in all respect. | 3 | Nos | 650000 | 100000 | 1950000 | 300000 | 2250000
2 | Overhauling of cooling tower gear box / motor replaced existing ball bearing with new and provide grease nipple for lubricant complete in all respect. | 6 | Nos | 120000 | 30000 | 720000 | 180000 | 900000
3 | Providing and installation of New Fan fiber blade, New hub in aluminum material with alignment of gear box. | 6 | Nos | 160000 | 15000 | 960000 | 90000 | 1050000
4 | Upper hot water distribution basin with new showering box fiber material need & lower cool basin & fan stack frame & metal fan guard replaced with fiber coating 3 layer apply & fiber material minor repairing required. | 12 | Nos | 18000 | 5000 | 216000 | 60000 | 276000
5 | Replacement of Complete new PVC fills (1150x3= Total 3450 Fills in 3 CT) with new fills foundation fiber metarial & louvers required as per approved sample. | 3 | Nos | 2200000 | 100000 | 6600000 | 300000 | 6900000
6 | Hydroplast showering pipe fittings joints leakage repairing with fiber coating 3 layer apply | 1 | Job | 80000 | 20000 | 80000 | 20000 | 100000
7 | Hydroplast Butterfly valve 4" replaced with flange | 12 | Nos | 35000 | 8000 | 420000 | 96000 | 516000
8 | Float ball valve stainless steel 1.5" need to be change. | 3 | Nos | 23000 | 5000 | 69000 | 15000 | 84000
9 | Gate valve brass 2" need to be change make HATTERSLEY OR GALA. | 9 | Nos | 18000 | 5000 | 162000 | 45000 | 207000
10 | Schneider Motorized Butterfly valve 8" Outlet side need to be change with flenges. | 3 | Nos | 630000 | 30000 | 1890000 | 90000 | 1980000
11 | Schneider Motorized Butterfly valve 6" Inlet side need to be change with flenges. | 3 | Nos | 430000 | 30000 | 1290000 | 90000 | 1380000
12 | Bitumen paint with enamel paint (GOBIS) for Cooling tower foundation steel beams /girders outside area walk way platform and complete m/s pipe with pipe foundation. | 3500 | Sft. | 300 | 50 | 1050000 | 175000 | 1225000
13 | Harnessing / Dressing of Electrical wires proper dress up upvc pipe fitting. | 1 | Job | 50000 | 2000 | 50000 | 2000 | 52000
14 | Nut Bolts, Washers, Screws & Rivits Need Stainless Steel required . | 1 | Job | 150000 | 30000 | 150000 | 30000 | 180000
15 | Cooling towers Pipeline header inlet & outlet 12'' Washing required. | 4 | Job | 10000 | 5000 | 40000 | 20000 | 60000
Sub Total Amount Rs | [5 empty] | 15647000 | 1513000 | 17160000
Discount 5% | [5 empty] | 782350 | 75650 | 858000
Total After Discount | [5 empty] | 14864650 | 1437350 | 16302000
Add SST 13% | [5 empty] | 0 | 186855.5 | 186855.5
Total After Discount | [5 empty] | 14864650 | 1624205.5 | 16488855.5