## Summary
AMRELI STEEL LIMITED
10th FLOOR, DOLMEN SKY TOWER, CLIFTON KARACHI.
GRAND SUMMARY OF COST
SR.NO. | DESCRIPTION |  | AMOUNT PAK Rs.
1 | ACMV WORKS | Rs. | 13213500
| Discount | Rs. | 2510565
| Net Amount |  | 10702935
2 | FSS WORKS | Rs. | 1158450
| Total Work: Rs. |  | 11861385

## HVAC
Bill of Quantities
ACMV WORKS
Amreli Steel Limited | [7 empty] | Rev.01
10th Floor, Dolmen Sky Tower, Karachi | [7 empty] | Date: 02-11-2022
S.NO. | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR |  | TOTAL
|  |  |  | RATE | AMOUNT | RATE | AMOUNT | AMOUNT Rs.
All works shall be completed, tested and commissioned as per
drawings, specifications and as per instruction of Consultant
1 | Supply, installation, testing and commissioning of of chilled water
ducted fan coil unit & cooling water - water cooled package unit
including supply and installation of all fixing accessories, lindaptor
support, hanger steel base, vibration isolators, including
interconnecting power & control wiring (terminal connection) with
inlet & outlet pipe connections, drain connection, flexible rubber duct
connection / connector etc. complete in all respects ready to operate
as per schedule, specification, drawings and as per instruction of
consultant.
1.1 | DFCU-01 | No. | 1 |  | 0 | 18000 | 18000 | 18000
1.2 | WCPU-01 | No. | 1 |  | 0 | 18000 | 18000 | 18000
2 | Supply, installation, testing and commissioning of of VAV Boxes as
per mentioned in schedule with digital thermostat controller, pressure
sensor, control wiring, including supply & installation of flexible duct
connector / connection, electrical connection, lindaptor supports &
hangers complete in all respects ready to operate as per drawings,
specification, instruction and approval of Consultant.
2.1 | VAV-01 | No. | 1 | 271500 | 271500 | 15000 | 15000 | 286500
2.2 | VAV-02 | Nos. | 2 | 271500 | 543000 | 15000 | 30000 | 573000
2.3 | VAV-03 | No. | 1 | 271500 | 271500 | 15000 | 15000 | 286500
2.4 | VAV-04 | No. | 1 | 271500 | 271500 | 15000 | 15000 | 286500
2.5 | VAV-05 | Nos. | 3 | 271500 | 814500 | 15000 | 45000 | 859500
2.6 | VAV-06 | No. | 1 | 271500 | 271500 | 15000 | 15000 | 286500
2.7 | VAV-07 | No. | 1 | 271500 | 271500 | 15000 | 15000 | 286500
2.8 | VAV-08 | No. | 1 | 271500 | 271500 | 15000 | 15000 | 286500
2.9 | VAV-09 | No. | 1 | 271500 | 271500 | 15000 | 15000 | 286500
2.1 | VAV-10 | No. | 1 | 271500 | 271500 | 15000 | 15000 | 286500
2.11 | VAV-11 | No. | 1 | 271500 | 271500 | 15000 | 15000 | 286500
3 | Supply & installation of valves & accessories for DFCU & WCPU
with supports, hangers, flanges, gas kits, nut & bolts where it
required, etc. complete in all respects as per specifications, drawings
and as per instructions of consultant.
A | for DFCU
3.1 | Ball Valve
i. | 1" dia | Nos. | 4 | 7700 | 30800 | 1000 | 4000 | 34800
3.2 | Strainers
i. | 1" dia | No. | 1 | 7500 | 7500 | 1000 | 1000 | 8500
3.3 | Balancing Valve (with self sealing measuring nipples)
i. | 1" dia | No. | 1 | 15800 | 15800 | 1000 | 1000 | 16800
3.4 | 2-Way Motorized Valve with Actuator (0-100% modulating)
i. | 1" dia | No. | 1 | 72000 | 72000 | 5000 | 5000 | 77000
3.5 | Thermometer 6" Height Scale Type (with Thermo well) 0 ºC to 60 ºC | Nos. | 2 | 9900 | 19800 | 1200 | 2400 | 22200
3.6 | Pressure Gauge with Ball Valve & Siphon, Liquid filled Dial type
| range | Nos. | 2 | 8800 | 17600 | 1200 | 2400 | 20000
0 psi to 100 psi. (4" dial Size)
3.7 | Digital Decorative Thermostat Controller (BMS Interfacable) with
| Duct Mounted Sensor | No. | 1 | 69000 | 69000 | 3000 | 3000 | 72000
3.8 | Control wiring from controller to sensors, motorized valve and power
| wiring up to 15’ radius | Job. | 1 | 25000 | 25000 | 10000 | 10000 | 35000
B | for WCPU
3.9 | Ball Valve
i. | 1" dia | Nos. | 4 | 7700 | 30800 | 1000 | 4000 | 34800
3.1 | Strainers
i. | 1" dia | No. | 1 | 7500 | 7500 | 1000 | 1000 | 8500
3.11 | Balancing Valve (with self sealing measuring nipples)
i. | 1" dia | No. | 1 | 15800 | 15800 | 1000 | 1000 | 16800
3.12 | Flexible Pipe Connector
i. | 1" dia | Nos. | 2 | 9900 | 19800 | 1000 | 2000 | 21800
3.13 | 2-Way Motorized Valve with Actuator (0-100% modulating)
i. | 1" dia | No. | 1 | 72000 | 72000 | 5000 | 5000 | 77000
3.14 | Flow Switch | Job. | 1 | 12800 | 12800 | 2000 | 2000 | 14800
3.15 | Digital Decorative Thermostat Controller (BMS Interfacable) with
| Duct Mounted Sensor | No. | 1 | 75000 | 75000 | 3000 | 3000 | 78000
3.16 | Control wiring from controller to sensors, motorized valve and power
| wiring up to 15’ radius | Job. | 1 | 25000 | 25000 | 10000 | 10000 | 35000
4 | Supply, installation, testing and commissioning of Variable
Frequency Drive (VFD) with controls complete in all respects as per
specifications, drawings and as per instructions of consultant.
4.1 | VFD-01 (2.5 kw approx) | Nos. | 2 | 185000 | 370000 | 10000 | 20000 | 390000
5 | Supply & installation of SCH-40 M.S.(As per ASME & API standard,
Heavy Quality with standard SCH 40 wall thickness) pipes & fitting
for chilled water circulation system complete with bends, tees,
unions, sockets, specials, lindaptor support, hangers & anchors,
M.S. angle, U-channel, roller support, bolts, rods, clamps, concrete
fasteners etc as required to complete in all respects ready to operate
as per specification, drawings and as per instruction of consultant.
5.1 | 1" dia | Rft | 200 | 790 | 158000 | 205 | 41000 | 199000
6 | Supply & installation of Pre Formed Polystyrene (Thermopore)
insulation (32 kg/m3 density) for chilled water pipes, bends, tees,
unions, sockets, valves and on specials protected with Kraft paper,
wrapped with 8oz Canvas cloth than paint with anti fungus paint
complete in all respects ready to operate as per specification,
drawings and as per instruction of consultant.
6.1 | 1" dia | Rft | 100 | 1990 | 199000 | 160 | 16000 | 215000
7 | Supply, installation of Ventilation Fans including electrical
connection, flexible duct connection / connector, lindaptor supports &
hangers complete in all respects ready to operate as per drawings,
specification and as per instruction of consultant.
7.1 | RAF-01 | No. | 1 | 1250000 | 1250000 | 25000 | 25000 | 1275000
8 | Supply, fabrication and installation of machine made G.I sheet metal
duct different sections supply, return, fresh & exhaust air including
plenums, splitter dampers, guide vanes, flexible duct connector /
connection, access door, transformation, plenums chambers,
wooden frame, lindaptor supports, anchors & hangers complete in all
| respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Sqft | 4700 | 450 | 2115000 | 95 | 446500 | 2561500
9 | Supply & installation of adhesive 3/4" thick rubber foam (XLPE)
insulation with aluminum foil over supply & return duct, complete in
| all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqft | 4500 | 540 | 2430000 | 79 | 355500 | 2785500
10 | Supply & installation of acoustical duct sound liner (adhesive 1/2"
thick) in supply air duct complete in all respects ready to operate as
| per specification, drawings and as per instruction of Consultant. | Sqft | 325 | 378 | 122850 | 79 | 25675 | 148525
11 | Supply & installation of aluminum fabricated, powder coated grills,
diffusers and registers etc for supply, return, exhaust & fresh air of
different sizes (Grade A) wooden frame, lindaptor supports and other
accessories etc. complete in all respects ready to operate as per
specification, drawings and as per instruction of Consultant.
11.1 | Grill / Reisters / Diffuser with Damper | Sqin | 8300 | 25 | 207500 | 8 | 66400 | 273900
11.2 | Linear Slots 6000 Series
i. | 1 Slots of 3/4" | Rft | 40 | 600 | 24000 | 70 | 2800 | 26800
ii. | 2 Slots of 3/4" | Rft | 75 | 999 | 74925 | 70 | 5250 | 80175
11.3 | Disc Valves
i. | 6" dia | Nos. | 8 | 3000 | 24000 | 1000 | 8000 | 32000
12 | Supply & installation of flexible duct including hangers, jubilee clamp
complete in all respects as per specification, drawings & as per
instruction of consultant.
12.1 | 4" dia | Rft | 55 | 460 | 25300 | 120 | 6600 | 31900
12.2 | 6" dia | Rft | 60 | 570 | 34200 | 120 | 7200 | 41400
13 | Supply & installation of butterfly damper for above flexible duct with
gas kits, nut bolts, complete in all respects, ready to operate as per
specification, drawings & as per instruction of consultant.
13.1 | 4" dia | Nos. | 16 | 2500 | 40000 | 1000 | 16000 | 56000
13.2 | 6" dia | Nos. | 18 | 3800 | 68400 | 1000 | 18000 | 86400
14 | Supply, Installation of Volume Control Damper in 16 SWG G.I sheet
metal with gas kits, nut bolts, etc, complete in all respects ready to
| operate as per specification, drawings and as per instruction, approval of consultant. | Sqin | 2000 | 27 | 54000 | 9 | 18000 | 72000
15 | Supply & installation of uPVC (Sch 40.) drain pipe insulated with 3/8"
thick rubber foam insulation including clamps, bends, tees, drain
plugs, sockets, protection treatment, PVC tape wrapping, lindaptor
supports & hangers complete in all respects as per specifications,
drawings & as per instructions of Consultant.
15.1 | 1" dia | Rft | 120 | 690 | 82800 | 130 | 15600 | 98400
16 | Painting & Identification work on chilled water pipes & exhaust duct,
supports, hangers etc. complete in all respects with one coat of ICI
| make Red lead oxide primer & two coats of ICI make enamel paint as per instruction of Consultant. | Job. | 1 | 35000 | 35000 | 15000 | 15000 | 50000
17 | Testing, balancing and commissioning of water & air side of the
system (from independent agency) complete in all respects including
flow measurement & balancing, temp, pressure, electrical data of
| related equipment etc. as per specifications and as per instructions of Consultant. | Job. | 1 | 100000 | 100000 | 35000 | 35000 | 135000
18 | Making of Shop drawings on Auto CAD (latest version) with section
details, equipment foundation details and Making of As Built
| drawings, Documentation Technical / Operational Manual & LOG Book for each equipment as per instruction of Consultant. | Job. | 1 | 25000 | 25000 | 10000 | 10000 | 35000
| Total Cost of ACMV Works Rs. | [6 empty] | 13213500

## Fire
Bill of Quantities
Fire Suppression Services
Amreli Steel Limited | [7 empty] | Rev.01
10th Floor, Dolmen Sky Tower, Karachi | [7 empty] | Date: 02-11-2022
S.No. | Description | Unit | Qty | Material |  | Labour |  | Total Amount
|  |  |  | Rate | Amount | Rate | Amount
SECTION-01 FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression services including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1.1 | MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
i. | Dia 1" (Threaded fitting) | Rft. | 350 | 610 | 213500 | 205 | 71750 | 285250
ii. | Dia 1-1/4" (Threaded fitting) | Rft. | 30 | 775 | 23250 | 220 | 6600 | 29850
iii. | Dia 1-1/2" (Threaded fitting) | Rft. | 70 | 890 | 62300 | 270 | 18900 | 81200
iv. | Dia 2" (Threaded fitting) | Rft. | 70 | 1195 | 83650 | 300 | 21000 | 104650
v. | Dia. 2-1/2" (Welded joints fitting) | Rft. | 20 | 1990 | 39800 | 305 | 6100 | 45900
vi. | Dia. 3" (Welded joints fitting) | Rft. | 50 | 2470 | 123500 | 400 | 20000 | 143500
1.2 | Sprinkler Heads | Nos. | 46 | 3000 | 138000 | 750 | 34500 | 172500
i. | Sprinkler Upright type quick response K = 5.6 (Opening Temperature 57ºC)
1.3 | Fire extinguishers with fixing accessories. | Nos. | 2 | 19500 | 39000 | 1000 | 2000 | 41000
i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas)
ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 2 | 14800 | 29600 | 1000 | 2000 | 31600
iii. | Type Class K FX-5 (6 Litre Wet chemical fire extinguisher). | Nos. | 1 | 35000 | 35000 | 3000 | 3000 | 38000
| SECTION-02 NOVEC SYSYEM | Kg. | 10 |  |  |  |  | 0
2.1 | CLEAN AGENT (FK-5-1-12 Stored In Cylinder - Ul Listed / Fm Approved) |  |  | SECURE VISION
Supply & installation of clean agent in engineered cylinders of FSS with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
a. | Clean Agent (FK-5-1-12, Fluoroketone)
b. | Engineered cylinder with head valve, top plug adapter, siphon tube, pressure gauge, brackets and all other items, complete in all respect. | Nos. | 2
2.2 | Supply & installation of MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Rft. | 40
i. | Dia 1/2" (Threaded fitting)
2.3 | SPRINKLER HEADS
Supply & installation of nozzles with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
| Brass Discharge Nozzle - 360 Degrees discharge pattern |  |  | SECURE VISION
i. | Dia 1/2" | Nos. | 2
2.4 | INPUT & OUTPUT DEVICES | Nos. | 1
Supply & installation of input and output devices for the clean agent suppression system (integrated with BMS) with wiring, controls & fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant
i. | Entinguishing Control Panel for the clean agent fire suppression system
ii. | Manual Abort / Emergency Cut Off Switch | Nos. | 2
iii. | Manual Release Switch - Single Action | Nos. | 2
iv. | Horn / Strobe | Nos. | 1
v. | Alarm Bell | Nos. | 1
2.5 | ACTUATION DEVICES | Nos. | 2
Supply & installation of actuation devices with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
i. | Solenoid Actuator for the specified cylinder size
ii. | Manual Control Head for manual actuation of cylinder with safety pull pin | Nos. | 2
iii. | Pressure Switch to indicated system discharge with an external manual reset button | Nos. | 2
iv. | Low Pressure Switch to monitor the pressure within the cylinder | Nos. | 2
2.6 | WIRING | Job. | 1 | SECURE VISION
i. | Supply & installation of wiring of 2C, 1.5 Sq.mm fire resistant shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia MS conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respects ready to operate as per drawings, specification, instruction of consultant.
2.7 | Making of Shop drawings on Auto CAD 2018 with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects as per instruction of consultant. | Job. | 1 | 25000 | 25000 | 5000 | 5000 | 30000
2.8 | Painting, identification and tagging to the installations and equipments, complete in all respects as per instruction of consultant. | Job. | 1 | 35000 | 35000 | 10000 | 10000 | 45000
2.9 | Flushing of entire fire pipe work according to (NFPA-13), complete in all respects as per instruction of consultant. | Job. | 1 | 25000 | 25000 | 10000 | 10000 | 35000
2.1 | Testing and commissioning of entire fire fighting and clean agent for fire suppression system complete in all respects as per instruction of consultant. | Job. | 1 | 50000 | 50000 | 25000 | 25000 | 75000
| Total Cost | [6 empty] | 1158450