## Summary
HVAC Work - Bank Al Habib |  |  |  | 2023-04-28
16th Floor Centerpoint Karachi.
SUMMARY OF RUNNING BILL
S.No | Description | Material Amount | Labour Amount | Total Amount
1 | HVAC Work | 2320300 | 902730 | 3223030
| Grand Total Amount |  |  | 3223030

## HVAC 16th Floor
Bill of Quantities | [5 empty] | Running bill
Sr. No. | Description | Unit | Qty | Material Rate | Labour Rate | Material |  | Labour |  | Total Amount
[6 empty] | Bill Qty | Amount | Bill Qty | Amount
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of Consultant
1 | Cutting dismantling and shifting o f the existing ACMV works as per instruc(ion of consultant, including cleaning the site and shifting lhe dism an fled parts / m aterial to suitable place giver by client complete in all respects ready to opera te as per drawings and as per instruction of consultant.
1.1 | ACMV Works i.e; FCU, Pipe, Vlaves, accessories, duct, insulation etc complete job as required. | Job | 1 | 0 | 225000 | 1 | 0 | 1 | 225000 | 225000
Unloading, installation, testing and commissioning of (Owner Supplied) of fan coil units of different capacities complete in all respects, ready to operate including supply and installation of all accessories, supports, hanger steel base, vibration isolators, including interconnecting power & control wiring (terminal connection) with inlet & outlet chilled water connections, drain connection, flexible rubber duct connection / connector etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction consultant
2.1 | FCU-01 | Nos | 2 | 25000 | 5000 |  | 0 | 0 | 0 | 0
3 | Supply & installation of valves & accessories for AHU withsupports, hangers, flanges, gas kits, nut & bol ts where it required, etc. complete in all respects as per specifications, drawings and as per instructions of consultant, | [6 empty] | 0
3.1 i | Ball Valve 25mm dia | Nos | 8 | 7200 | 1000 |  | 0 | 0 | 0 | 0
3.2 i | Strainers 25mm dia | Nos | 2 | 6500 | 1000 |  | 0 | 0 | 0 | 0
0
3.3 i | Balancing Valve (with selI sealing measuring nipples) 25mm dia | Nos | 2 | 14500 | 1000 |  | 0 | 0 | 0 | 0
3.4 | Thermometer 150mm Height Scale type (with Thermo well) 0 °C to 60 °C | Nos | 4 | 8500 | 700 |  | 0 | 0 | 0 | 0
3.5 | Pressure Gauge with Ball Valve & Siphon, Liquid filled ” Dial type range 0 psi to 100 psi. (100mm dial Size) | Nos | 4 | 10500 | 700 |  | 0 | 0 | 0 | 0
3.6 i | 2-Way Motorized Valve with Actua tar (0-100% modulating 25mm dia | Nos | 2 | 80000 | 3500 |  | 0 | 0 | 0 | 0
3.7 | Digital Decorative Thermostat Controller (BMS Interfacable) with Duct Mounted Sensor | Nos | 2 | 55000 | 3500 |  | 0 | 0 | 0 | 0
3.8 | Control wiring from controller to sensors, motorized valve and Power wiring up to 15’ radius | Job | 2 | 13000 | 3000 |  | 0 | 0 | 0 | 0
4 | Supply & installation of SC H 40 M.S.(As per ASME & API standard, Heavy Quality with standard SCH 40 wall thickness) pipes & filting for chilled & cooling water circulation system complete with bends, tees, unions, sockets, specials, support, hangers & anchors, M.S. angle, U channel, roller support, bolts, rods, clamps, concrete fasteners etc as required to complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | [6 empty] | 0
4.1 | 25mm dia | Rm | 25 | 2700 | 600 | 22 | 59400 | 22 | 13200 | 72600
4.2 | 32mm dia | Rm | 15 | 3250 | 700 | 13 | 42250 | 13 | 9100 | 51350
0
5 | Supply & installation of Pre Formed Polystyrene (Thermopore) insulation (32 kg/m* density) for chilled water pipes, bends, tees, unions, sockets, yalves and on specials protected with Kraft paper, wrapped with 8oz Canvas cloth than paint with anti fungus paint complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. 25mm dia | Rm | 25 | 1350 | 180 | 22 | 29700 | 22 | 3960 | 33660
i | 32mm dia | Rm | 15 | 1550 | 190 | 13 | 20150 | 13 | 2470 | 22620
6 | Supply & istaliation of uPVC (Sch 40.) drain pipe insulated with 3/8" thick rubber foam insulation including clamps, bends, tees, drain plugs, sockets, protection treatment, PVC tape wrapping, supports & hangers complete in all respects as per specifications, drawings & as per instructions of Consultant. 25mm dia | Rm | 20 | 650 | 250 | 10 | 6500 | 10 | 2500 | 9000
7 | Unloading, installation, testing and commissioning of (Owner Supplied) of VAV Boxes as per mentioned in schedule with digita¦ thermostat controller, pressure sensor, control wiring, including supply & installation of flexible duct connection / connector, electrical connection, lindaptor support & hangers complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | [6 empty] | 0
7.1 | VAV-01 | Nos | 1 |  | 7500 | 1 | 0 | 1 | 7500 | 7500
7.2 | VAV-02 | Nos | 1 |  | 7500 | 1 | 0 | 1 | 7500 | 7500
7.3 | VAV-03 | Nos | 3 |  | 8000 | 3 | 0 | 3 | 24000 | 24000
7.4 | VAV-04 | Nos | 2 |  | 8000 | 2 | 0 | 2 | 16000 | 16000
7.5 | VAV-05 | Nos | 1 |  | 8000 | 1 | 0 | 1 | 8000 | 8000
7.6 | VAV-06 | Nos | 1 |  | 8000 | 1 | 0 | 1 | 8000 | 8000
7.7 | VAV-07 | Nos | 3 |  | 10000 | 3 | 0 | 3 | 30000 | 30000
7.8 | VAV-08 | Nos | 1 |  | 8000 | 1 | 0 | 1 | 8000 | 8000
7.9 | VAV-09 | Nos | 2 |  | 8500 | 2 | 0 | 2 | 17000 | 17000
7.1 | VAV-10 | Nos | 1 |  | 8500 | 1 | 0 | 1 | 8500 | 8500
7.11 | VAV-11 | Nos | 1 |  | 9000 | 1 | 0 | 1 | 9000 | 9000
7.12 | VAV-12 | Nos | 1 |  | 9000 | 1 | 0 | 1 | 9000 | 9000
7.13 | VAV-13 | Nos | 1 |  | 8500 | 1 | 0 | 1 | 8500 | 8500
7.14 | VAV-14 | Nos | 1 |  | 9000 | 1 | 0 | 1 | 9000 | 9000
7.15 | VAV-15 | Nos | 1 |  | 10000 | 1 | 0 | 1 | 10000 | 10000
8 | Supply, fabrication and installation of pre-insulated ductwork of polyurethane foam panel with 52 Kg/m 3 density, 20 mm thickness, coa1ed on bolh sides with 80 micron thick aluminum foil complete with a 2 g/m2 layer for internal duct work including manufacturer's aluminum hardware glue, Hot Dipped galvanized hangers and supports, flexible duct connection wooden frame, etc. Complete in all respects ready to operate as per drarwings, specification and as per instruction of consultant. | Sqm | 875 | 4600 | 800 | 171 | 786600 | 171 | 136800 | 923400
0
9 | Supp!y, insta!lation of Aluminum fabricated, powder coated Gri!ls, Diffusers and Registers for supply air, return air, exhaust air & fresh air of different sizes {Grade A ), wooden frame, supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. Supply & Return Air Registers/ Diffuser with Damper | [6 empty] | 0
i | 300mmx300mm Square Diffuser | Nos | 8 | 3500 | 750 | 9 | 31500 | 9 | 6750 | 38250
ii | 350mm dia Jet Diffuser | Nos | 8 | 8900 | 750 | 0 | 0 | 0 | 0 | 0 | 15.463
iii | Supply and return air grills 450mm x 250mm | Nos | 2 | 6000 | 1500 | 0 | 0 | 0 | 0 | 0
iv | S.S Wire mech with G.I Frame | Sqm | 4 | 22000 | 1000 | 3.5 | 77000 | 3.5 | 3500 | 80500
v | Linear slot 6000 series 2 Slots of 20mm | Rm | 135 | 3800 | 400 | 131 | 497800 | 131 | 52400 | 550200
10 | Supply & installation of flexible duct including hangers, jubilee clamp complete in all respects as per specification, drawings & as per instruction of consultant. 150mm dia | Rm | 200 | 1460 | 150 | 190 | 277400 | 190 | 28500 | 305900
11 | Supply & installation of butterfly damper for above flexible duct with gas kits, nut bolts, complete in al! respects, ready to operate as per specification, drawings & as per instruction of consultant. 150mm dia | Nos | 167 | 2400 | 750 | 165 | 396000 | 165 | 123750 | 519750
0
12 | Supply, fabrication & installation of pre-insulated Volume Control Damper, blades to be constructed with extruded aluminum in airfoil shape with thermal isolation gape & shall have seals, pvc / aluminum profiles duct connection at both end etc. complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Sqm | 6 | 6000 | 800 | 6 | 36000 | 6 | 4800 | 40800
13 | Paining & Identification work on supports, hangers, platform of condensing units etc complete in all respec(s with one coat of ICI make Red lead oxide primer & two coats of ICI make enamel paint complete in all respects ready to operate as per drawings, specification, instruction and approval of Consuftant. | Lot | 1 | 35000 | 5000 | 1 | 35000 | 1 | 5000 | 40000
14 | Testing, balancing and commissioning of waler & air side of the system (from independent agency) complete in all respects including air measurement & balancing, temp pressure & electrical data of related equipment etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job | 1 | 0 | 95000 | 1 | 0 | 1 | 95000 | 95000
15 | Making of Shop drawings on Auto CAD (latest version) with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job | 1 | 25000 | 10000 | 1 | 25000 | 1 | 10000 | 35000
| Total Cost of Works Rs. | [5 empty] | 2320300 |  | 902730 | 3223030