## TITLE
BILL OF QUANTITIES
Architecture/Interior & Furniture Works
EY
4th FLOOR, NAVEENA TOWER,
LAHORE
| Principal Design Consultant | Project Management and Cost Consultants

## Grand Summary
EY Lahore - 4th Floor - Grand Summary
S.No | Activity. | Supply Amount | Installation Amount | Total
A | Civil ID | 0 | 0 | 0
B | Electrical | 0 | 0 | 0
C | Firefighting | 0 | 0 | 0
D | HVAC | 0 | 0 | 0
E | Plumbing | 0 | 0 | 0
| TOTAL RS. | 0 | 0 | 0
| General Contractor's Markup on MEP Cost | 0 | 0 | #REF!
Grand Total Inclusive of Markup |  | 0 | 0 | #REF!
Taxes
GST on Supply
PST on Installation
Grand Total Inclusive of Tax |  | 0

## Summary Civil ID
EY Lahore - 4th Floor - Civil ID Summary
S.No | Activity. | Supply Amount | Installation Amount | Total
A | CIVIL & ARCHITECTURE WORKS
B | FURNITURE WORKS
Grand Total |  | 0 | 0 | 0
Taxes
| GST on Supply | 0
| PST on Installation |  | 0
Grand Total Inclusive of Tax

## A-CIVIL
EY Lahore - 4th Floor - Civil ID
A | CIVIL & ARCHITECTURE WORKS |  |  | SUPPLY |  | INSTALLATION |  | TOTAL | Lead Time | Brand | Remarks
S.No. | DESCRIPTION | Qty | Units | Rate | Amount | Rate | Amount
1 | CORDON OFF
| Cordoning off - Curtain walls to be completely cordoned off as required by fitout guidelines. Provide and fix 3mm to 6mm thick hard board sheets over partal wood framing (600mmx600mm) covering at least 2400mm height supported in between RCC column providing a 300 mm to 600 mm adequate distance from the curtain glass | 300 | Sqm.
2 | DISMANTLING
| Dismantling/ cutting/ removal of existing masonry walls, flooring & wall chipping, doors, windows, ceiling, cladding, electrical fixtures etc. complete in all respect including removal of debris from site and handling over the client properties to the client representative. | 1 | Job
3 | WALL PARTITIONS
3.1 | PW-01 100MM THK. CEMENT BOARD STUD PARTITION (FULL HEIGHT)
| Providing, Fabricating and fixing 150mm thick Partition up to full height (SLAB LEVEL) with 10mm cement board to be fixed both side with screw over G.I channel frame 22swg, including cost of all hardware, scaffolding, lifting, etc. including cost of rock wool filling in cavity for insulation and fire Barrier for all openings/joints, complete in all respect as per specifications, drawings and as directed by the Architect. | 213.63 | Sqm.
3.2 | PW-02 100MM THK. CEMENT BOARD STUD PARTITION (LOW HEIGHT)
| Providing, Fabricating and fixing 100mm thick Partition up to full height (SLAB LEVEL) with 10mm cement board to be fixed both side with screw over G.I channel frame 22swg, including cost of all hardware, scaffolding, lifting, etc. including cost of rock wool filling in cavity for insulation and fire Barrier for all openings/joints, complete in all respect as per specifications, drawings and as directed by the Architect. | Rate Only | Sqm.
3.3 | PW-03 200MM THK. CEMENT BOARD STUD PARTITION (LOW HEIGHT)
| Providing, Fabricating and fixing 200mm thick Partition up to 1200mm height (LOW HEIGHT) with 10mm Thick double layer cement board to be fixed both side with screw over G.I channel frame, including cost of all hardware, scaffolding, lifting, etc. including cost of rock wool filling in cavity for insulation, complete in all respect as per specifications, drawings and as directed by the Architect. | Rate Only | Sqm.
3.4 | PW-04 FIXED TEMPERED GLASS PARTITION
| Provide and install in position fixed glazing consist of 6mm+0.76mm (PVB interlayer)+6mm Tampered Laminated with powder coated Aluminum frame including cost of all hardware, wastage, silicon sealant, lifting, etc., complete as per drawing, hardware schedule & instruction of the Architect | 101.27 | Sqm.
b. | Providing & applying of Plotter / Laser cut Frosted film 50 Micron (3M or approved equivalent) on glazing as per approved sample, shade / colour with wastage and as per instruction of the Architect etc., complete in all respect. | 50.635 | Sqm
c | Providing & applying of 150 microns anti shatter film from one side supplied by 3m or equivalent or as per instruction of the Architect. | 101.27 | Sqm
3.5 | PW-05 BRICK MASONRY
a. | Providing and laying at mentioned floor first class 9" thick full height brick masonry using burnt brick minimum 1500 PSI set in (1:5) cement sand mortar in super structure including curing, finishing racking out joints, scaffolding, lifting, hoisting etc, complete in all respect as per specifications, drawings and as directed by the Architect. | 42.68 | Sqm.
b. | Providing and laying 1/2" to 3/4" thick cement, sand plaster (1 : 5 ) to internal/External walls, making edges and corners including cost of fixing wire mesh 22 swg G.I. Expanded metal 8" wide at joint of R.C.C. members and block masonry works, preparation of surface before plastering finishing scaffolding, curing etc. complete in all respect as specified and as approved by the Architect. | 84.5 | Sqm.
3.6 | PW-06 ALUMINUM FOLDING PARTITION
| Provide and install in position Openable / foldable partitions consist of 8mm acoustic fabric with Powder coated Aluminium frame including cost of all hardwares, Necessary MS supports, wastage, silicon sealant, lifting, etc., complete as per drawing, hardware schedule & instruction of the Architect. | 13.45 | Sqm.
3.7 | PW-07 150MM THK. CEMENT BOARD STUD PARTITION (LOW HEIGHT)
| Providing, Fabricating and fixing 150mm thick Partition up to 1200mm height (LOW HEIGHT) with 12mm cement board to be fixed both side with screw over 38mmx75mmx0.75mm thick G.I channel frame, including cost of all hardware, scaffolding, lifting, etc. Complete in all respect as per specifications, drawings and as directed by the Architect. | Rate Only | Sqm.
4 | CLADDING
4.1 | CL-01 10MM THK CEMENT BOARD CLADDING
| Providing, making & install 10mm thick Cement cladding on single face over masonry or existing surface to be fixed with screw over 38mmx75mmx 0.75mm GI Stud frame @ 600mmx600mm c/c with anti rust paint if required, including cost of all hardware, scaffolding, lifting, etc., complete in all respect as per specifications, drawings and as directed by the Architect. (Cement board exposed area will be measure for payment.) | 61.91 | Sqm.
4.2 | CL-02 12MM THK MDF BOARD CLADDING
| Providing, making & install 12mm thick MDF board cladding on single face over masonry or existing surface to be fixed with screw over 25mm x 50mm solignum treated partal wood frame @ 600mm x 600mm c/c, including cost of all hardwares scaffolding, lifting, etc, complete in all respect as per specifications, drawings and as directed by the Architect. (MDF board exposed area will be measure for payment.) | 10.76 | Sqm.
4.3 | CL-03 12MM THK MDF BOARD WITH OAK WOOD STRIP
| Providing, making & install 12mm thick MDF board cladding on single face over masonry or existing surface to be fixed with screw, including 38mmx50mm solid oak wood poilsh finish strip to be fixed over MDF with equal distance as shown in drawing, including cost of all hardwares scaffolding, lifting, etc, complete in all respect as per specifications, drawings and as directed by the Architect. | 14.83 | Sqm.
5 | WALL FINISHES
5.1 | WF-01 PAINT FINISH (TYPE-01)
| Provide and apply paint (National, Jotun / ICI or approved) minimum three coats as per approved shade over a coat of primer to internal surfaces prepared smooth with carborundum stone, filling the depression with putty including scaffolding, etc. complete in all respect. | 992.62 | Sqm.
5.2 | WF-02 PAINT FINISH (TYPE-02)
| Provide and apply paint (National, Jotun / ICI or approved) minimum three coats as per approved shade over a coat of primer to internal surfaces prepared smooth with carborundum stone, filling the depression with putty including scaffolding, etc. complete in all respect. | 127.76 | Sqm.
5.3 | WF-02a PAINT FINISH (TYPE-03)
| Provide and apply paint (National, Jotun / ICI or approved) minimum three coats as per approved shade over a coat of primer to internal surfaces prepared smooth with carborundum stone, filling the depression with putty including scaffolding, etc. complete in all respect. | 29.48 | Sqm.
5.4 | WF-02b PAINT FINISH (TYPE-04)
| Provide and apply paint (National, Jotun / ICI or approved) minimum three coats as per approved shade over a coat of primer to internal surfaces prepared smooth with carborundum stone, filling the depression with putty including scaffolding, etc. complete in all respect. | 10.67 | Sqm.
5.5 | WF-02c PAINT FINISH (TYPE-05)
| Provide and apply paint (National, Jotun / ICI or approved) minimum three coats as per approved shade over a coat of primer to internal surfaces prepared smooth with carborundum stone, filling the depression with putty including scaffolding, etc. complete in all respect. | 49.14 | Sqm.
5.6 | WF-03 TEXTURE PAINT FINISH
| Providing and applying at any height texture paint to surface walls ,columns and ceiling etc. roller applied having egg shell finish over one base primer coat including rubbing or scrapping , filling etc complete in all respects as per instructions and as directed by the Architect. | 69.96 | Sqm.
5.7 | WF-04 FABRIC WITH MDF FLUTE
| Providing and fixing fabric cladding with 30mm thick MDF Flute panels over 6mm thick MDF board to be fixed with existing wall as per drawing and instructions of the Architect. | 8.68 | Sqm.
5.8 | WF-05 ART WORK DIFFERENT SIZES
| Providing and fixing art work printed from high resolution file pasted over 18mm MDF sheet as per given details including cost of wooden gola framing polish finish. complete in all respects as per instructions and as directed by the Architect. | 6 | Jobs.
5.9 | WF-06 WINDOW ROLLER BLINDS
| Provide and install roll down sun screen of approved colour & sample i/c 18mm thick lasani box the with oak wood lipping i/c all hardwares as per drawing & detail or approved by the consultant and directed by the Architect. Basic price Rs. 4800/sqm. | 175.8 | Sqm.
5.1 | WF-07 WHITE BOARD (TYPE-01)
| Providing and fixing White board consist of White High Gloss Lamination sheet fixed over 25mmX35mm wooden frame including cost of all hardware for fixing as per instruction of the Architect. | 19.6 | Sqm.
5.11 | WF-08 IMPORTED FORMICA/OAK PLY POLISH FINISH
| Providing and pasting Formica over 8mm thick MDF backing with 5mm "C" groove both sides at joints, over existing surface as per approved sample including cost of pasting adhesive as per instructions of the Architect. | 136.07 | Sqm.
5.12 | WF-09 600MMX300MM PORCELAIN TILES
| Providing and laying best quality imported full body porcelain tile as approved size cutting where required for wall up to 2400mm Height with 1 : 4 cement sand mortar base or dry bond of required thickness for setting the tiles in pattern with cement mortar, I/c bacteria resistance grouting in the joints including curing cleaning etc., complete in all respect and as per instructions and as directed by the Architect.. (Basic price of tiles Rs. 7000/Sqm.) | 220.87 | Sqm.
5.13 | WF-10 OAK VEENER POLISH FINISH
| Providing and pasting 6mm thick oak veener over existing MDF/Cement board with 3mm wide groove if required and approved polish finish as per approved sample including cost of pasting adhesive as per instyructions of the Architect. | 0 | Sqm.
5.14 | WF-11 12MM CORIAN CLADDING
| Providing and fixing of 12mm Corian cladding over existing surface as per Drawing complete in all respect including cutting of holes where required etc as per Architect instructions. | 3.99 | Sqm.
5.15 | WF-12 WHITE BOARD (TYPE-02)
| Providing and fixing White board consist of White Glossy MDF Lamination sheet with 38mm x 25mm MS powder coated tube frame including cost of all hardware for fixing as per instruction of the Architect. | 36.53 | Sqm.
5.16 | WF-13 LOGO
| Providing & fixing 50mm deep acrylic finish logo MDF CNC Cut deco Finish as per approved design and color including cost of fixing arrangements complete with all hardware as approved by the consultant and directed by the Architect. | 1 | Job.
5.17 | WF-14 SILK SCREEN PRINTING TOILET SIGN
| Providing and pasting Silk Screen (Toilet signs) printed as per given details including cost of adhesive, rubbing or scrapping of surface , filling, cleaning etc. complete in all respects as per instructions and as directed by the Architect. | 2 | Jobs.
5.18 | TEXT 18MM THICK ACRYLIC LETTERS
| Providing and fixing of 18mm thick Acrylic text, consist of Flat cut acrylic sheet including cost of all fixing arrangements as per detail drawings and directed by the Architect. (ref ID-301) | 2 | Job
5.19 | SK-01 75MM HIGH PVC SKIRTING
| Provide and install, in position where required, 75mm high approved quality heavy duty PVC skirting (supplied by approved manufacturer) with approved adhesive, etc. complete with all hardware as approved by the Architect.. | 396.04 | Mtr.
6 | FLOOR FINISHES
6.1 | FF-01 CARPET TILES (TYPE-01)
| Supply and Installation of Carpet Tiles flooring with underlay backing with termite proofing as per manufacture specification complete in all respect and directed by the Architect. (As per approved code as mentioned in RFP) | 164.08 | Sqm.
6.2 | FF-02 CARPET TILES (TYPE-02)
| Supply and Installation of Carpet Tiles flooring with underlay backing with termite proofing as per manufacture specification complete in all respect and directed by the Architect. (As per approved code as mentioned in RFP) | 124.87 | Sqm.
6.3 | FF-03 LVT FLOOR (TYPE-01)
| Supply and Installation of 4mm thick Luxury Vinyl Tile (LVT) flooring to be pasted by imported adhesive from South Africa on existing floor with all necessary hardware & bond etc., complete in all respects as per drawing and directed by the Architect. (As per approved code as mentioned in RFP) | 218.94 | Sqm.
6.4 | FF-04 600x1200 PORCELAIN TILES
| Providing and laying best quality imported full body 600mm x 1200mm porcelain tile as approved cutting where required for floor with 1 : 4 cement sand mortar base of 37mm to 75mm or dry bond of required thickness for setting the tiles in pattern with cement mortar + water proofing chemicals , I/c bacteria resistance grouting in the joints including curing cleaning etc., complete in all respect and as per the instruction of the Architect. (Basic Price of Tiles Rs. 7000/sqm.) | 45.92 | Sqm.
6.5 | FF-05 CARPET TILES (TYPE-03)
| Supply and Installation of Carpet Tiles flooring with underlay backing with termite proofing as per manufacture specification complete in all respect and directed by the Architect. (As per approved code as mentioned in RFP) | 0 | Sqm.
6.6 | FF-06 LVT FLOOR (TYPE-02)
| Supply and Installation of 4mm thick Luxury Vinyl Tile (LVT) flooring to be pasted by imported adhesive from South Africa on existing floor with all necessary hardware & bond etc., complete in all respects as per drawing and directed by the Architect. (As per approved code as mentioned in RFP) | 133.79 | Sqm.
6.7 | FF-07 CARPET TILES (TYPE-04)
| Supply and Installation of Carpet Tiles flooring with underlay backing with termite proofing as per manufacture specification complete in all respect and directed by the Architect. (As per approved code as mentioned in RFP) | 36.37 | Sqm.
6.8 | FF-08 CARPET TILES (TYPE-05)
| Supply and Installation of Carpet Tiles flooring with underlay backing with termite proofing as per manufacture specification complete in all respect and directed by the Architect. (As per approved code as mentioned in RFP) | 52.83 | Sqm.
6.9 | WF-09 RUG (TYPE-01)
| Providing and laying rug of approved design and color having size as per approved by the Architect. | 18.98 | Sqm.
6.1 | WF-10 RUG (TYPE-02)
| Providing and laying rug of approved design and color having size as per approved by the Architect. | 0 | Sqm.
6.11 | MT-01 METAL TRIM
| Providing and fixing of 5mmx18mm thk solid SS trim at all joints of carpet and floor or where required complete in all respect and as per the instruction of the Architect. | 237.21 | Mtr.
6.12 | WATER PROOFING
| Providing and Laying water proofing by two coats of master seal 550 (BASF) including cleaning and chipping of surface, removing excess material, wastage, etc. complete in all respect and applying as per manufacturer specification and directions of the Architect/Project Manager | 48 | Sqm.
6.13 | CC FLOOR SMOOTH FINISH
| Provide and laying 1:3:6 cement concrete floor smooth finished minimum 50mm to 75mm thick laid in panels, including hacking of existing surface for bonding where necessary, etc., complete in all respect as per specifications and drawings. | 730.88 | Sqm.
6.14 | SELF LEVELING FLOOR
| Provide and laying self leveling compound 4mm thick of Ressi SLS 610 or approved equivalent, complete in all respect as per specifications and drawings. Ressi SLS 610 is ready to use premixed self-leveling floor screed which is ideal for use to level substrates prior to laying raised flooring system, carpets, floor tiles etc. as per required lvt flooring. | 730.88 | Sqm.
7 | CEILING FINISHES
7.1 | FC-01 12MM THK. GYPSUM BOARD CEILING
| Provide and install in position Gypsum Board Ceiling, consisting of G.I. frame work with G.I. Hangers and 16-18 swg. aluminum edgings, 12mm thick Gypsum Board Sheet (Elephant brand Thailand or approved equivalent) fixed on frame, all over board as shown in drawings & details, cutting of opening for light fixtures / diffusers with making of light pelmet, fiber tape on joints, including with 3 coats of Matt Enamel paint finish (Jotun / ICI or Berger), of Gypsum board, approved shade on Gypsum board, primer coat filling if required and all other hardware, wastage, scaffolding, making access panel (where required), making light pelmet in gypsum board as shown in drawing, etc., complete in all respect and instruction of the Architect. For payment exposed painted sheet surface area will be measured. | 95.6 | Sqm.
7.2 | FC-02 MR GYPSUM BOARD CEILING
a. | Provide and install in position Moisture resistant Gypsum Board Ceiling, consisting of G.I. frame work with G.I. Hangers and 16-18 swg. aluminum edgings, 12mm thick Moisture resistant Gypsum Board Sheet (Elephant brand Thailand or approved equivalent) fixed on frame , in drawings & details, cutting of opening for light fixtures / diffusers with making of light pelmet, fiber tape on joints, including with 3 coats of Matt Enamel paint finish (Jotun / ICI or Berger), of Gypsum board, approved shade on Gypsum board, primer coat filling if required and all other hardware, wastage, scaffolding, making access panel (where required), making light pelmet in gypsum board as shown in drawing, etc., complete in all respect and instruction of the Architect. For payment exposed painted sheet surface area will be measured. | 231.08 | Sqm.
b. | Providing and fixing Pre Fabricated Access Panel 600mmx600mm | 25 | No
7.3 | FC-03 MDF CEILING WITH OAK PLY
| Providing and Installation of 12mm MDF board false ceiling with 100mm wide oak ply pressed with 3mm groove as per design and pattern with light palmet and approved polish finish of approved shade and quality with solignum treated solid wooden frame in back ,having provision of lights, complete as per manufacture's specification and as directed by Architect. | 14.97 | Sqm.
7.4 | FC-04 MDF CEILING/BULKHEAD
| Providing and Installation of 18mm MDF board false ceiling/ Bulkhead with paint as per design and pattern with approved paint finish of approved shade and quality with solignum treated solid wooden frame in back ,having provision of lights, complete as per manufacture's specification and as directed by Architect. | 42.6 | Sqm.
7.5 | FC-05 PERFORATED SHEET CEILING
| Providing and fixing 16 SWG GI perforated sheet ceiling to be fix with MS tube frame with deco paint finish including cost of fixing arrangements as per detail drawing and directed by the Architect | 16.21 | Sqm.
7.5 | ES-01 EXISTING SLAB PAINT FINISH
| Providing and applying at any height 03 coats of paint "ICI" , "Jotun" or approved to existing RCC Slab surface etc. roller applied having egg shell finish over one base primer coat including the cost of painting over all services, rubbing or scrapping , filling etc. complete in all respects as per instructions and as directed by the Architect. For payment only horizonital surface area will be covered | 656.6 | Sqm.
7.6 | FC-06 HOUSING FOR LINEAR LIGHT
| Providing and Fixing at any height and level housing for 50mm wide linear light, consisting of two 8mm X 150mm x3600mm MDF cladded with high density foam wrapped in architect approved fabric. Complete in all respect including the cost of lifting, shifting, pasting, cutting and all necessary arrangements for fixing etc. complete in all respects as per instructions and as directed by the Architect. | 19 | Nos.
8 | DOOR AND WINDOWS
8.1 | providing , making and fixing in position 45mm solid core flush door single/double shutters with approved sample imported Formica pressed on both sides I/c grooves if required ,i/c approved polish finish, beading, solid oak wood polish finish lipping all hardware including cost of hinges, hold fasts,S.S. screw, door stopper, 100mm wide S.S. kick plates both sides polish finish door frame as per given size and glass vision panel where required complete in all respects as per drawing and directed by the Architect.
a. | D1 1050x2400mm | 7 | Nos.
b. | D2 900x2400mm | 7 | Nos.
c. | D2a 900x2400mm (with vision panel and Aluminium louver) | 4 | Nos.
d. | D3 750x2400mm | 5 | Nos.
e. | D6 900x2400mm (with vision panel and Aluminium louver) | 2 | Nos.
8.2 | Provide and install in position Glass door consist of 12mm thick tempered glass with Powder coated Aluminum frame including cost of all hardware, wastage, silicon sealant, lifting, etc. All glass will be tempered, Complete as per drawing, hardware schedule & instruction of the Architect including cost of 175 microns anti shatter film supplied by 3m or equivalent or as per instruction of the Architect.
a. | D4 1800x2400mm Double leaf | 1 | Nos.
b. | D5 900x2400mm Single leaf | 10 | Nos.
8.3 | Provide and install single shutter imported factory assembled four side air tight fire rated up to 2 hours metal door with approved color including hinges, panic bar, Door frame, lock etc. as shown in drawing . Complete in all respects for emergency exit. Certified with UL.
a. | D1 1000x2400mm Single leaf with-out vision panel | 2 | Nos.
b. | D2 1000x2400mm Single leaf with vision panel | 1 | Nos.
c. | SD1 1050x2400mm Slidding | 0 | Nos.
9 | TOILET/ PANTRY
9.1 | MIRROR
| Providing & fixing imported mirror 6mm thick having 6mm thick commercial ply backing and solid wood frame for hanging, fixing with S.S.clips & silicon lay etc., including cost of fixing arrangements complete with all hardware as approved by the consultant and directed by the Architect. | 20 | Sqm.
9.2 | MARBLE LEDGE / THRESHOLD
| Providing and installation of marble 25mm thick for ledge and threshold complete in all aspects as per detail drawings and directed by the Architect. ((Basic Price of marble = Rs. 15000/Sqm.) | 3.21 | Sqm.
9.3 | PANTRY CABINET
| Providing and Installation of Pantry counter consist of following materials: | 1 | Job
Russian Ply Shutter Cabinets with shutter/Drawers with 100mm raised platform
16mmthk.mdf formica lamination with flip for trash bin with 18 gauge s/s finish along engrave trash bin symbol on shutter
Imported Formica pasted over shutters, drawers and all outer surface &1mm thick PVC lipping around
Fomite or approved Formica pasted over internal partitions, shelves and drawers internal surface
18mm pre-polished marble top with SS sink bowl
MDF board box hanging Cabinets with shutters
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Base Cabinet Size = as per drawing
Hanging Cabinet Size = as per drawing
9.4 | MARBLE VANITY COUNTER
| Providing and fixing of 19mm pre-polished marble top vanity as per Drawing complete in all respect including the cost of cutting for sink, drains, taps etc, making corner gola, as per Architect instructions. (Basic Price of marble = Rs. 15000/) | 2 | Job
10 | Certified/Qualified full time HSE Supervisor
| Certified/Qualified full time Health and Safety Supervisor other than the Resident Engineer/Site Supervisor. The HSE representative has to be on site full time during fitout works. | 1 | Job
11 | Artificial Plants
| Providing artificial plants approved by the Architect with pre painted pots including cost of fixing the plants with wall as per detail drawing and directed by the Architect. | 3 | Nos.
TOTAL ESTIMATED COST OF CIVIL/ID WORK.
Note:
* Before quote the rates, the contractor should first visit the site.
* Above quantities are approximate, subject to increase or decrease as per site.
* Area will be measured from face to face of said job.
* Contractor should submit As built drawings (AutoCAD + print) of the project after completion.

## B - Furniture
EY Lahore - 4th Floor - Furniture
B | FURNITURE WORKS |  |  | Supply |  | INSTALLATION |  | Total | Lead Time | Brand | Remarks
S.No. | DESCRIPTION | Qty | Units | Rate | Amount | Rate | Amount
CUSTOMIZE FURNITURE
1 | CUF-01 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 5 | Nos.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1400mmX300mmX1200mm
2 | CUF-02 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 2 | Nos.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =975mmX300mmX1200mm
3 | CUF-03 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 0 | Nos.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1400mmX650mmX1200mm
4 | CUF-04 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 0 | No.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =900mmX900mmX1200mm
5 | CUF-05 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 2 | Nos.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1200mmX750mmX1200mm
6 | CUF-06 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 0 | Nos.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1600mmX385mmX1200mm
7 | CUF-07 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 0 | No.
6mm+6mm MDF board planter box with rough wood frame and PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1200mmX1575mmX750mm
8 | CUF-08 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 0 | Nos.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =2000mmX600mmX1200mm
9 | CUF-09 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 0 | No.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1500mmX600mmX1200mm
10 | CUF-10 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 3 | Nos.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1400mmX260mmX1200mm
11 | CUF-11 PLANTER
| Providing and Installation of PLANTER consist of following materials: | 3 | Nos.
19mm+19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1400mmX200mmX1200mm
12 | CUF-12 PRINTING STATION
| Providing and Installation of PRINTING STATION consist of following materials: | 0 | No.
100mm high 19mm thick MDF base with Formica pasted and rough wood frame
19mm thick MDF cabinet box with Formica pasted both side with pvc lipping
19mm thick MDF shutter with Formica pasted both sides with pvc lipping
19mm thick MDF shelf with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Base Size =1550mmX600mmX900mm
Hanging Size =2587mmX350mmX950mm
13 | CUF-13 PRINTING STATION
| Providing and Installation of PRINTING STATION consist of following materials: | 1 | No.
100mm high 19mm thick MDF base with Formica pasted and rough wood frame
19mm thick MDF cabinet box with Formica pasted both side with pvc lipping
19mm thick MDF shutter with Formica pasted both sides with pvc lipping
19mm thick MDF shelf with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Base Size =2150mmX600mmX900mm
Hanging Size =3111mmX350mmX950mm
14 | CUF-14 STORAGE CABINET
| Providing and Installation of STORAGE CABINET consist of following materials: | 1 | No.
100mm high 19mm thick MDF base with Formica pasted and rough wood frame
19mm thick MDF cabinet box with Formica pasted both side with pvc lipping
19mm thick MDF shutter with Formica pasted both sides with pvc lipping
19mm thick MDF shelf with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1956mmX600mmX2550mm
15 | CUF-15 LOCKERS
| Providing and Installation of LOCKERS consist of following materials: | 0 | No.
100mm high 19mm thick MDF base with Formica pasted and rough wood frame
19mm thick MDF cabinet box with Formica pasted both side with pvc lipping
19mm thick MDF shutter with Formica pasted both sides with pvc lipping
19mm thick MDF shelf with Formica pasted both sides with pvc lipping
Seating Nich 3" Thk.Foam Over Fabric Fixed With 2" Wide Velcro Tape/Cementex As per drawing and Architect direction
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =8357mmX475mmX2175mm
16 | CUF-16 LOCKERS
| Providing and Installation of LOCKERS consist of following materials: | 1 | No.
100mm high 19mm thick MDF base with Formica pasted and rough wood frame
19mm thick MDF cabinet box with Formica pasted both side with pvc lipping
Seating Nich 3" Thk.Foam Over Fabric Fixed With 2" Wide Velcro Tape/Cementex As per drawing and Architect direction
19mm thick MDF shutter with Formica pasted both sides with pvc lipping
19mm thick MDF shelf with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =8333mmX573mmX2175mm
17 | CUF-17 RECEPTION COUNTER
| Providing and Installation of RECEPTION COUNTER consist of following materials: | 1 | No.
19mm MDF board planter box with PVC lipping on edges
Formica pasted over MDF board box
19mm MDF board shutters with imported formica pasted and pvc lipping on edges
19mm thic MDF shelves with formica pasted and pvc lippings
38mmx50mmx 3100 solid oak wood polish finish strips to be fixed with the gap of 75mm C/C
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1400mmX260mmX1200mm
18 | CUF-18 STORAGE CABINET
| Providing and Installation of STORAGE CABINET consist of following materials: | 1 | No.
100mm high 19mm thick MDF base with Formica pasted and rough wood frame
19mm thick MDF cabinet box with Formica pasted both side with pvc lipping
19mm thick MDF shutter with Formica pasted both sides with pvc lipping
19mm thick MDF shelf with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1063mmX600mmX2550mm
19 | CUF-19 COFFEE COUNTER
| Providing and Installation of PRINTING STATION consist of following materials: | 1 | No.
100mm high 19mm thick MDF base with Formica pasted and rough wood frame
19mm thick MDF cabinet box with Formica pasted both side with pvc lipping
19mm thick MDF shutter with Formica pasted both sides with pvc lipping
19mm thick MDF shelf with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Base Size =1522mmX600mmX900mm
Hanging Size =1522mmX300mmX850mm
20 | CUF-20 PRINTING STATION
| Providing and Installation of PRINTING STATION consist of following materials: | 1 | No.
100mm high 19mm thick MDF base with Formica pasted and rough wood frame
19mm thick MDF cabinet box with Formica pasted both side with pvc lipping
19mm thick MDF shutter with Formica pasted both sides with pvc lipping
19mm thick MDF shelf with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Base Size =933mmX634mmX900mm
Hanging Size =933mmX350mmX950mm
21 | CUF-21 LOCKER BOOTH
| Providing and Installation of LOCKER BOOTH consist of following materials: | 0 | No.
19mm thick MDF base with rough wood frame
75mm thick fabric cladded foam fixed with Velcro tabe
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Base Size =933mmX634mmX900mm
Hanging Size =933mmX350mmX950mm
22 | CUF-22 OPEN SHELVE
| Providing and Installation of OPEN SHELVE consist of following materials: | 2 | No.
18mm thick MDF base with Formica pasted both sides
18mm thick MDF cabinet box with Formica pasted both side with pvc lipping
18mm thick MDF shelf with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =750mmX400mmX1800mm
23 | CUF-23 OPEN SHELVE
| Providing and Installation of OPEN SHELVE consist of following materials: | 2 | No.
16mm thick MDF base with Formica pasted both sides
16mm thick MDF cabinet box with Formica pasted both side with pvc lipping
18mm thick MDF shelf with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1200mmX350mmX1200mm
24 | CUF-24 RACK STAND
| Providing and Installation of RACK STAND consist of following materials: | 1 | No.
19mm Dia 16swg powder coated MS pipe base frame
19mm thick MDF shelf with Formica pasted both sides with 1mm thick pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1050mmX300mmX1350mm
25 | CUF-25 BASE CABINETS
| Providing and Installation of CABINETS consist of following materials: | 0 | No.
100mm high 16mm thick MDF base with Formica pasted both sides
16mm thick MDF cabinet box with Formica pasted both side with 1mm pvc lipping
16mm thick MDF shutter with Formica pasted both sides with pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =600mmX600mmX900mm
Size =750mmX600mmX1200mm
26 | CUF-26 HANGING CABINETS
| Providing and Installation of HANGING CABINETS consist of following materials: | 0 | No.
16mm thick MDF cabinet box with Formica pasted both side with 1mm pvc lipping
16mm thick MDF shutter with Formica pasted both sides with pvc lipping
16mm thick MDF shelf with Formica pasted both sides with 1mm pvc lipping
to be assemble as per detail drawing complete as per drawing with all hardware and directed by Architect.
Size =1400mmX350mmX900mm
27 | WG-05 DUST BIN
| Providing of SS finished Dustbin (20L) of required volume as per the approved design by Architect. | 15 | No.
28 | GRAB RAIL
| Providing and fixing of SS finish Grab Rail as approved by Architect | 4 | No.
29 | WG-11 FLOOR LAMP
| Providing floor lamp as approved by Architect | 1 | No.
TOTAL ESTIMATED COST OF FURNITURE WORK.
with shelves
18mm Thk. Formica Lamination with PVC Lipping with 18mm Deep 16mm Thk. Formica Lamination Base
Note:
* All External Formica/Lamination will be read as imported Formica (As approved by the Architect).
* All Internal Formica/Lamination will be read as (Formite)
* Before quote the rates, the contractor should first visit the site.
* Above quantities are approximate, subject to increase or decrease as per site.
* Before quote the rates, contractor should see detail presentation of Furniture.
* Contractor should submit As built drawings (AutoCAD + print) of the each furniture after completion.

## HVAC
EY Lahore - 4th Floor - HVAC
[5 empty] | MATERIAL |  | LABOUR |  | TOTAL | BRAND/MAKE | LEAD TIMES | REMARKS
S.NO. |  | DESCRIPTION | UNIT | QTY | RATE | AMOUNT | RATE | AMOUNT | AMOUNT Rs.
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of Consultant
1 |  | Unloading, Rigging, lifting, placement & installation of air handling units and fan coil units (OFM items) of different types & capacities complete in all respects, ready to operate with supply and fixing of all accessories, including hanger steel base, vibration isolators, interconnecting power & control wiring with inlet & outlet chilled water connections, drain connection, flexible rubber duct connection etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of Consultant.
| 1.1 | DFCU-01 (as per schedule) | Nos. | 4
| 1.2 | DFCU-02 (as per schedule) | Nos. | 6
| 1.3 | DFCU-03 (as per schedule) | Nos. | 5
| 1.4 | DFCU-04 (as per schedule) | Nos. | 8
| 1.5 | FAHU-03 (as per schedule) | No. | 1
| 1.6 | FAHU-04 (as per schedule) | No. | 1
2 |  | Supply & installation of valves & accessories for AHUs & FCUs (non false ceiling areas only) including supports, hangers, flanges, gas kits, nut & bolts etc. complete in all respects as per specifications, drawings and as per instructions of consultant.
| 2.1 | Ball Valve
| i. | 25mm dia | Nos. | 48
| ii. | 32mm dia | Nos. | 4
| 2.2 | Strainers
| i. | 25mm dia | Nos. | 12
| ii. | 32mm dia | No. | 1
| 2.3 | Balancing Valve (with self sealing measuring nipples)
| i. | 25mm dia | Nos. | 12
| ii. | 32mm dia | No. | 1
| 2.4 | Thermometer 150 mm Height Scale Type (with Thermo well) 0ºC to 60ºC | Nos. | 26
| 2.5 | Pressure Gauge with with Ball Valve & Siphon, Liquid filled Dial type range -ve 5 psi to 100 psi. (100mm dial Size) | Nos. | 26
| 2.6 | 2-Way Motorized Valve with Actuator (0-100% modulating)
| i. | 25mm dia | Nos. | 13
| 2.7 | Isolation valves (for units with Valve box only)
| i. | 25mm dia | Nos. | 24
| 2.9 | Control wiring from controller to sensors, motorized valve and Power wiring from FCP to fan, up to 5 meter radius | Nos. | 13
3 |  | Supply & installation of valve assembly kit included; PICV, isolation valves, bypass, strainer, drain valve, insulated flexible connector (30 cm) braiding type with 2-Way Motorized valve with actuator (0-100% modulating) assembly shall be pre-insulated with threaded ends, etc. complete in all respects as per specifications, drawings and as per instructions of consultant. (false ceiling areas only)
| 3.1 | 25mm dia | Nos. | 12
4 |  | Supply, Installation, testing and commissioning of Duct heaters for DFCUs, complete in all respects ready to operate as per specifications, drawings and as per instructions of consultant.
| i. | 300 x 150 | No. | 1
| i. | 300 x 200 | No. | 3
| ii. | 300 x 250 | Nos. | 6
| iii. | 450 x 250 | Nos. | 1
| iv. | 500 x 200 | Nos. | 5
| vi. | 550 x 200 | Nos. | 7
5 |  | Supply, Installation, testing and commissioning of SCH-40 M.S.(As per ASME & API standard, Heavy Quality with standard SCH 40 wall thickness) pipes & fitting for chilled water circulation system complete with bends, tees, unions, sockets, specials, MS Pipe support, hangers & anchors, M.S. angle, U channel, Roller Support, bolts, rods, clamps, Concrete fasteners etc as required to complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of Consultant.
| 5.1 | 25mm dia | Rm | 70
| 5.2 | 32mm dia | Rm | 50
| 5.3 | 40mm dia | Rm | 25
| 5.4 | 50mm dia | Rm | 30
| 5.5 | 65mm dia | Rm | 10
| 5.6 | 75mm dia | Rm | 5 |  | Rate Only |  | Rate Only | Rate Only
| 5.7 | 100mm dia | Rm | 5 |  | Rate Only |  | Rate Only | Rate Only
6 |  | Supply & installation of closed cell insulation (20 mm thick) with aluminium facing for Internal chilled water pipes, bends, tees, unions, sockets, valves complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
| 6.1 | 25mm dia | Rm | 70
| 6.2 | 32mm dia | Rm | 50
| 6.3 | 40mm dia | Rm | 25
| 6.4 | 50mm dia | Rm | 30
| 6.5 | 65mm dia | Rm | 10
| 6.6 | 75mm dia | Rm | 5 |  | Rate Only |  | Rate Only | Rate Only
| 6.7 | 100mm dia | Rm | 5 |  | Rate Only |  | Rate Only | Rate Only
7 |  | Supply, installation, testing and commissioning of Air Conditioning units Decorative type of different capacities (as per mentioned in schedule) including supply of supports, brackets, rubber isolator, flashing, control wiring & power wiring (connection) in G.I. for external / PVC for internal from outdoor unit to indoor unit complete in all respects ready to operate as per specification, drawings and as per instructions of Consultant.
| 7.1 | AC-01 (as per schedule) | No. | 1
8 |  | Supply, installation, testing and commissioning of refrigerant pipes (liquid + gas) with expended rubber foam insulation 12mm thick, PVC tape wrapping + control wiring from indoor to outdoor for Split type units complete in all respects ready to operate as per specification, drawings and as per instructions of Consultant. | Rm | 35
9 |  | Supply, fabrication, installation & testing of pre-insulated ductwork of polyurethane foam panel with 52Kg/m3 density, 20mm thickness, coated on both sides with 80 micron thick aluminum foil complete with a 2g/m2 layer for internal duct work including manufacturer's aluminum hardware glue, hangers and supports, flexible duct connection, wooden frame, etc. Complete in all respects ready to operate as per drawings, specification and as per instruction of consultant. | Sqm | 350
10 |  | Supply and Installation of acoustical duct sound liner (adhesive with aluminum facing 12mm thick) in supply air duct complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Sqm | 75
11 |  | Supply, fabrication, installation & testing of machine made G.I sheet metal duct for external / exposed area complete in all respects including splitter dampers, guide vanes, flexible duct connection, access door, transformation, plenums chambers, anchors supports & hangers, wooden frame complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Sqm | 10
11 |  | Supply & installation of aluminum fabricated powder coated Fresh & Exhaust Air louvers including supply of wooden frame, rain protection sheet bird mesh etc complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant.
| 11.1 | 250mm x 200mm | Nos. | 2
| 11.2 | 250mm x 250mm | No. | 1
| 11.3 | 350mm x 200mm | No. | 1
12 |  | Supply, Installation of Aluminum fabricated, powder coated Grills, Diffusers and Registers for supply air, return air, exhaust air & fresh air of different sizes (Grade A ) wooden frame, supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant.
| 12.1 | Supply, Return, Fresh, Exhaust Air Register / Diffuser with Damper
| i. | 225mm x 225mm | Nos. | 24
| ii. | 300mm x 300mm | Nos. | 34
| iii. | 375mm x 375mm | Nos. | 3
| 12.2 | Supply, Return, Fresh, Exhaust, Smoke Air Grills / Registers with Dampers
| i. | 150mm x 100mm | Nos. | 25
| ii. | 150mm x 150mm | No. | 3
| iii. | 250mm x 100mm | No. | 1
| iv. | 300mm x 300mm | No. | 2
| 12.3 | Supply & Return Air Linear Slot 6000 Series
| i. | 2 Slot of 20mm | Rm | 30
| 12.4 | Disc Valves with Dampers
| i. | 150mm Dia | Nos. | 14
13 |  | Supply & installation of flexible duct including hangers, jubilee clamp complete in all respects as per specification, drawings & as per instruction of consultant.
| 13.1 | 150mm Dia | Rm | 50
14 |  | Supply & installation of butterfly damper for above flexible duct with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of Consultant.
| 14.1 | 150mm Dia | Nos. | 46
15 |  | Supply, fabrication & installation of pre-insulated Volume Control Damper, blades to be constructed with extruded aluminum in airfoil shape with thermal isolation gape & shall have seals, pvc / aluminum profiles duct connection at both end etc. complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant.
| 15.1 | 150mm x 100mm | Nos. | 1 |  | Rate Only |  | Rate Only | Rate Only
| 15.2 | 150mm x 150mm | Nos. | 1 |  | Rate Only |  | Rate Only | Rate Only
| 15.3 | 200mm x 150mm | Nos. | 1 |  | Rate Only |  | Rate Only | Rate Only
| 15.4 | 200mm x 200mm | No. | 1 |  | Rate Only |  | Rate Only | Rate Only
| 15.5 | 250mm x 150mm | Nos. | 1 |  | Rate Only |  | Rate Only | Rate Only
| 15.6 | 250mm x 200mm | Nos. | 1 |  | Rate Only |  | Rate Only | Rate Only
| 15.7 | 350mm x 150mm | Nos. | 1 |  | Rate Only |  | Rate Only | Rate Only
| 15.8 | 350mm x 200mm | No. | 1 |  | Rate Only |  | Rate Only | Rate Only
16 |  | Supply & installation of Volume Control Damper in 16 SWG G.I sheet metal with gas kits, nut bolts, complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant.
| 16.1 | 150mm x 100mm | Nos. | 1 |  | Rate Only |  | Rate Only | Rate Only
17 |  | Supply, installation of Motorized Fire Damper with gas kits, nut bolts, including controller & control wiring, complete in all respects, ready to operate as per specification, drawings & as per instruction of Consultant.(UL 555s)
| 17.1 | 300mm x 250mm | Nos. | 2
18 |  | Supply, Installation, testing and commissioning of uPVC (Sch 40.) drain pipe insulated with 10mm thick rubber foam insulation including clamps, bends, tees, drain plugs, sockets, protection treatment, PVC tape wrapping, hanger & supports etc, complete in all respects as per specifications, drawings & as per instructions of Consultant.
| 18.1 | 25mm dia | Rm | 90
| 18.2 | 32mm dia | Rm | 60
| 18.3 | 40mm dia | Rm | 5
| 18.4 | 50mm dia | Rm | 5
19 |  | Painting & Identification work on chilled water pipes, duct, supports, hangers, platform of condensing units etc. complete in all respects with one coat of ICI make Red lead oxide primer & two coats of ICI make enamel paint as per instruction of Consultant. | Job. | 1
20 |  | Testing, balancing and commissioning of water side of the system (from independent agency) complete in all respects including flow measurement & balancing, temp, pressure, electrical data of related equipment etc. as per specifications and as per instructions of Consultant. | Job. | 1
21 |  | Testing, balancing and commissioning of air side of the system complete (from independent agency) in all respects including air measurement & balancing, temp, pressure & electrical data of related equipment etc. as per specifications and as per instructions of Consultant. | Job. | 1
22 |  | Making of Shop drawings on Auto CAD latest version with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment as per instruction of consultant. | Job. | 1
Total Cost of ACMV Works Rs.
Cost of GST (On Material) and PST (On Installation)
Grand Total of ACMV Works Rs.
Note:
1) | Contractor to add core cutting cost (as per site requirement) in above rates.
2) | Equipment RCC pad / plateform / civil work not included in this BOQ.
3) | Any HVAC work related to existing HVAC system is not included in this BOQ.
4) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
5) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## PLUMBING
EY Lahore - 4th Floor - Plumbing
S.No. |  | Description | Unit | Qty | Material |  | Labour |  | Total | BRAND/MAKE | LEAD TIMES | REMARKS
[5 empty] | Rate | Amount | Rate | Amount | Amount Rs.
SECTION - 01, PLUMBING FIXTURES.
Supply and Installation of plumbing fixtures & faucets complete in all respects including all accessories, support, hangers, etc. ready to use as per specifications, drawings and instructions of Consultant.
1.1 |  | European style water closet wall hung type with seat cover, concealed flush tank with frame, cover plate, C.P. connector, thimble, etc and fixing accessories.
| i. | Type - EWC-WH | Nos. | 4
1.2 |  | European style water closet wall hung type with seat cover, concealed flush tank with frame, cover plate, for disabled person S.S bracket, grap bar support, C.P. (chrome plated) connector, thimble, etc.
| i. | Type - EWC-WH | Nos. | 4
1.3 |  | Toilet Hand Spray with flexible chain & telephone type shower Including tee stop cock etc. complete in all respect.
| i. | Type - TS | Nos. | 8
1.4 |  | Wash basin (WB) including bottle trap, waste, stop cocks, etc.
| i. | Type - WB | Nos. | 4
| ii. | Type - WB (Vanity) | Nos. | 8
1.5 |  | Wash basin hot and cold water mixer, etc.
| i. | Type - WB | Nos. | 4
| ii. | Type - WB (Vanity) | Nos. | 8
1.6 |  | Stainless steel kitchen sink including stop cocks, P-trap / Bottle trap, waste pipe etc complete in all respects.
| i. | SK - 1, 500 x 500 mm single bowl and single drainer. | No. | 1
1.7 |  | Sink hot and cold water mixer, etc.
| i. | SK - 1 | No. | 1
1.8 |  | Toilet accessories complete set.
| i. | Soap Dispenser | Nos. | 12
| ii. | Towel Rail | Nos. | 8
| iii. | Paper Holder | Nos. | 8
| iv. | Double Coat Hooks | Nos. | 8
| v. | Hand Dryer | Nos. | 4
| vi. | Grab Rail for Handicapped Toilets | Nos. | 4
Sub Total Rs.
SECTION-02 WATER SUPPLY SYSTEM.
Supply, installation, testing and commissioning of complete pipe work for cold and hot water system including all accessories required to complete systems ready to operate as per specification, drawings & instruction of Consultant.
2.1 |  | Polypropylene Random PP-R pipes PN 20 and fittings with fusion jointing along with all types of unions, tees, bends, sockets, clamps, hangers, supports, sleeves, masking plates, chiseling, making holes making good, excavation, bedding backfilling as required complete in all respect.
| i. | Dia. OD 25 mm | Rm. | 25
| ii. | Dia. OD 32 mm | Rm. | 20
| iii. | Dia. OD 50 mm | Rm. | 15
2.2 |  | Same as item # 2.1 but for hot water supply with Polypropylene Random PP-R (PN -25) with Aluminium foil.
| i. | Dia OD 25 mm | Rm. | 40
| ii. | Dia. OD 32 mm | Rm. | 5
2.3 |  | Open cell rubber foam insulation 3/8" thick & pvc tape wrapping for hot water pipes.
| i. | Dia OD 25 mm | Rm. | 30
| ii. | Dia. OD 32 mm | Rm. | 5
2.4 |  | Brass body gate valves / ball valves with unions.
| i. | Size 25 mm (3/4") | Nos. | 2
| ii. | Size 32 mm (1") | Nos. | 2
| iii. | Size 40 mm (1-1/4") | Nos. | 2
| iv. | Size 50 mm (1-1/2") | Nos. | 2
2.5 |  | Hot water storage heater (Electric) suitable for 30 psi working pressure including thermostat, inlet/outlet connection. Pressure relief valve.
| ii. | HWE-80 (80 Litres Storage Capacity) | Nos. | 2
Sub Total Rs.
SECTION-03 SOIL, WASTE VENT AND RAIN WATER DRAINAGE SYSTEM
Supply, fixing, testing and commissioning of equipment, pipe work required to complete the soil, waste, vent and rain water systems in all respects with accessories ready to operate as per specifications, drawings and instructions of Consultant.
3.1 |  | uPVC pipes of approved make along with specials, fittings, bends, wye, tees, sockets, flexible connectors, sleeves, masking plates, chiseling, making hole, excavation, backfilling making good where as required jointing with rubber ring seal.
| i. | Dia. 32 mm | Rm. | 15
| ii. | Dia. 50 mm | Rm. | 2
| iii. | Dia. 100 mm | Rm. | 5
3.2 |  | Floor trap including S.S grating floor trap, inlet outlet connection complete in all respects.
| i. | FT- with 100 mm P - trap | Nos. | 13
3.3 |  | Cleanout for soil, waste pipes of approved make.
| i. | For 100 mm dia. Pipe with SS floor cover plate (FCO) | Nos. | 4
Sub Total Rs.
SECTION-04 SUNDRIES
Contractor will priced the sundries items for all Plumbing & Sanitary (P&S) services as per specifications, drawings and instruction of consultant.
4.1 |  | Submittals, samples, shop drawings, inspections, As-Built drawings, operation and maintenance manuals and the like as required by specification. | Job. | 1
4.2 |  | Testing, and commissioning entire P&S installation as per Engineer's approval. | Job. | 1
Sub Total Rs.
|  | Total Cost of All Sections Rs. |  |  |  | 0 |  | 0 | 0
Cost of GST (On Material) and PST (On Installation)
Grand Total of Plumbing Works Rs.

## FIRE
EY Lahore - 4th Floor - Fire
S.No. |  | Description | Unit | Qty | Material Rate | Amount | Labour Rate | Amount | Total Amount Rs. | BRAND/MAKE | LEAD TIMES | REMARKS
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire hydrant system including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of Consultants.
1 |  | MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, supports and hangers, sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
| i. | Dia 25 mm | Rm. | 180
| ii. | Dia 32 mm | Rm. | 25
| iii. | Dia 40 mm | Rm. | 10
| iv. | Dia 50 mm | Rm. | 45
| v. | Dia 65 mm | Rm. | 40
| vi. | Dia 75 mm | Rm. | 2
2 |  | Sprinkler Heads
| i. | Sprinkler Upright type, quick response K = 5.6 (Opening Temperature 57ºC) | Nos. | 26
| ii. | Sprinkler Pendent type concealed with CP escutcheon face cover plate, quick response K = 5.6 (Opening Temperature 57ºC) | Nos. | 35
| iii. | Corrugated stainless steel hose with stainless steel braid for pendent type sprinklers 3ft length | Nos. | 35
3 |  | Fire extinguishers with fixing accessories.
| i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 3
| ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 3
4 |  | Supply, installation, testing & commissioning of Novec 1230 fire fighting system for MCR including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
| 4.1 | MCR room (1500 cubic feet) | 1 | Job.
5 |  | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1
6 |  | Submittals, samples, shop drawings, inspections, As-built drawings, operation and maintenance manuals and the like as required by specifications. | Job. | 1
7 |  | Painting, identification and tagging to the installations and equipments. | Job. | 1
8 |  | Flushing of entire fire pipe work according to (NFPA-13). | Job. | 1
9 |  | Testing, and commissioning of entire fire fighting installation as per Consultant's approval. | Job. | 1
Total Cost of Fire Suppression Services Rs.
Cost of GST (On Material) and PST (On Installation)
Grand Total of Fire Works Rs.

## Elect Summary
EY Lahore - 4th Floor - Electrical Summary
S.# | DESCRIPTION | SUPPLY (Rs.) | INSTALLATION (Rs.) | TOTAL (Rs.)
1 | SECTION - A WIRING / WIRING ACCESSORIES
2 | SECTION - B CABLE CONTAINMENT
3 | SECTION - C SWITCHES & SOCKETS
4 | SECTION - D MAIN / SUB-MAIN CABLES
5 | SECTION - E DISTRIBUTION BOARDS |  |  |  | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS
6 | SECTION - F LIGHTING FIXTURES
7 | SECTION - G FIRE ALARM SYSTEM
8 | SECTION - H PUBLIC ADDRESS SYSTEM
9 | SECTION - I ACCESS CONTROL SYSTEM
10 | SECTION - J SHOP DRAWINGS / AS-BUILT DRAWINGS
11 | SECTION - K PERSONAL PROTECTIVE EQUIPMENTS
12 | SECTION - L TEMPORARY CCTV FOR MONITORING
| Total Amount (Rs.) | 0 | 0 | 0
GST
PST
Grand total (including all taxes)
Notes: ● Contractor is advised to inform missing items (if any) in BOQ at time of submitting this tender. No escalation will be considered at time of execution of work. ● Owner can supply any material of Contractor scope at any stage and its cost will be completely deleted from Contractor scope without any kind of adjustment. ● Contractor should mark the selected brands and vendors in approved manufacturer list with submission of Tender Documents. ● Owner / Consultant have all the rights to select any brand / vendor from provided approved manufacturer list, Contractor shall not finalize any brand / vendor without written approval from consultant / owner. ● Upon completion of 1st fix electrical works, the fit-out contractor should request for first fix inspection by the Fit-Out Team, before closing the false ceiling through ● At the time of 2nd fix Main Distribution Board will be connected up and the wiring will be tested through Megger Test in front of the Fit-Out Team. The report of the same will be duly signed by the Occupant’s Contractor/Project Manager and the Fit-Out Team. Megger Test with KC number punched along with valid calibration certificate of megger test must be submitted. ● Fit-Out contractor to submit Electrical As-Built drawings and other relevant documents immediately after completion of works.
SECTION - G VOICE & DATA COMMUNICATION SYSTEM
Total Amount (Rs.) Sec - G (CARRIED FORWARD TO SUMMARY)
SECTION - H CCTV SYSTEM (IP BASED)
Total Amount (Rs.) Sec - H (CARRIED FORWARD TO SUMMARY)
SECTION - I FIRE ALARM SYSTEM
Fire Repeater Panel along with termination of all Control / Signal cables complete in all aspects. Panel to have all loops marked in distinguishable colors with individual LED's
Total Amount (Rs.) Sec - I (CARRIED FORWARD TO SUMMARY)
SECTION - J INTELLIGENT LIGHTING CONTROL SYSTEM
Total Amount (Rs.) Sec - J (CARRIED FORWARD TO SUMMARY)
SECTION - K PUBLIC ADDRESS SYSTEM
60W - 2 Channel Power Amplifier (For Office) operating at 220V, AC suitable for rack mounting incorporates two audio line level inputs: a Music input and a priority call input. A built-in relay switches the amplifier from the music input of priority call input.
Total Amount (Rs.) Sec - K (CARRIED FORWARD TO SUMMARY)
SECTION - L IP ACCESS CONTROL SYSTEM
|  | 1 | No
|  | 10 | No
|  | 10 | No
|  | 10 | No
|  | 20 | No
6 |  | 8 | No
7 |  | 1 | Job
8
Total Amount (Rs.) Sec - L (CARRIED FORWARD TO SUMMARY)
SECTION - M SHOP DRAWINGS / AS-BUILT DRAWINGS
Total Amount (Rs.) Sec - M (CARRIED FORWARD TO SUMMARY)
SECTION - N PERSONAL PROTECTIVE EQUIPMENTS
Total Amount (Rs.) Sec - N (CARRIED FORWARD TO SUMMARY)

## Elect BOQ
EY Lahore - 4th Floor - Electrical
S.# | DESCRIPTION | QTY | UNIT | SUPPLY |  | INSTALLATION |  | TOTAL (Rs.) | Brand | Lead Time | Remarks
|  |  |  | RATE (Rs.) | AMOUNT (Rs.) | RATE (Rs.) | AMOUNT (Rs.)
SECTION - A WIRING / WIRING ACCESSORIES
Supply, Installation, Testing & Commissioning of the following items including all material, labour & tools required for completion of work as per item description, specifications & drawings including cutting, chiseling, making good and all necessary accessories such as bends, junction boxes, conduit sockets, earth connecting point connectors, etc. as shown on drawings, specifications and approval by the Engineer. Complete in all respects. Note: - The cost of wiring items shall includes Imported Fire Rated WAGO or equivalent Connectors and flexible G.I conduit with PVC Coating of appropriate size on each light point. - The circuit wire drop shall be sufficient as per ceiling levels. - The wiring shall be done with LSZH with 450/750 volts to BS 6004. - Megger Test of each circuit to be done by the Contractor. - Wiring for Occupancy Sensor shall be included in light wiring. - All General Wiring grade should be 450/750 copper with green/yellow Color. - Surface conduiting wherever required shall be done in decorative / aesthetic manner. - Wherever the circuits are running in cable tray, it will enter / leave tray using proper glands / Junction boxes (IP44). The cost of all such accessories to be included in wiring cost. - All electrical circuits and power outlets shall be numbered (i.e. circuit number and distribution board number) and the circuit schedule of the distribution board must accurately reflect the installation. The load across all phases must be balanced.
1 | Circuit wiring from DB to Switchboard including any wiring from switch board to switch board with 2x2.5 Sq.mm Cu/PVC + 2.5 sqmm as ECC wires in 25mm dia PVC conduit / Cable Tray as shown in drawings. | 9 | No.
2 | Wiring for light point from switch board to first light point / PIR Sensor with phase 1.5 Sq.mm, common neutral 2.5 Sq.mm and common ECC 2.5 Sq.mm, in 25mm dia PVC conduit as shown on drawings. | 47 | No.
a | Point to Point wiring using the same wires & conduit size as mentioned in the above item. | 130 | No.
3 | Wiring for Group Control light fixtures from DB to first light point with 2x2.5 Sq.mm Cu/PVC+ 2.5 sqmm as ECC wires in 25mm dia PVC conduit / Cable Tray as shown in drawings. | 4 | No.
a | Point to Point wiring using the same wires in 25mm dia PVC conduit / Cable Tray as shown in drawings. | 40 | No.
4 | Emergency Circuit wiring from DB to First light point / Switchboard including any wiring from switch board to switch board with 2x2.5 Sq.mm Cu/PVC+ 2.5 sqmm as ECC wires in 25mm dia PVC conduit / Cable Tray as shown in drawings. | 4 | No.
a | Point to Point wiring using the same wires in 25mm dia PVC conduit / Cable Tray as shown in drawings. | 46 | No.
7 | Wiring of 13A/15A Switch Socket units (RAW Power) from DB to first outlet including wiring within same technology box / adjacent power outlets in separate back boxes with following size of 1-core PVC wires in already laid floor trunking under wall / floor as shown in the drawings.
a | 2 x 4 Sq.mm + ECC 1 x 4 Sq.mm | 21 | No.
b | Outlet to Outlet wiring using the same wires & conduit size as mentioned in the above item. | 59 | No.
c | Within Floor Box outlet to Outlet wiring using the same wires & conduit size as mentioned in the above item. | 98 | No.
8 | Wiring of 20A DP Switch socket unit for Hand dryer from DB to socket outlet with 2 x 4 Sq.mm Cu/PVC + ECC 1 x 4 Sq.mm Cu/PVC size PVC wires in 25mm dia PVC conduit as shown on drawings. | 4 | No.
9 | Wiring of 20A DP Isolator for Electric Heater / DFCU / Fan from DB to Isolator with 2 x 4 Sq.mm Cu/PVC + ECC 1 x 4 Sq.mm Cu/PVC size of wires in 25mm dia PVC conduit / Cable Tray as shown on drawings. | 30 | No.
10 | Wiring of 25A TP Isolator for VRF Unit outdoor from DB to Isolator with 3 x 4 Sq.mm Cu/PVC + ECC 1 x 4 Sq.mm Cu/PVC size of wires in 25mm dia PVC conduit / Cable Tray as shown on drawings. (Outdoor located at GF) | 1 | No. |  | Rate Only |  | Rate Only | Rate Only
11 | Wiring of 32A TP Isolator for Return Air Fan/AHU Units from DB to Isolator with 4C-6 Sq.mm Cu/PVC/PVC + ECC 1C-6 Sqmm Cu/PVC size of wires in 32mm dia PVC conduit / Cable Tray as shown on drawings. | 1 | No. |  | Rate Only |  | Rate Only | Rate Only
12 | Wiring of 32A 3-Pin Industrial Socket for Comm. Racks from DB with 3 x 4 Sqmm Cu/PVC size of wires in 25mm dia PVC conduit / Cable Tray as shown on drawings. | 3 | No.
13 | Wiring of 16A 3-Pin Industrial Socket for Comm. Racks from DB with 3 x 4 Sqmm Cu/PVC size of wires in 25mm dia PVC conduit / Cable Tray as shown on drawings. | 3 | No.
Note: - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. - The ECC to be run with each circuit shall be loop-in and loop-out type, joints are not allowed. - All the cables shall be colour coded according to phases / types of services.
Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY)
SECTION - B CABLE CONTAINMENT
1 | Supply & Installation of following sizes of PVC/UPVC Conduits including all accessories such as bends, sockets, j-boxes, flexible conduits, metal saddles e.t.c for Main / Sub Main Power, Telephone & Data Cables, concealed / surface on wall as per design drawings.
a | 25mm dia PVC Conduit | 225 | Rm.
b | 32mm dia PVC Conduit | 200 | Rm.
c | 50mm dia PVC Conduit | 150 | Rm.
d | 25mm dia Al anodized EMT Conduit (20 SWG) | 150 | Rm.
e | 25mm dia Stainless Steel Conduit (18 SWG, Grade 304) | 1 | Rm. |  | Rate Only |  | Rate Only | Rate Only
f | 25mm dia Flexible GI Conduit with PVC Coating | 50 | Rm.
2 | Supply & Installation of following MS Powder Coated 16 SWG Ceiling / Floor / Wall Pull Boxes for data / voice / power / UPS circuits, recessed on wall or column as per design drawings. Complete in all respect.
a | 450mm x 450mm x 50mm (Small Wiring & Data) (Floor / Ceiling Mounted) | 2 | No.
b | 300mm x 300mm x 50mm (Power & Lighting) (Floor / Ceiling Mounted) | 8 | No.
c | 200mm x 200mm x 50mm (Power & Lighting) (Floor / Ceiling Mounted) | 8 | No.
3 | Supply & Installation of following sizes of 16 SWG Perforated Powder Coated G.I Cable Tray & 18 SWG Solid Cover (4 feet cover) with prime quality Japanese standard JIS 3302 36-38 microns Galvanized iron steel in line with NEMA standards with min. 36 microns Zinc overlap coating, duly Painted after degreesing, derusting, phosphating and antirust primer including all installation accessories such as rawal bolts, supporting hangers, brackets, elbows, tee & mounting accessories etc. Note: - Color Printed Tags to be provided at every 3 Meter Length. - U-shaped fischer plates to be used for joints. - Earth bonding to be done with every joint. - G.I adapters with smooth finishing must be installed on the cable tray to provide passage to the lighting and power circuits. - Thread rods cannot be installed directly to the ceiling. Suspension system Type TR60 to be provided cable tray shall be directly clamped with the Iron Girder (Refer Details).
a | 300mm x 50mm (For Data Cables) (With Ceiling Mounted Hanging Accessories) | 100 | Rm.
b | 300mm x 50mm (For Lighting and Power Cables) (With Ceiling Mounted Hanging Accessories) | 150 | Rm.
5 | Supply & Installation of Imported Floor Outlet Boxes without face plates made of 16 SWG G.I Sheet, recessed in ground as per design drawings.
a | Type-A (4 No. Face Plates including 4 No. 13A International Switch Socket, 4 No. RJ-45) | 40 | No.
b | Type-B (4 No. Face Plates including 2 No. 13A International Switch Socket, 1 No. Micro HDMI Port and 2 No. RJ-45 Data/Voice Duplex) | 4 | No.
c | Type-C (4 No. Face Plates including 3 No. 13A International Switch Socket 1 No. RJ-45 Data/Voice Simplex) | 1 | No. |  | Rate Only |  | Rate Only | Rate Only
Note: 1. Core Cutting between floors for interconnectivity is in Civil Scope. 2. Contractor is advised to confirm the sizes, running lengths and termination as per site conditions before commencement of work. All the conduits / cable tray crossings through partition walls shall be properly sealed by fire retardant material after installation. 3. Conduitings will also be laid in LL provided shafts for interconnectivity between floors.
Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY)
SECTION - C SWITCHES & SOCKETS
Supply & Installation of following Light Switches, Power Outlets, DP Switches, Isolators & Industrial Sockets including 16 SWG sheet steel back boxes (Selected Series for Switch socket outlet is Clipsal Pieno for Switch, Vivace for Socket or equivalent)
1 | 10A, 220V One Gang Switch Unit | 7 | No.
2 | 10A, 220V Two Gang Switch Unit | 11 | No.
3 | 10A, 220V Three Gang Switch Unit | 6 | No.
4 | 13A 3-Pin Flat Simplex Switch Socket unit | 1 | No. |  | Rate Only |  | Rate Only | Rate Only
5 | 13A 3-Pin Flat Duplex Switch Socket unit | 4 | No.
6 | 13A International Switch Socket unit (For Raw Power) | 170 | No.
7 | 15A 3-Pin Round Switch Socket Unit (For Raw Power) | 6 | No.
8 | 20A DP Switch with Neon Indication Light (For Hand Dryer) | 4 | No.
9 | 20A DP Isolator (For Electric Water Heater, DFCU) (Kavacha Series) | 30 | No.
10 | 16A, 3-Pin Industrial Socket with Plug for Comm. Racks | 3 | No.
11 | 32A, 3-Pin Industrial Socket with Plug for Comm. Racks | 3 | No.
12 | Blank Plate with Micro HDMI Port pre-installed | 6 | No.
13 | 220V, Wi-Fi Two Gang Flat Switch Unit with LED indication | 1 | No. |  | Rate Only |  | Rate Only | Rate Only
14 | Ceiling suspended cameras mounting poles (Aluminum finish) adjustable 2ft to 4ft. | 23 | No.
15 | Stand Alone Passive Infrared + Ultrasonic Motion Sensor (Ocupancy Sensor) for Lights having following specifications: Coverage Range : 360 ° Operating Voltage : 230 V AC Timing Range : 5 sec to 20 minutes Connection : Parallel Switching Mode : Auto IP Value : IP 21 (min) | 8 | No.
Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY)
SECTION - D MAIN / SUB-MAIN CABLES
Supply, Installation, Testing and Commissioning of following sizes of Low Smoke Zero Halogen (LSZH) or Low Smoke and Fume (LSF) with 120 minutes Fire Resistant 600/1000V grade Copper Cables in already installed cable tray, conduit etc. Including all accessories, lugs, glands etc. complete in all respect as shown on drawing. Note: - The LV Power cables to be 600/1000 V BS 6346 & IEC 60502. - All power Cables to be LSZH or LSF. - Appropriate Size of Cable Brass Glands and Lugs to be used for termination. - Thread rods cannot be installed directly to the ceiling. Any conduit required to be hanged shall be clamped with the Iron Girder using Type TR60. (Refer Details). - Contractor is instructed to confirm the cable running lengths and termination as per site conditions before commencement of work. - Imported Lugs and Connectors shall be used in LV Cables. - Megger Test of all LV Cables to be done by contractor.
1 | From TAP-OFF TO MDB-4F(A) 4C-16 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 10 | Rm.
2 | From TAP-OFF TO MDB-4F(B) 4C-16 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 10 | Rm.
3 | From MDB-4F(A) TO DB-HVAC-4F(A) 4C-16 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 8 | Rm.
4 | From MDB-4F(B) TO DB-HVAC-4F(B) 4C-16 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 8 | Rm.
5 | From MDB-4F(A) TO DB-LP-4F(A) 4C-10 Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 7 | Rm.
6 | From MDB-4F(B) TO DB-LP-4F(B) 4C-10 Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 7 | Rm.
7 | From MDB-4F(A) TO DB-MCR 4C-10 Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 30 | Rm.
8 | From MDB-4F(B) TO DB-MCR 4C-10 Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 55 | Rm.
9 | From DB-MCR TO UPS 2 x 1C-6 Sqmm Cu/PVC + ECC 1C-6 Sqmm Cu/PVC | 10 | Rm.
10 | From MCR RACKS TO EARTH CONNECTION POINT ECC 1C-6 Sqmm Cu/PVC | 40 | Rm.
Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY)
| SECTION - E DISTRIBUTION BOARDS | [10 empty] | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS | SECTION - E DISTRIBUTION BOARDS
Supply, Installation, Testing & Commissioning of following Distribution Boards as shown on drawing made with 14 SWG sheet steel housing including all installation accessories such as Rovel bolt etc. Complete in all respects. Note: - All the DB should be front accessible and maintainable. - Cost of Power Supply for KNX Based Lighting Control Relay shall also be included in Distribution Board cost. - The transportation and placement of DBs upto dedicated location is also included in the work scope, complete in all respects including levelling, grouting etc. - Laser engraved tags required as mention in SLDs - Space for circuit tagging required with permanent installation on protective sheet via rivets - 20% space required in DB for future provision - Tin platted Imported Cu bus bar with heat shrink color coded sleeves to be used. - Hindged protective metallic door required with knob/handle. - Braided Door earth required. - Lockable handle required for main door. - As-built drawing pocket. - Cable hanging arrangement. Minimum One Year Warranty Required from date of successful comissioning on site.
1 | BREAKER BOX | 2 | No.
2 | MDB-4F(A) | 1 | No.
3 | MDB-4F(B) | 1 | No.
4 | DB-LP-4F(A) | 1 | No.
5 | DB-LP-4F(B) | 1 | No.
6 | DB-HVAC-4F(A) | 1 | No.
7 | DB-HVAC-4F(B) | 1 | No.
8 | DB-MCR | 1 | No.
| Total Amount (Rs.) Sec - E (CARRIED FORWARD TO SUMMARY) | [10 empty] | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY)
SECTION - F LIGHTING FIXTURES
Supply,Installation, Testing & Commissioning of the following lighting fixtures complete with driver and specified lamps, installation and hanging accessories upto 1 meter length for all pendant lights as per drawings and specificaion complete in all respect. (Refer Drawing Light Fixture Schedule) Note: - Color temperature will be as per Architect's requirement. - Efficacy of light fixtures shall be more than 100 Lumens / Watt. - 3 Year Replacement Warranty is required both for the fixture and driver. - Power Factory shall be 0.9. - Minimum Operational life should be more than 50,000 Hours.
1 | D1- Downlight LED 10 watt Suspended | 2 | No.
2 | D2- Downlight LED 20 watt Suspended | 14 | No.
3 | D3- Downlight LED 20 watt Suspended | 14 | No.
4 | D4- Downlight LED 10 watt Suspended | 5 | No.
5 | D5- Downlight LED 15 watt Suspended | 80 | No.
6 | D6- Downlight LED 14 watt Recessed | 44 | No.
7 | D7- Spotlight LED 7 watt Recessed | 20 | No.
8 | D8- Downlight LED 12 watt Recessed | 16 | No.
9 | L1- Linear LED 40 watt Suspended | 6 | No.
10 | L2- Linear LED 80 watt Suspended | 4 | No.
11 | L3- Linear LED 120 watt Suspended | 13 | No.
12 | L4- Linear LED 20 watt (2w/mtr) Recessed as per Architect Design | 2 | Lot.
13 | L5- Linear LED 80 watt Suspended as per Architect Design | 1 | No. |  | Rate Only |  | Rate Only | Rate Only
14 | E1- Exit Light LED 3 watt with Built-in Battery Backup (including all direction signage) | 7 | No.
15 | E2- Emergency LED 3 watt with Built-in Battery Backup (including Wide and Narrow Beam) | 40 | No.
| Total Amount (Rs.) Sec - F (CARRIED FORWARD TO SUMMARY) | [10 empty] | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY) | Total Rs. Sec-E (CARRIED FORWARD TO SUMMARY)
SECTION - G FIRE ALARM SYSTEM
Supply, Installation of following items for Addressable Fire Alarm System comprising of following equipments including all accessories required for the completion of the system in all respects. Cables shall be Fire retardant, Low Smoke, Zero Halogen and must comply BS 6387 standard
1 | Supply & wiring for whole Fire Alarm System using 2C, 1.5 Sq.mm Fire Resistant Shielded Cable (Fire Rating for 2 hours) in 25mm Al EMT conduit from fire alarm control panel to all sensors & devices including all installation accessories. Complete in all respects. Cable should comply below standard: Fire retardant, Low Smoke, Zero Halogen cable BS 6387 | 300 | Rm.
2 | Supply & wiring for power of FACP using 2C, 2.5 Sq.mm PVC cable with 25mm dia Al EMT Conduit. | 30 | Rm.
Note: 1) The given quantities are slightly higher then those on drawings, this includes spare and contingencies as well. 2) Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - G (CARRIED FORWARD TO SUMMARY)
SECTION - H PUBLIC ADDRESS SYSTEM
Supply, Installation, of following items for Public Address System as described below including all accessories. Complete with mounting brackets, wiring, adapters etc.
1 | Supply and Installation of of Wiring for Public Address / Back Ground Music System using 2C, 1.5 Sq.mm flexible Speaker Cable as per zoning layout shown in drawings in 25 mm dia PVC conduit. Complete in all respects. | 200 | Rm.
Note: - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. - The Bidder shall provide the complete Technical Literature for the system offered.
Total Amount (Rs.) Sec - H (CARRIED FORWARD TO SUMMARY)
SECTION - I ACCESS CONTROL SYSTEM
Supply, Installation testing and Commisioning of following items for IP Access Control System (with features of Bio Metric,Face Recognization & RFID for authorization as well as attendance) as described below including all accessories. Complete with mounting brackets, wiring, adapters etc.
1 | Supply, Installation and connection 22AWG 4 cores stranded Recommended (LSZH) – Belden or equivalent for 12/24 DC power wiring in 25mm dia PVC conduit / already laid cable tray including all accessories as per specifications and drawings. NOTE: Running distances must not exceed 150 meters @ 24VDC. | 150 | Rm.
2 | Supply, Installation and connection 22/23 AWG 6 cores stranded flexible Recommended (LSZH) – Belden or equivalent for access control data wiring in 25mm dia PVC conduit / already laid cable tray including all accessories as per specifications and drawings. | 250 | Rm.
3 | Supply and Wiring of CAT-6, UTP Cables from Door Controller to all devices as shown in the schematic diagram in 25mm dia PVC Conduit, including termination and tagging at both ends. Complete in all respects. | 1 | Coil. |  | Rate Only |  | Rate Only | Rate Only
Note: - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. - The Bidder shall provide the complete Technical Literature for the system offered.
Total Amount (Rs.) Sec - I (CARRIED FORWARD TO SUMMARY)
SECTION - J SHOP DRAWINGS / AS-BUILT DRAWINGS
1 | Preparation of shop drawings and as-built drawings of all electrical and allied works after final approval from the consultant/client. 1) Submission of as-built drawings 2 sets after work completion of each floor and 3 sets & soft copy of complete electrical works after final commissioning of project. Approval of final bills are subject to completion of as built drawings. 2) Documents including the Operation and Maintenance Manuals. 3) Testing Reports and Measurement Sheets. 4) Warranty certificates for products. | 1 | Job
Total Amount (Rs.) Sec - J (CARRIED FORWARD TO SUMMARY)
SECTION - K PERSONAL PROTECTIVE EQUIPMENTS
1 | Include below as billable item: Provision of PPEs for clients, consultants and contractors with following while doing construction: Cotton Dangree / Coverall color: Light Grey Steel toe Shoes Jaguar / Catapiller / Color: Black Safety Helmet Economical with "chin strap" / Color: Blue / White / Red | 1 | Job
Total Amount (Rs.) Sec - K (CARRIED FORWARD TO SUMMARY)
SECTION - L Temporary CCTV for Monitoring
1 | Supply & Installation of Cat 6 Cable for temporary CCTV | Coil | 2
2 | Supply & Installation of 2MP Camera | Nos | 8
3 | Supply & Installation of 8 Port POE Switch | Nos | 1
4 | Supply & Installation of 8 Channel NVR | Nos | 1
5 | Supply & Installation of 4U Rack | Nos | 1
6 | Supply, Installation & commissioing of Wifi Router/Modem with Fiber Port | Job | 1
Total Amount (Rs.) Sec - L (CARRIED FORWARD TO SUMMARY)