## Table 1
Bill of Quantities
ACMV WORKS
Meezan Bank Head Office | [7 empty] | 2023-03-14
Karachi. |  | Only costing
S.NO. | DESCRIPTION | UNIT | QTY | MATERIAL |  | LABOUR |  | TOTAL
|  |  |  | RATE | AMOUNT | RATE | AMOUNT | AMOUNT Rs.
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of Consultant
1 | Unloading, rigging, lifting, installation, testing and commissioning of OWNER SUPPLIED Modular type Air Handling Units with VFD of different capacities complete in all respects, ready to operate with supply and fixing of all accessories, including hanger steel base, vibration isolators, including interconnecting power & control wiring (terminations) with inlet & outlet chilled water connections, drain connection, flexible rubber duct connection etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
1.1 | GF-MAHU-01 | No. | 1 | 25000 | 25000 | 40000 | 40000 | 30000
1.2 | FF-MAHU-01 | No. | 1 | 30000 | 30000 | 45000 | 45000 | 50000
1.3 | TF-MAHU-01 | Nos. | 5 | 30000 | 150000 | 50000 | 250000 | 200000
2 | Supply & installation of valves & accessories for MAHUs including supports, hangers, flanges, gas kits, nut & bolts etc. complete in all respects as per specifications, drawings and as per instructions of consultant.
2.1 | Butterfly Valve
i. | 2.5" dia (Lever Type) | Nos. | 4 | 7000 | 28000 | 4000 | 16000 | 44000
ii. | 3" dia (Lever Type) | Nos. | 4 | 8500 | 34000 | 4000 | 16000 | 50000
iii. | 4" dia (Gear Operated) | Nos. | 20 | 9000 | 180000 | 5000 | 100000 | 280000
2.2 | Strainers
i. | 2.5" dia | No. | 1 | 19000 | 19000 | 4000 | 4000 | 23000
ii. | 3" dia | No. | 1 | 20000 | 20000 | 4000 | 4000 | 24000
iii. | 4" dia | Nos. | 5 | 30000 | 150000 | 5000 | 25000 | 175000
2.3 | Balancing Valve (with self sealing measuring nipples)
i. | 2.5" dia | No. | 1 | 50000 | 50000 | 4000 | 4000 | 54000
ii. | 3" dia | No. | 1 | 65000 | 65000 | 4000 | 4000 | 69000
iii. | 4" dia | Nos. | 5 | 80000 | 400000 | 5000 | 25000 | 425000
2.4 | Thermometer 6" Height Scale Type (with Thermo well) 0 ºC to 60 ºC | Nos. | 14 | 8000 | 112000 | 1000 | 14000 | 126000
2.5 | Pressure Gauge with with Ball Valve & Siphon, Liquid filled Dial type range -ve 5 psi to 100 psi. (4" dial Size) | Nos. | 14 | 8000 | 112000 | 1000 | 14000 | 126000
2.6 | 2-Way Motorized Valve with Actuator (0-100% modulating)
i. | 2" dia | No. | 1 | 87000 | 87000 | 3000 | 3000 | 90000
ii. | 2.5" dia | No. | 1 | 165000 | 165000 | 4000 | 4000 | 169000
iii. | 3" dia | Nos. | 5 |  | 0 | 5000 | 25000 | 25000
2.7 | Digital Decorative Thermostat Controller with Duct Sensor (BMS Interfacable) | Nos. | 7 | 25000 | 175000 | 5000 | 35000 | 210000
2.8 | Fan Control Panel with incoming Ckt. Breaker, auto S/D starter with protections and safeties | Nos. | 7 | 30000 | 210000 | 5000 | 35000 | 245000
2.9 | Control wiring from controller to sensors, motorized valve and Power wiring from FCP to fan, up to 15' radius | Lot | 7 | 8000 | 56000 | 5000 | 35000 | 91000
3 | Supply, Installation, testing and commissioning of SCH-40 M.S.(As per ASME & API standard, Heavy Quality with standard SCH 40 wall thickness) pipes & fitting for chilled water circulation system complete with bends, tees, unions, sockets, specials, MS Pipe support, hangers & anchors, M.S. angle, U channel, Roller Support, bolts, rods, clamps, Concrete fasteners etc as required to complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of Consultant.
3.1 | 2.5" dia | Rft | 55 | 1900 | 104500 | 400 | 22000 | 126500
3.2 | 3" dia | Rft | 110 | 2300 | 253000 | 450 | 49500 | 302500
3.3 | 4" dia | Rft | 275 | 2900 | 797500 | 500 | 137500 | 935000
3.4 | 5" dia | Rft | Rate only | 6450 | 0 | 600 | 0 | 0
3.5 | 6" dia | Rft | Rate only | 9200 | 0 | 900 | 0 | 0
3.6 | 8" dia | Rft | 200 | 6000 | 1200000 | 1200 | 240000 | 1440000
4 | Supply, Installation of Pre Formed Polystyrene (Thermopore) insulation (32 kg/m3 density) for Internal chilled water pipes (GF to 5F), bends, tees, unions, sockets, valves and on specials protected with Kraft paper, wrapped with 8oz Canvas cloth than paint with Anti fungus paint complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of Consultant.
4.1 | 2.5" dia | Rft | 55 | 400 | 22000 | 60 | 3300 | 25300
4.2 | 3" dia | Rft | 110 | 570 | 62700 | 70 | 7700 | 70400
4.3 | 4" dia | Rft | 275 | 640 | 176000 | 80 | 22000 | 198000
4.4 | 5" dia | Rft | Rate only | 1010 | 0 | 100 | 0 | 0
4.5 | 6" dia | Rft | Rate only | 1140 | 0 | 125 | 0 | 0
4.6 | 8" dia | Rft | 200 | 1000 | 200000 | 150 | 30000 | 230000
5 | Supply & installation single split air conditioning units decorative type (inverter) of different capacities, including supply & installation of supports, brackets, rubber isolator, flashing, power wiring upto 15' + connection, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
5.1 | AC-01 (2 Tr) | Nos. | 7 | 200000 | 1400000 | 5000 | 35000 | 1435000
6 | Supply & installation of refrigerant pipes (liquid + gas) with 1/2" thick expended rubber foam insulation, PVC tape wrapping + control wiring in G.I. for external / PVC for internal from outdoor unit to indoor unit, including gas charging if required complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
6.1 | AC-01 (2 Tr) | Rft | 182 | 1450 | 263900 | 250 | 45500 | 250000
7 | Supply & installation of 18 SWG G.I. sheet metal tray for refrigerant pipes and control wiring exposed to weather complete in all respects including hangers, supports brackets complete in all respects ready to operate as per specification, drawings and as per instruction, approval of consultant. | Sqft | 150 | 650 | 97500 | 150 | 22500 | 120000
8 | Supply, rigging, lifting, placement, installation, testing and commissioning of Ventilation Fans as per mentioned in schedule, including supply of vibration isolator, electrical connection, flexible duct connection, support & hangers complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant.
8.1 | B2-JF-01 | Nos. | 2 |  | 0 | 8000 | 16000 | 16000
8.2 | B2-EAF-01 | Nos. | 2 |  | 0 | 11000 | 22000 | 22000
8.3 | B2-FAF-01 | No. | 1 |  | 0 | 15000 | 15000 | 15000
8.4 | B1-JF-01 | Nos. | 2 |  | 0 | 7000 | 14000 | 14000
8.5 | B1-EAF-01 | Nos. | 2 |  | 0 | 20000 | 40000 | 40000
8.6 | GF-EAF-01 | No. | 1 |  | 0 | 2000 | 2000 | 2000
8.7 | FF-EAF-01 | No. | 1 |  | 0 | 2000 | 2000 | 2000
8.8 | FF-EAF-02 | No. | 1 |  | 0 | 3000 | 3000 | 3000
8.9 | TF-EAF-01 | Nos. | 5 |  | 0 | 3000 | 15000 | 15000
8.1 | TF-EAF-02 | Nos. | 5 |  | 0 | 3000 | 15000 | 15000
8.11 | FAF-01 | No. | 1 | 6000000 | 6000000 | 12000 | 12000 | 6012000
9 | Supply, fabrication and installation of machine made G.I sheet metal duct different sections supply, return, fresh & exhaust air including plenums, splitter dampers, guide vanes, flexible duct connector / connection, access door, transformation, plenums chambers, wooden frame, anchors supports & hangers complete in all respects ready to operate as per drawings, specification, instruction of Consultant. (for basement, MAHUs Room & Roof Area only) | Sqft | 7450 | 260 | 1937000 | 50 | 372500 | 2309500
10 | Supply & installation of 3/4" thick adhesive rubber foam (XLPE) insulation with aluminum foil over fresh air duct only, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.. (for MAHUs Room only) | Sqft | 6166 | 355 | 2188930 | 30 | 184980 | 2373910
11 | Supply and Installation of acoustical duct sound liner (adhesive with aluminum facing 19mm thick) in supply air duct complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Sqft | 5900 | 485 | 2861500 | 40 | 236000 | 3097500
12 | Supply, fabrication and installation of pre-insulated ductwork of polyurethane foam panel with 52 Kg/m3 density, 20 mm thickness, coated on both sides with 80 micron thick aluminum foil complete with a 2 g/m2 layer for internal duct work including manufacturer's aluminum hardware glue, Hot Dipped galvanized hangers and supports, flexible duct connection, wooden frame, etc. Complete in all respects ready to operate as per drawings, specification and as per instruction of consultant. (for Floor Areas only) | Sqft | 49811 | 315 | 15690465 | 40 | 1992440 | 17682905
13 | Supply & installation of aluminum fabricated powder coated Fresh & Exhaust Air louvers including supply of wooden frame, rain protection sheet bird mesh etc complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Sqin | 21732 | 23 | 499836 | 5 | 108660 | 608496
14 | Supply, Installation of Aluminum fabricated, powder coated Grills, Diffusers and Registers for supply air, return air, exhaust air & fresh air of different sizes (Grade A ) wooden frame, supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant.
14.1 | Supply, Return, Fresh, Exhaust Air Diffuser with Damper | Sqin | 54905 | 23 | 1262815 | 5 | 274525 | 1537340
14.2 | Supply, Return, Fresh & Exhaust Air Grills / Transfer Grills | Sqin | 88163 | 20 | 1763260 | 5 | 440815 | 2204075
14.3 | Supply, Return, Fresh & Exhaust Air Registers | Sqin | 550 | 20 | 11000 | 5 | 2750 | 13750
14.4 | S.S. Wire Mesh with G.I Frame | Sqin | 70356 | 8 | 562848 | 2 | 140712 | 703560
14.5 | Swirl Diffuser with Damper |  |  |  | 0
i. | 12" dia | Nos. | 650 | 8500 | 5525000 | 500 | 325000 | 5850000
14.5 | Supply & Return Air Linear Slot 6000 Series
i. | 2 Slot of 1" | Rft | 292 | 950 | 277400 | 300 | 87600 | 365000
14.6 | Supply & Return Air Linear Bar Grill 4000 Series
i. | 10" width | Rft | 20 | 4000 | 80000 | 400 | 8000 | 88000
14.7 | Disc Valves
i. | 6" Dia | Nos. | 107 | 1800 | 192600 | 300 | 32100 | 224700
15 | Supply & installation of flexible duct including hangers, jubilee clamp complete in all respects as per specification, drawings & as per instruction of consultant.
15.1 | 6" Dia | Rft | 25 | 450 | 11250 | 100 | 2500 | 13750
16 | Supply & installation of butterfly damper for above flexible duct with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of Consultant.
16.1 | 6" Dia | Nos. | 5 | 1500 | 7500 | 500 | 2500 | 10000
17 | Supply, fabrication & installation of pre-insulated Volume Control Damper, blades to be constructed with extruded aluminum in airfoil shape with thermal isolation gape & shall have seals, pvc / aluminum profiles duct connection at both end etc. complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Sqin | 53835 | 30 | 1615050 | 8 | 430680 | 2045730
18 | Supply & installation of Volume Control Damper in 16 SWG G.I sheet metal with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of Consultant. | Sqin | 550 | 20 | 11000 | 5 | 2750 | 13750
19 | Supply, Installation of Motorized Damper with gas kits, nut bolts, including pressure transmeter, controller & control wiring, complete in all respects, ready to operate as per specification, drawings & as per instruction of Consultant. | Sqin | 0 | 0 | 0 | 0 | 0 | 0
20 | Supply and installation of Back Draft Damper in MS Sheet with gas kits, nut botls. complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant. | Sqin | 5702 | 28 | 159656 | 5 | 28510 | 188166
21 | Supply and installation of Fire Damper with linkage & fuse complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant. | Sqin | 0 | 0 | 0 | 0 | 0 | 0
22 | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Lot | 1 | 45000 | 45000 | 15000 | 15000 | 60000
23 | Supply, Installation, Testing and Commissioning of allied electrical works for ACMV Systems including Motor Control Centre, MCCs complete in all respects including weather proof sheet metal cabinet, bus bars, internal wiring, earth strip, connector strip, MCB, MCCB, Control fuses, magnetic connector, Overload relay, indication lights, voltmeter, ammeter, under voltage, phase reversible, phase failure device, selector switch, related civil works etc. complete in all respects as per schedule, specifications, drawings & as per instructions of
23.1 | MCC-01 (basement ventilation fans) | Job. | 1 | 350000 | 350000 | 35000 | 35000 | 385000
24 | Supply, installation, testing and commissioning of interconnecting wiring, control wiring, power wiring from MCC, DB, panel to HVAC equipment with isolation switches near the equipment, including civil works related to complete wiring works etc. complete in all respects as per schedule, specifications, drawings & as per instructions of Consultant | Lot | 1 | 500000 | 500000 | 45000 | 45000 | 545000
25 | Supply, installation, testing and commissioning of perforated cable trays made with 1.63mm SWG (16 Guage) painted G.I Sheet, including hanger, bracket, proper bends, cover of trays shall be made with 1.22mm SWG (18 guage) painted G.I sheet, complete in all respects, ready to operate as per schedule, specification, drawings and as per instruction of Consultant. | Lot | 1 | 400000 | 400000 | 45000 | 45000 | 445000
26 | Supply, Installation, testing and commissioning of uPVC (Sch 40.) drain pipe insulated with 3/8" thick rubber foam insulation including clamps, bends, tees, drain plugs, sockets, protection treatment, PVC tape wrapping, hanger & supports etc, complete in all respects as per specifications, drawings & as per instructions of Consultant.
26.1 | 1" dia | Rft | 210 | 260 | 54600 | 100 | 21000 | 75600
26.2 | 1.25" dia | Rft | 210 | 400 | 84000 | 100 | 21000 | 105000
26.3 | 1.5" dia | Rft | 40 | 380 | 15200 | 125 | 5000 | 20200
26.4 | 2" dia | Rft | 198 | 420 | 83160 | 150 | 29700 | 112860
27 | Painting & Identification work on chilled, cooling water pipes & exhaust duct, supports, hangers etc. complete in all respects with one coat of ICI make Red lead oxide primer & two coats of ICI make enamel paint as per instruction of Consultant. | Job. | 1 | 15000 | 15000 | 45000 | 45000 | 60000
28 | Testing, balancing and commissioning of water & air side of the system (from independent agency) complete in all respects including flow measurement & balancing, temp, pressure, electrical data of related equipment etc. as per specifications and as per instructions of Consultant. | Job. | 1 | 0 | 0 | 90000 | 90000 | 90000
29 | Making of Shop drawings on Auto CAD latest version with section details and equipment foundation details, as per instruction of Consultant. | Job. | 1 | 10000 | 10000 | 15000 | 15000 | 25000
30 | Making of As Built drawings on Auto CAD latest version with Documentation Technical / Operational Manual & LOG Book for each equipment as per instruction of Consultant. | Job. | 1 | 5000 | 5000 | 10000 | 10000 | 15000
Total Cost of ACMV Works Rs. |  |  |  |  | 48864170 |  | 6518722 | 55063492 | Bilal final working