## BOQ
SH-2021-22 | [15 empty] | August 01, 2023.
SAIFEE HOSPITAL
BOQ OF FIRE FIGHTING & PLUMBING SYSTEM FOR CARDIAC WING SAIFEE HOSPITAL NORTH NAZIMABAD KARACHI.
S. No. | DESCRIPTION | QTY |  | BOQ rates (June 2021) |  | Revised costing | [9 empty] | TOTAL AMOUNT
|  |  |  | COST OF SUPPLY | COST OF SUPPLY | Material | Wastage | related Fittings | Transp | Hangers & Supports | O/H Profit | Material Rate | Labour Rate | Material Amount | Labour Amount
PART-A FIRE FIGHTING SYSTEM
1 | Supply, installation, testing & commissioning of Fire Pump Skid Mounted Package set complete with Electric, Diesel & Jockey pump including Control panel, fuel tank all special fitting, Painting and hangers complete in all respects as per drawing & specifications.(250GPM & 10BAR) | 1 | Set | 3650000 | 3650000 | 15280533 | 0 | 0 | 45000 | 60000 | 1538553.3 | 16924086.3 | 150000 | 16924086.3 | 150000 | 17074086.3
2 | Supply, installation, testing & commissioning of Fire Hose Cabinets including automatic 1" diameter Hose reel, Nozzle, CO2, Dry Powder Extinguishers, 25mm Lock shield Valve, 1" pressure reducing Valve, 2 1/2" diameter landing Valve with pressure regulator complete in all respectss as shown on drawings & specifications | 10 | Nos | 218500 | 2185000 | 396481 | 0 | 0 | 2000 | 3000 | 40148.1 | 441629.1 | 17000 | 4416291 | 170000 | 4586291
3 | Supply, installation, testing & commissioning of 2-way Fire Department Connection Including all accessories complete in all respects as shown on Drawings / Specifications. | 1 | Nos | 45500 | 45500 | 79905 | 0 | 0 | 1000 | 0 | 12135.75 | 93040.75 | 4700 | 93040.75 | 4700 | 97740.75
4 | Supply, Installation, testing & commissioning of OS&Y Gate valve Including all accessories complete in all respects as shown on Drawings / Specifications. | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 2-1/2" dia | 10 | Nos | 46900 | 469000 | 114731 | 0 | 4600 | 0 | 0 | 11933.1 | 131264.1 | 4500 | 1312641 | 45000 | 1357641
5 | Supply & Installation of puddle connection in water tank complete with all repect. 5" dia | 2 | Nos | 15000 | 30000 | 15000 | 0 | 2000 | 0 | 0 | 2550 | 19550 | 4000 | 39100 | 8000 | 47100 | 40700 | 50875
6 | Supply, Installation, testing & commissioning of Water proof MCC for fire System with circuit Breakers, Disconnect switches, fuses, phase reversal, starters etc. for all equipment as per specification & drawing. (Isolation breakers shall be finalized as per manufacturer specifications.) | 1 | Nos | 195000 | 195000 | 450000 | 0 | 0 | 5000 | 3000 | 68700 | 526700 | 15000 | 526700 | 15000 | 541700
7 | Supply, Installation, testing & commissioning of seamless M.S schedule-40 Fire piping including all special fitting, Painting and hangers complete in all respects show on drawing & specifications. | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 5" dia | 280 | Rft. | 3750 | 1050000 | 3252 | 87 | 813 | 16.26 | 200 | 436.826 | 4805.086 | 500 | 1345424.08 | 140000 | 1485424.08
ii | 2-1/2" dia | 250 | Rft. | 1680 | 420000 | 1289 | 64.45 | 322.25 | 6.445 | 150 | 183.2145 | 2015.3595 | 350 | 503839.875 | 87500 | 591339.875
8 | Supply, Installation, testing & commissioning of Complete Electric power & control wiring complete with PVC conduit and power wiring will be in G.I.Cable tray & hanger supports etc. for Equipment as per Specification and drawings. | 1 | Lot. | 170000 | 170000 | 170000 | 0 | 10000 | 0 | 0 | 27000 | 207000 | 18000 | 207000 | 18000 | 225000
9 | Supply & Installation of Wall Mounted Fire Extinguisher with hangers as per drawing and specification. | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | Fire Extinguisher 6 Kg Dry Powder | 9 | Nos | 8700 | 78300 | 18264 | 0 | 0 | 0 | 500 | 2814.6 | 21578.6 | 1700 | 194207.4 | 15300 | 209507.4
ii | Fire Extinguisher 6 Kg CO2 | 9 | Nos | 19000 | 171000 | 37290 | 0 | 0 | 0 | 500 | 5668.5 | 43458.5 | 1700 | 391126.5 | 15300 | 406426.5
TOTAL COST PART -B (RS.) | [15 empty] | 26622256.905
PART-B WATER SUPPLY AND DRAINAGE SYSTEM. | [10 empty] | 0 | 0 |  | 0 | 0 | 0
1 | Supply, Installation, testing & commissioning of End Suction O.H Water Transfer pumps complete with accessories as per drawings and specifications. (100gpm, 160 ft. Head) | 2 | Nos. | 175000 | 350000 | 0 | 0 | 0 | 3000 |  | 300 | 3300 | 15000 | 6600 | 30000 | 36600
2 | Supply & Installation of Hot Water Electric operated Geyser 50 Gallons Capacity Storage Type. Inner Tank made with G.I Sheet 8 SWG/3.8mm Outer Shell made With Stainless Steel Sheet, With Imported Thermostat, Upto 60 Psi. | 3 | Nos. | 95000 | 285000 | 135000 | 0 | 5000 | 2000 | 0 | 14200 | 156200 | 10000 | 468600 | 30000 | 498600
3 | Supply, Installation, testing & commissioning of Circulation Hot water pumps complete with accessories as per drawings and specifications. (25gpm, 20ft Head) | 3 | Nos. | 77000 | 231000 | 170554 |  |  |  |  | 17055.4 | 187609.4 | 15000 | 562828.2 | 45000 | 607828.2
4 | Water closets European style with close coupled cistern, cistern fittings, acrylic seat cover, complete with accessories. | 25 | Nos. | 25000 | 625000 | 50875 |  | 1500 |  |  | 5237.5 | 57612.5 | 8000 | 1440312.5 | 200000 | 1640312.5
5 | Water closets European style with close coupled cistern, cistern fittings, acrylic seat cover, for handi cap toilet complete with accessories. | 3 | Nos. | 25000 | 75000 | 50875 |  | 1500 |  |  | 5237.5 | 57612.5 | 8000 | 172837.5 | 24000 | 196837.5
6 | Wash basins, single center hole, suitable for counter top fittings for below, complete with accessories. | 44 | Nos. | 19000 | 836000 | 19000 |  | 0 |  |  | 1900 | 20900 | 6000 | 919600 | 264000 | 1183600
7 | Wash basins, single center hole, suitable for counter top fittings for below, for dirty utility complete with accessories. | 4 | Nos. | 17500 | 70000 | 17500 |  | 0 |  |  | 1750 | 19250 | 6000 | 77000 | 24000 | 101000
8 | C.P Tee valves, for cistern water inlet CP connectors with nuts and fittings, complete with accessories. | 56 | Nos. | 1800 | 100800 | 1875 |  | 0 |  |  | 187.5 | 2062.5 | 500 | 115500 | 28000 | 143500
9 | Muslim Shower with flexible hose, valve nozzle angle valve spont, complete with accessories. | 28 | Nos. | 6500 | 182000 | 7800 |  | 0 |  |  | 780 | 8580 | 1000 | 240240 | 28000 | 268240
10 | CP Tee valves for wash basins, CP connections with nutes, fittings and complete with all accessories. | 100 | Nos. | 2250 | 225000 | 3000 |  | 0 |  |  | 300 | 3300 | 500 | 330000 | 50000 | 380000
11 | CP bottle trap 1-1/4" with pipe for wash basin waste connection and water strainer, complete with all accessories. | 48 | Nos. | 3500 | 168000 | 5500 |  | 0 |  |  | 550 | 6050 | 500 | 290400 | 24000 | 314400
12 | CP Toilet paper roll holder Asia or approved equal complete with accessories. | 28 | Nos. | 3900 | 109200 | 5000 |  | 0 |  |  | 500 | 5500 | 500 | 154000 | 14000 | 168000
13 | Soap bottles, decorative type complete with accessories. | 48 | Nos. | 5200 | 249600 | 5200 |  | 0 |  |  | 520 | 5720 | 750 | 274560 | 36000 | 310560
14 | Supply and installation of basins mixture complete with all accessories. | 48 | Nos. | 9900 | 475200 | 9900 |  | 0 |  |  | 990 | 10890 | 2000 | 522720 | 96000 | 618720
15 | Supply & Installation of Sanitizer -Automatic. | 48 | Nos. | 10500 | 504000 | 30000 |  | 0 |  |  | 3000 | 33000 | 1200 | 1584000 | 57600 | 1641600
16 | Supply & Installation of hand Dryer. | 12 | Nos. | 18900 | 226800 | 18900 |  | 0 |  |  | 1890 | 20790 | 2000 | 249480 | 24000 | 273480
17 | WATER DISTRIBUTION SYSTEM | [9 empty] | 0 | 0 |  | 0 | 0 | 0
a. | Supply and installation of PPR PN 20 piping for cold & Hot water system, with fittings, specialties, including all cutting, fitting, fixing and cleaning, wall and slab sleeves/Core Cutting, CP clamps, hangers and supports, making connection with fixtures, valves and specialties, chiseling, making wall an floor openings and making good, pressure testing at a pressure of 250 psig, painting of exposed piping in occupied areas with primer and coats of approved paint in approved color complete in all respect. | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 2" dia | 900 | Rft. | 498 | 448200 | 1196 | 59.8 | 478.4 |  | 119.6 | 185.38 | 2039.18 | 250 | 1835262 | 225000 | 2060262
ii. | 1-1/4" dia | 300 | Rft. | 370 | 111000 | 568 | 28.4 | 227.2 |  | 56.8 | 88.04 | 968.44 | 200 | 290532 | 60000 | 350532
iii. | 1" dia | 700 | Rft. | 198 | 138600 | 416 | 20.8 | 166.4 |  | 41.6 | 64.48 | 709.28 | 175 | 496496 | 122500 | 618996
iv. | 3/4" dia | 850 | Rft. | 160 | 136000 | 313 | 15.65 | 125.2 |  | 31.3 | 48.515 | 533.665 | 150 | 453615.25 | 127500 | 581115.25
v. | 1/2" dia | 1000 | Rft. | 145 | 145000 | 255 | 12.75 | 102 |  | 25.5 | 39.525 | 434.775 | 125 | 434775 | 125000 | 559775
b. | Gate Valve | [9 empty] | 0 | 0 |  |  | 0 | 0
i. | 2" dia | 6 | Nos | 9900 | 59400 | 16700 |  | 4175 |  |  | 2087.5 | 22962.5 | 2000 | 137775 | 12000 | 149775
ii. | 1-1/2" dia | 6 | Nos | 8800 | 52800 | 11930 |  | 2982.5 |  |  | 1491.25 | 16403.75 | 1500 | 98422.5 | 9000 | 107422.5
iii. | 1-1/4" dia | 10 | Nos | 7700 | 77000 | 8070 |  | 2017.5 |  |  | 1008.75 | 11096.25 | 1200 | 110962.5 | 12000 | 122962.5
iv. | 1" dia | 12 | Nos | 6500 | 78000 | 5700 |  | 1425 |  |  | 712.5 | 7837.5 | 1000 | 94050 | 12000 | 106050
v | 3/4" dia | 6 | Nos | 5000 | 30000 | 4080 |  | 1020 |  |  | 510 | 5610 | 1000 | 33660 | 6000 | 39660
c. | Ball Valve | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 1/2" dia | 9 | Nos | 2200 | 19800 | 2760 |  | 690 |  |  | 345 | 3795 | 1000 | 34155 | 9000 | 43155
ii. | 2" dia | 3 | Nos | 6800 | 20400 | 16890 |  | 4222.5 |  |  | 2111.25 | 23223.75 | 2000 | 69671.25 | 6000 | 75671.25
d. | Float valve | 2 | Nos | 8000 | 16000 | 9600 |  | 2400 |  |  | 1200 | 13200 | 1500 | 26400 | 3000 | 29400
e. | Foot valve 2" dia | 2 | Nos | 6000 | 12000 | 8750 |  | 2187.5 |  |  | 1093.75 | 12031.25 | 2000 | 24062.5 | 4000 | 28062.5
f. | Strainer 2" dia | 2 | Nos | 4500 | 9000 | 13800 |  | 3450 |  |  | 1725 | 18975 | 2000 | 37950 | 4000 | 41950
g. | Check valve 2" dia | 2 | Nos | 15000 | 30000 | 15000 |  | 3750 |  |  | 1875 | 20625 | 2000 | 41250 | 4000 | 45250
18 | SOIL, WASTE AND VENT SYSTEM | [9 empty] | 0 | 0 |  | 0 | 0 | 0
a. | Supply and installation of UPVC Class D piping including all fittings, sockets, hangers and specials for soil, waste,rain& vent stacks and horizontal runs buried in ground or above false ceiling, in shafts exposed or concealed in floors and walls and connecting to manholes, including cutting, fitting, chiseling, wall and slab sleeves/Core Cutting, making good, fixing and cleaning, wall and slab openings complete in all | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 8" dia | 100 | Rft. | 2300 | 230000 | 3010 | 150.5 | 1204 |  | 301 | 466.55 | 5132.05 | 300 | 513205 | 30000 | 543205
ii. | 6" dia | 160 | Rft. | 1800 | 288000 | 2002 | 100.1 | 800.8 |  | 200.2 | 310.31 | 3413.41 | 260 | 546145.6 | 41600 | 587745.6
iii. | 4" dia | 1300 | Rft. | 990 | 1287000 | 1058 | 52.9 | 423.2 |  | 105.8 | 163.99 | 1803.89 | 220 | 2345057 | 286000 | 2631057
iv. | 3" dia | 1400 | Rft. | 680 | 952000 | 729 | 36.45 | 291.6 |  | 72.9 | 112.995 | 1242.945 | 215 | 1740123 | 301000 | 2041123
v. | 2" dia | 1200 | Rft. | 310 | 372000 | 375 | 18.75 | 150 |  | 37.5 | 58.125 | 639.375 | 200 | 767250 | 240000 | 1007250
19 | Supply and installation of Roof Drain with Trap complete in all respect. | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i | 6" dia | 2 | Nos. | 6000 | 12000 | 14500 | 0 | 0 | 0 | 0 | 1450 | 15950 | 1500 | 31900 | 3000 | 34900
20 | Supply and installation of Floor Drain with Trap complete in all respect. | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 4" dia | 90 | Nos. | 4000 | 360000 | 6500 | 0 | 0 | 0 | 0 | 650 | 7150 | 1000 | 643500 | 90000 | 733500
21 | Supply & installation of Vent cowl complete with all respect as per drawing & specificaiton. | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 6" dia | 1 | Nos. | 2000 | 2000 | 2000 | 0 | 0 | 0 | 0 | 200 | 2200 | 700 | 2200 | 700 | 2900
ii | 4" dia | 1 | Nos. | 1800 | 1800 | 1800 | 0 | 0 | 0 | 0 | 180 | 1980 | 700 | 1980 | 700 | 2680
iii. | 3" dia | 1 | Nos. | 1700 | 1700 | 1700 | 0 | 0 | 0 | 0 | 170 | 1870 | 700 | 1870 | 700 | 2570
22 | Supply and installation of Clean Out complete in all respect. | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 4" dia | 13 | Nos. | 1500 | 19500 | 4000 | 0 | 0 | 0 | 0 | 400 | 4400 | 700 | 57200 | 9100 | 66300
ii. | 3" dia | 30 | Nos. | 1400 | 42000 | 3000 | 0 | 0 | 0 | 0 | 300 | 3300 | 700 | 99000 | 21000 | 120000
23 | Supply & Installation of Weatherproof MCC for Plumbing System with circuit Breakers, Disconnect switches, fuses, starters etc. for all equipment as per specification & drawing.(Isolation breakers shall be finalized as per manufacturer specifications. | 1 | Nos. | 175000 | 175000 | 365000 | 0 | 0 | 0 | 0 | 36500 | 401500 | 25000 | 401500 | 25000 | 426500
24 | Supply & installation of R.C.C M.H with Heavy duty cover complete with all respect as per drawing & specification. | 4 | Nos. | 45000 | 180000 | 60000 | 0 | 0 | 0 | 0 | 6000 | 66000 | 15000 | 264000 | 60000 | 324000
25 | Supply & installation of G.T with Heavy duty cover complete with all respect as per drawing & specification. | 2 | Nos. | 38000 | 76000 | 38000 |  |  |  |  | 3800 | 41800 | 7000 | 83600 | 14000 | 97600
26 | Supply & Installation of Complete Electric power & control wiring complete with PVC conduit and power wiring will be in G.I.Cable tray & hanger supports etc. for Equipment as per Specification and drawings. | 1 | Lot. | 75000 | 75000 | 140000 | 0 | 0 | 0 | 0 | 14000 | 154000 | 25000 | 154000 | 25000 | 179000
27 | City sewerage and water supply connection from city connection point to building connection location. | 1 | Lot. | 50000 | 50000 | 100000 | 0 | 0 | 0 | 0 | 10000 | 110000 | 50000 | 110000 | 50000 | 160000
TOTAL COST PART -B (RS.) | [15 empty] | 22303647.8
PART-C RO WATER SYSTEM SYSTEM | [10 empty] | 0 | 0 |  | 0 | 0 | 0
1 | Installation, testing & commissioning of OFM RO water system complete in all respectss as shown on drawings & specifications | 1 | Set | 0 | 0 | [5 empty] | 0 | 0 | 60000 | 0 | 60000 | 60000
2 | Supply, Installation, testing & commissioning of PE (1000 USG) tank complete in all respectss as shown on drawings & specifications | 3 | Nos. | 135000 | 405000 | 200000 |  |  |  |  | 20000 | 220000 | 15000 | 660000 | 45000 | 705000
3 | Supply, Installation, Testing & Commissioning of Multistage (2+1 No's) Boosting Pumping system 2nos running and 1no standby with speed controller, control pannel,integrated dry running detection and low water cut out switch complete with valve fitting with all respect as per drawings and specification.(60 Gpm and 8 bar) | 1 | Set | 475000 | 475000 | 0 |  |  |  |  | 0 | 0 | 35000 | 0 | 35000 | 35000
4 | RO WATER DISTRIBUTION SYSTEM | [9 empty] | 0 | 0 |  | 0 | 0 | 0
a. | PPR PN 20 piping for RO water system, with fittings, specialties, including all cutting, fitting, fixing and cleaning, wall and slab sleeves, CP clamps, hangers and supports, making connection with fixtures, valves and specialties, chiseling, making wall an floor openings and making good, pressure testing at a pressure of 250 psig, painting of exposed piping in occupied areas with primer and coats of approved paint in approved color complete in all respect. | [9 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 2" dia | 270 | Rft. | 498 | 134460 | 1196 | 59.8 | 478.4 |  | 119.6 | 185.38 | 2039.18 | 250 | 550578.6 | 67500 | 618078.6
ii. | 1-1/2" dia | 160 | Rft. | 399 | 63840 | 850 | 42.5 | 425 |  | 85 | 140.25 | 1542.75 | 225 | 246840 | 36000 | 282840
iii. | 1-1/4" dia | 370 | Rft. | 370 | 136900 | 568 | 28.4 | 227.2 |  | 56.8 | 88.04 | 968.44 | 200 | 358322.8 | 74000 | 432322.8
iv. | 1" dia | 260 | Rft. | 198 | 51480 | 416 | 20.8 | 166.4 |  | 41.6 | 64.48 | 709.28 | 175 | 184412.8 | 45500 | 229912.8
v. | 3/4" dia | 220 | Rft. | 160 | 35200 | 313 | 15.65 | 125.2 |  | 31.3 | 48.515 | 533.665 | 150 | 117406.3 | 33000 | 150406.3
vi | 1/2" dia | 530 | Rft. | 155 | 82150 | 255 | 12.75 | 102 |  | 25.5 | 39.525 | 434.775 | 125 | 230430.75 | 66250 | 296680.75
5 | Gate Valve |  |  |  | 0 | [5 empty] | 0 | 0 |  | 0 | 0 | 0
i. | 2" dia | 4 | Nos | 9900 | 39600 | 16700 |  | 4175 |  |  | 2087.5 | 22962.5 | 2000 | 91850 | 8000 | 99850
ii | 1 1/4" dia | 7 | Nos | 6000 | 42000 | 8070 |  | 2017.5 |  |  | 1008.75 | 11096.25 | 1200 | 77673.75 | 8400 | 86073.75 | gala kitz
6 | Strainer 2" dia | 2 | Nos | 13500 | 27000 | 13800 |  | 3450 |  |  | 1725 | 18975 | 2000 | 37950 | 4000 | 41950
7 | Check valve 2" dia | 2 | Nos | 11500 | 23000 | 13700 |  | 3425 |  |  | 1712.5 | 18837.5 | 2000 | 37675 | 4000 | 41675
TOTAL COST PART -C RO WATER SYSTEM (RS.) | [15 empty] | 3079790
PART-D GERNAL WORKS | [10 empty] | 0 | 0 |  | 0 | 0 | 0
1 | Equipment foundation and equipment shifting charges from Ground floor to foundation pads as per specification and drawings. | 1 | Job | 75000 | 75000 | 120000 |  |  |  |  | 12000 | 132000 | 60000 | 132000 | 60000 | 192000
2 | Supply, installation, testing & commissioning of level sensor for Fire Fighting & Plumbing system complete with all respect as per drawings & specification. | 1 | Job | 275000 | 275000 | 275000 |  |  |  |  | 27500 | 302500 |  | 302500 | 50000 | 352500
3 | M&P Services Shop drawings & As Built Drawings Color Copies. (Minimum scale 1-1/8”) Hard Copy and Soft Copy in Autocad format in CD | 4 | Set | 12000 | 48000 | 12000 |  |  |  |  | 1200 | 13200 |  | 52800 | 3000 | 55800
4 | Cost of testing, Starting up, commissioning, balancing, adjusting and handling over of the complete Plant. | 1 | Job | 150000 | 150000 | 150000 |  |  |  |  | 15000 | 165000 |  | 165000 | 25000 | 190000
5 | Cost of System operation for 3 months (2 Operators ). | 1 | Job | 0 | 0 | [5 empty] | 0 | 0 |  | 0 | 0 | 0
TATAL COST PART -D (RS.) | [15 empty] | 790300
GRAND TOTAL PART-A, B,C & D. (RS) | [15 empty] | 52795994.705
26174746

## comparison
UPVC Class D
Size | Qty | Unit | PIONEER |  |  |  | DADEX |  | Steelex
| Qty |  | Mat Rate | Lab Rate | Mat Amount | Lab Amount | Rate | Amount | Rate | Amount
8" dia | 100 | Rft. | 2300 | 300 | 230000 | 30000 | 823.8567 | 82385.6707 | 1095 | 109500
6" dia | 160 | Rft. | 1800 | 260 | 288000 | 41600 | 542.0732 | 86731.7073 | 720 | 115200
4" dia | 1300 | Rft. | 990 | 220 | 1287000 | 286000 | 366.1585 | 476006.0976 | 413 | 536900
3" dia | 1400 | Rft. | 680 | 215 | 952000 | 301000 | 234.3496 | 328089.4309 | 292 | 408800
2" dia | 1200 | Rft. | 310 | 200 | 372000 | 240000 | 151.0671 | 181280.4878 | 140 | 168000
[5 empty] | 3129000 | 898600 |  | 1154493.3943 |  | 1338400
|  |  | Amount Diff with DADEX |  |  | 1974506.6057
|  |  | Amount Diff with STEELEX |  |  | 1790600
PPR PN 20 piping
Size | Qty | Unit | PIONEER |  |  |  | DADEX |  | Steelex
| Qty |  | Mat Rate | Lab Rate | Mat Amount | Lab Amount | Rate | Amount | Rate | Amount
2" dia | 900 | Rft. | 498 | 190 | 448200 | 171000 | 247 | 222300 | PPRC not avlbe in Steelex
1-1/4" dia | 300 | Rft. | 370 | 185 | 111000 | 55500 | 102.2104 | 30663.1098
1" dia | 700 | Rft. | 198 | 180 | 138600 | 126000 | 62.5762 | 43803.3537
3/4" dia | 850 | Rft. | 160 | 170 | 136000 | 144500 | 40.3201 | 34272.1037
1/2" dia | 1000 | Rft. | 145 | 100 | 145000 | 100000 | 0 | 0
[5 empty] | 978800 | 597000 |  | 331038.5671
|  |  | Amount Diff with DADEX |  |  | 647761.4329
PPR PN 20 (RO PIPING)
Size | Qty | Unit | PIONEER |  |  |  | DADEX |  | Steelex
| Qty |  | Mat Rate | Lab Rate | Mat Amount | Lab Amount | Rate | Amount | Rate | Amount
2" dia | 270 | Rft. | 498 | 120 | 134460 | 32400 | 247.0274 | 66697.4085 | PPRC not avlbe in Steelex
1-1/2" dia | 160 | Rft. | 399 | 115 | 63840 | 18400 | 156.25 | 25000
1-1/4" dia | 370 | Rft. | 370 | 110 | 136900 | 40700 | 102.2104 | 37817.8354
1" dia | 260 | Rft. | 198 | 105 | 51480 | 27300 | 63.186 | 16428.3537
3/4" dia | 220 | Rft. | 160 | 80 | 35200 | 17600 | 40.3201 | 8870.4268
1/2" dia | 530 | Rft. | 155 | 75 | 82150 | 39750 | 0 | 0
[5 empty] | 504030 | 176150 |  | 154814.0244
|  |  | Amount Diff with DADEX |  |  | 349215.9756

## Fire rates comparison
Fire Equipment Rates Analysis with ZARA Engineers
Size | Qty | Unit | PIONEER |  |  |  | ZARA Engineers
| Qty |  | Mat Rate | Lab Rate | Mat Amount | Lab Amount | Rate | Amount
Fire Pump Skid Mounted Package | 1 | Set | 3650000 | 150000 | 3650000 | 150000 | 2460966 | 2460966
Fire Hose Cabinets including automatic 1" diameter Hose reel | 10 | Nos | 218500 | 17000 | 2185000 | 170000 | 213018 | 2130180
2-way Fire Department Connection | 1 | No | 45500 | 4700 | 45500 | 4700 | 32823 | 32823
OS&Y Gate valve 2-1/2" | 10 | Nos | 46900 | 4500 | 469000 | 45000 | 55507 | 555070
puddle connection in water tank | 2 | Nos | 15000 | 400 | 30000 | 800 |  | 0
M.S Pipe 5" | 280 | Rft. | 3750 | 410 | 1050000 | 114800 | 2900 | 812000
M.S Pipe 2-1/2" | 250 | Rft. | 1680 | 300 | 420000 | 75000 | 1145 | 286250 | 7151
Fire Extinguisher 6 Kg Dry Powder | 9 | Nos | 8700 | 1700 | 78300 | 15300 | 8367 | 75303 | 8366.67
Fire Extinguisher 6 Kg CO2 | 9 | Nos | 19000 | 1700 | 171000 | 15300 | 18340 | 165060
[5 empty] | 8098800 | 590900 |  | 6517652
|  |  | Amount Diff |  |  | 1581148

## Ebitt vs Naffco
Fire Equipment Rates Analysis / Comparison
Size | Qty | Unit | PIONEER |  | SAFE & SOUND-NAFFCO |  | AMCON-EBITT
| Qty |  | Rate | Amount | Rate | Amount | Rate | Amount
Fire Pump Skid Mounted Package | 1 | Set | 3650000 | 3650000 | 3111500 | 3111500 | 4914000 | 4914000 | 4200000
Fire Hose Cabinets including automatic 1" diameter Hose reel | 10 | Nos | 218500 | 2185000 | 184500 | 1845000 | 256505 | 2565050 | 219235
2-way Fire Department Connection | 1 | No | 45500 | 45500 | 36000 | 36000 | 74261 | 74261 | 63471
OS&Y Gate valve 2-1/2" | 10 | Nos | 46900 | 469000 | 35000 | 350000 | 67888 | 678880 | 57853
Fire Extinguisher 6 Kg Dry Powder | 9 | Nos | 8700 | 78300 | 5500 | 49500 | 5850 | 52650 | 5000
Fire Extinguisher 6 Kg CO2 | 9 | Nos | 19000 | 171000 | 12000 | 108000 | 9360 | 84240 | 8000
|  |  |  | 6598800 |  | 5500000 |  | 8369081
7229697
8458745.49

## Finance
Financial Summary for the project SAIFEE HOSPITAL
|  |  |  | Contract Value | 26174746 |  | Contract Value | 21000000
[7 empty] | Total Received | 2434251.378
|  |  |  | Payable amount | 26174746 |  | Net Payable | 18565748.622
Receiving details
Payment | Receiving date | Gross payment reeived | Tax 7% | Chq amount | Remarks | Remarks
Mobilization advance 10% | 2022-04-18 | 2617474.6 | 183223.222 | 2434251.378 | Depositted in DIB
Total receiving till todate |  | 2617474.6 | 183223.222 | 2434251.378
Net Receivable amount |  |  |  | 23740494.622
Add Retention Money |  |  |  | 0
Total Payable Amount Rs |  |  |  | 23740494.622
3780000
283500
3496500

## submittal
SAIFEE HOSPITAL
| Description | Qty | unit | Submittal received | Submittal Submitted | Status | Remarks
PART-A FIRE FIGHTING SYSTEM
1 | Supply, installation, testing & commissioning of Fire Pump Skid Mounted Package set complete with Electric, Diesel & Jockey pump including Control panel, fuel tank all special fitting, Painting and hangers complete in all respects as per drawing & specifications.(250GPM & 10BAR) | 1 | Set
2 | Supply, installation, testing & commissioning of Fire Hose Cabinets including automatic 1" diameter Hose reel, Nozzle, CO2, Dry Powder Extinguishers, 25mm Lock shield Valve, 1" pressure reducing Valve, 2 1/2" diameter landing Valve with pressure regulator complete in all respectss as shown on drawings & specifications | 10 | Nos
3 | Supply, installation, testing & commissioning of 2-way Fire Department Connection Including all accessories complete in all respects as shown on Drawings / Specifications. | 1 | Nos
4 | Supply, Installation, testing & commissioning of OS&Y Gate valve Including all accessories complete in all respects as shown on Drawings / Specifications.
i. | 2-1/2" dia | 10 | Nos
5 | Supply & Installation of puddle connection in water tank complete with all repect. 5" dia | 2 | Nos
6 | Supply, Installation, testing & commissioning of Water proof MCC for fire System with circuit Breakers, Disconnect switches, fuses, phase reversal, starters etc. for all equipment as per specification & drawing. (Isolation breakers shall be finalized as per manufacturer specifications.) | 1 | Nos
7 | Supply, Installation, testing & commissioning of seamless M.S schedule-40 Fire piping including all special fitting, Painting and hangers complete in all respects show on drawing & specifications.
i. | 5" dia | 280 | Rft.
ii | 2-1/2" dia | 250 | Rft.
8 | Supply, Installation, testing & commissioning of Complete Electric power & control wiring complete with PVC conduit and power wiring will be in G.I.Cable tray & hanger supports etc. for Equipment as per Specification and drawings. | 1 | Lot.
9 | Supply & Installation of Wall Mounted Fire Extinguisher with hangers as per drawing and specification.
i. | Fire Extinguisher 6 Kg Dry Powder | 9 | Nos
ii | Fire Extinguisher 6 Kg CO2 | 9 | Nos
TOTAL COST PART -B (RS.) | [6 empty] | 0
PART-B WATER SUPPLY AND DRAINAGE SYSTEM.
1 | Supply, Installation, testing & commissioning of End Suction O.H Water Transfer pumps complete with accessories as per drawings and specifications. (100gpm, 160 ft. Head) | 2 | Nos.
2 | Supply & Installation of Hot Water Electric operated Geyser 50 Gallons Capacity Storage Type. Inner Tank made with G.I Sheet 8 SWG/3.8mm Outer Shell made With Stainless Steel Sheet, With Imported Thermostat, Upto 60 Psi. | 3 | Nos.
3 | Supply, Installation, testing & commissioning of Circulation Hot water pumps complete with accessories as per drawings and specifications. (25gpm, 20ft Head) | 3 | Nos.
4 | Water closets European style with close coupled cistern, cistern fittings, acrylic seat cover, complete with accessories. | 25 | Nos.
5 | Water closets European style with close coupled cistern, cistern fittings, acrylic seat cover, for handi cap toilet complete with accessories. | 3 | Nos.
6 | Wash basins, single center hole, suitable for counter top fittings for below, complete with accessories. | 44 | Nos.
7 | Wash basins, single center hole, suitable for counter top fittings for below, for dirty utility complete with accessories. | 4 | Nos.
8 | C.P Tee valves, for cistern water inlet CP connectors with nuts and fittings, complete with accessories. | 56 | Nos.
9 | Muslim Shower with flexible hose, valve nozzle angle valve spont, complete with accessories. | 28 | Nos.
10 | CP Tee valves for wash basins, CP connections with nutes, fittings and complete with all accessories. | 100 | Nos.
11 | CP bottle trap 1-1/4" with pipe for wash basin waste connection and water strainer, complete with all accessories. | 48 | Nos.
12 | CP Toilet paper roll holder Asia or approved equal complete with accessories. | 28 | Nos.
13 | Soap bottles, decorative type complete with accessories. | 48 | Nos.
14 | Supply and installation of basins mixture complete with all accessories. | 48 | Nos.
15 | Supply & Installation of Sanitizer -Automatic. | 48 | Nos.
16 | Supply & Installation of hand Dryer. | 12 | Nos.
17 | WATER DISTRIBUTION SYSTEM
a. | Supply and installation of PPR PN 20 piping for cold & Hot water system, with fittings, specialties, including all cutting, fitting, fixing and cleaning, wall and slab sleeves/Core Cutting, CP clamps, hangers and supports, making connection with fixtures, valves and specialties, chiseling, making wall an floor openings and making good, pressure testing at a pressure of 250 psig, painting of exposed piping in occupied areas with primer and coats of approved paint in approved color complete in all respect.
i. | 2" dia | 900 | Rft.
ii. | 1-1/4" dia | 300 | Rft.
iii. | 1" dia | 700 | Rft.
iv. | 3/4" dia | 850 | Rft.
v. | 1/2" dia | 1000 | Rft.
b. | Gate Valve
i. | 2" dia | 6 | Nos
ii. | 1-1/2" dia | 6 | Nos
iii. | 1-1/4" dia | 10 | Nos
iv. | 1" dia | 12 | Nos
v | 3/4" dia | 6 | Nos
c. | Ball Valve
i. | 1/2" dia | 9 | Nos
ii. | 2" dia | 3 | Nos
d. | Float valve | 2 | Nos
e. | Foot valve 2" dia | 2 | Nos
f. | Strainer 2" dia | 2 | Nos
g. | Check valve 2" dia | 2 | Nos
18 | SOIL, WASTE AND VENT SYSTEM
a. | Supply and installation of UPVC Class D piping including all fittings, sockets, hangers and specials for soil, waste,rain& vent stacks and horizontal runs buried in ground or above false ceiling, in shafts exposed or concealed in floors and walls and connecting to manholes, including cutting, fitting, chiseling, wall and slab sleeves/Core Cutting, making good, fixing and cleaning, wall and slab openings complete in all
i. | 8" dia | 100 | Rft.
ii. | 6" dia | 160 | Rft.
iii. | 4" dia | 1300 | Rft.
iv. | 3" dia | 1400 | Rft.
v. | 2" dia | 1200 | Rft.
19 | Supply and installation of Roof Drain with Trap complete in all respect.
i | 6" dia | 2 | Nos.
20 | Supply and installation of Floor Drain with Trap complete in all respect.
i. | 4" dia | 90 | Nos.
21 | Supply & installation of Vent cowl complete with all respect as per drawing & specificaiton.
i. | 6" dia | 1 | Nos.
ii | 4" dia | 1 | Nos.
iii. | 3" dia | 1 | Nos.
22 | Supply and installation of Clean Out complete in all respect.
i. | 4" dia | 13 | Nos.
ii. | 3" dia | 30 | Nos.
23 | Supply & Installation of Weatherproof MCC for Plumbing System with circuit Breakers, Disconnect switches, fuses, starters etc. for all equipment as per specification & drawing.(Isolation breakers shall be finalized as per manufacturer specifications. ) | 1 | Nos.
24 | Supply & installation of R.C.C M.H with Heavy duty cover complete with all respect as per drawing & specification. | 4 | Nos.
25 | Supply & installation of G.T with Heavy duty cover complete with all respect as per drawing & specification. | 2 | Nos.
26 | Supply & Installation of Complete Electric power & control wiring complete with PVC conduit and power wiring will be in G.I.Cable tray & hanger supports etc. for Equipment as per Specification and drawings. | 1 | Lot.
27 | City sewerage and water supply connection from city connection point to building connection location. | 1 | Lot.
PART-C RO WATER SYSTEM SYSTEM
1 | Installation, testing & commissioning of OFM RO water system complete in all respectss as shown on drawings & specifications | 1 | Set
2 | Supply, Installation, testing & commissioning of PE(1000 USG) tank complete in all respectss as shown on drawings & specifications | 3 | Nos.
3 | Supply, Installation, Testing & Commissioning of Multistage (2+1 No's) Boosting Pumping system 2nos running and 1no standby with speed controller, control pannel,integrated dry running detection and low water cut out switch complete with valve fitting with all respect as per drawings and specification.(60 Gpm and 8 bar) | 1 | Set
4 | RO WATER DISTRIBUTION SYSTEM
a. | PPR PN 20 piping for RO water system, with fittings, specialties, including all cutting, fitting, fixing and cleaning, wall and slab sleeves, CP clamps, hangers and supports, making connection with fixtures, valves and specialties, chiseling, making wall an floor openings and making good, pressure testing at a pressure of 250 psig, painting of exposed piping in occupied areas with primer and coats of approved paint in approved color complete in all respect.
i. | 2" dia | 270 | Rft.
ii. | 1-1/2" dia | 160 | Rft.
iii. | 1-1/4" dia | 370 | Rft.
iv. | 1" dia | 260 | Rft.
v. | 3/4" dia | 220 | Rft.
vi | 1/2" dia | 530 | Rft.
5 | Gate Valve
i. | 2" dia | 4 | Nos
ii | 1 1/4" dia | 7 | Nos
6 | Strainer 2" dia | 2 | Nos
7 | Check valve 2" dia | 2 | Nos
PART-D GERNAL WORKS
1 | Equipment foundation and equipment shifting charges from Ground floor to foundation pads as per specification and drawings. | 1 | Job
2 | Supply, installation, testing & commissioning of level sensor for Fire Fighting & Plumbing system complete with all respect as per drawings & specification. | 1 | Job
3 | M&P Services Shop drawings & As Built Drawings Color Copies. (Minimum scale 1- 1/8”) Hard Copy and Soft Copy in Autocad format in CD | 4 | Set
4 | Cost of testing, Starting up, commissioning, balancing, adjusting and handling over of the complete Plant. | 1 | Job
5 | Cost of System operation for 3 months (2 Operators ). | 1 | Job