## Summary
GRAND SUMMARY
ACMV, Fire suppression & NOVEC-1230 System
UEP (17th Floor) |  |  |  | Rev.01
Clifton, Karachi. |  |  |  | Date: 22-06-2023
Note: Bilal bhai instructed that SST will be charged on Gross Total Amount
Sr.# | Description | Material | Labour | Total
1 | HVAC | 35926663 | 2838800 | 38765463
2 | FSS | 4626850 | 838250 | 5465100
3 | Novec System | 10354943 | 578000 | 10932943
| Total Cost Rs. | 14981793 | 1416250 | 55163506
Note:
1) | Electric power wiring / supply to be provided at equipment with isolation box by electrical contractor.
2) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
3) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).
4) | Contractor should quote imported make DFCU & WCPU in BOQ / Tender Bids. Local make units (DFCU & WCPU) rates must be provided on letter head only.
Saeed Sahab looking account of ASA

## HVAC
Bill of Quantities
ACMV Works
UEP (17th Floor) | [8 empty] | Rev.01
Clifton, Karachi. | [8 empty] | Date: 22-06-2023
[5 empty] | MATERIAL |  | LABOUR |  | TOTAL
Sr. No. |  | DESCRIPTION | UNIT | QTY | RATE | AMOUNT | RATE | AMOUNT | AMOUNT
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of Consultant
1 |  | Supply and installation of fan coil units of different capacities complete in all respects, ready to operate including all accessories, lindaptor type supports, hanger steel base, vibration isolators, including interconnecting power & control wiring (terminal connection) with inlet & outlet chilled water connections, drain connection, flexible rubber duct connection / connector etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 1.1 | DFCU-01 | Nos. | 2 | 325000 | 650000 | 5000 | 10000 | 660000
2 |  | Supply & installation of valves & accessories for DFCU, complete in all respects as per specifications, drawings and as per instructions of consultant.
| 2.1 | Ball Valve
| i. | 25mm dia | No. | 8 | 6900 | 55200 | 1000 | 8000 | 63200
| 2.2 | Strainers
| i. | 25mm dia | No. | 2 | 6500 | 13000 | 1000 | 2000 | 15000
| 2.3 | Balancing Valve (with self sealing measuring nipples)
| i. | 25mm dia | No. | 2 | 16500 | 33000 | 1500 | 3000 | 36000
| 2.4 | Thermometer 150mm Height Scale Type (with Thermo well) 0 ºC to 60 ºC | No. | 4 | 7000 | 28000 | 1000 | 4000 | 32000
| 2.5 | Pressure Gauge with Ball Valve & Siphon, Liquid filled Dial type range 0 psi to 100 psi. (100mm dial Size) | No. | 4 | 9000 | 36000 | 1000 | 4000 | 40000
| 2.6 | 2-Way Motorized Valve with Actuator (0-100% modulating)
| i. | 25mm dia | No. | 2 | 55000 | 110000 | 1500 | 3000 | 113000
| 2.7 | Digital Decorative Thermostat Controller (BMS Interfacable) with Duct Mounted Sensor | No. | 2 | 58000 | 116000 | 1500 | 3000 | 119000
| 2.8 | Control wiring from controller to sensors, motorized valve and Power wiring up to 15' radius | Job. | 2 | 28000 | 56000 | 3000 | 6000 | 62000
3 |  | Supply and installation of water cooled package units of different capacities complete in all respects, ready to operate with all accessories, lindaptor type supports, including hanger steel base, vibration isolators, including interconnecting power & control wiring (terminal connection) with inlet & outlet chilled water connections, drain connection, flexible rubber duct connection / connector etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 3.1 | WCPU-01 | Nos. | 3 | 750000 | 2250000 | 15000 | 45000 | 2295000
| 3.2 | WCPU-02 | No. | 3 | 950000 | 2850000 | 15000 | 45000 | 2895000
4 |  | Supply & installation of valves & accessories of water cooled package units, complete in all respects as per specifications, drawings and as per instructions of consultant.
| 4.1 | Ball Valve
| i. | 25mm dia | No. | 24 | 7250 | 174000 | 1000 | 24000 | 198000
| 4.2 | Strainer
| i. | 25mm dia | No. | 6 | 6900 | 41400 | 1000 | 6000 | 47400
| 4.3 | Balancing Valve (with self sealing measuring nipples)
| i. | 25mm dia | No. | 6 | 17500 | 105000 | 1500 | 9000 | 114000
| 4.4 | Flexible pipe connectors
| i. | 25mm dia | No. | 12 | 7500 | 90000 | 1000 | 12000 | 102000
| 4.5 | 2-Way Motorized Valve with Actuator (0-100% modulation)
| i. | 25mm dia | No. | 6 | 57000 | 342000 | 1500 | 9000 | 351000
| 4.6 | Flow Switches | No. | 6 | 17000 | 102000 | 1000 | 6000 | 108000
5 |  | Supply & installation of SCH-40 M.S.(As per ASME & API standard, Heavy Quality with standard SCH 40 wall thickness) pipes & fitting for chilled & cooling water circulation system complete with bends, tees, unions, sockets, specials, lindaptor type supports, hangers & anchors, M.S. angle, U channel, roller support, bolts, rods, clamps, concrete fasteners etc as required to complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
| 5.1 | 25mm dia | Rm | 100 | 2300 | 230000 | 650 | 65000 | 295000
| 5.2 | 32mm dia | Rm | 15 | 2880 | 43200 | 750 | 11250 | 54450
| 5.3 | 50mm dia | Rm | 40 | 4340 | 173600 | 820 | 32800 | 206400
6 |  | Supply & installation of Pre Formed Polystyrene (Thermopore) insulation (32 kg/m3 density) for chilled water pipes, bends, tees, unions, sockets, valves and on specials protected with Kraft paper, wrapped with 8oz Canvas cloth than paint with anti fungus paint complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
| 6.1 | 25mm dia | Rm | 15 | 1150 | 17250 | 200 | 3000 | 20250
7 |  | Supply & istallation of uPVC (Sch 40.) drain pipe insulated with 3/8" thick rubber foam insulation including clamps, bends, tees, drain plugs, sockets, protection treatment, PVC tape wrapping, supports & hangers complete in all respects as per specifications, drawings & as per instructions of Consultant.
| 7.1 | 25mm dia | Rm | 40 | 1450 | 58000 | 200 | 8000 | 66000
| 7.2 | 32mm dia | Rm | 20 | 1700 | 34000 | 200 | 4000 | 38000
8 |  | Supply & installation of VAV Boxes as per mentioned in schedule with digital thermostat controller, pressure sensor, control wiring, including flexible duct connection / connector, electrical connection, lindaptor support & hangers complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant.
| 8.1 | VAV-01 | No. | 1 | 268305.6 | 268305.6 | 2500 | 2500 | 270805.6
| 8.2 | VAV-02 | No. | 1 | 273969.6 | 273969.6 | 2500 | 2500 | 276469.6
| 8.3 | VAV-03 | No. | 1 | 273969.6 | 273969.6 | 2500 | 2500 | 276469.6
| 8.4 | VAV-04 | No. | 1 | 279633.6 | 279633.6 | 2500 | 2500 | 282133.6
| 8.5 | VAV-05 | No. | 1 | 279633.6 | 279633.6 | 2500 | 2500 | 282133.6
| 8.6 | VAV-06 | No. | 1 | 279633.6 | 279633.6 | 2500 | 2500 | 282133.6
| 8.7 | VAV-07 | No. | 1 | 279633.6 | 279633.6 | 2500 | 2500 | 282133.6
| 8.8 | VAV-08 | No. | 1 | 279633.6 | 279633.6 | 2500 | 2500 | 282133.6
| 8.9 | VAV-09 | No. | 1 | 279633.6 | 279633.6 | 2500 | 2500 | 282133.6
| 8.1 | VAV-10 | No. | 1 | 285297.6 | 285297.6 | 2500 | 2500 | 287797.6
| 8.11 | VAV-11 | Nos. | 2 | 279633.6 | 559267.2 | 2500 | 5000 | 564267.2
| 8.12 | VAV-12 | Nos. | 3 | 285297.6 | 855892.8 | 2500 | 7500 | 863392.8
| 8.13 | VAV-13 | No. | 1 | 285297.6 | 285297.6 | 2500 | 2500 | 287797.6
| 8.14 | VAV-14 | Nos. | 4 | 285297.6 | 1141190.4 | 2500 | 10000 | 1151190.4
| 8.15 | VAV-15 | No. | 1 | 285297.6 | 285297.6 | 2500 | 2500 | 287797.6
| 8.16 | VAV-16 | No. | 1 | 285297.6 | 285297.6 | 2500 | 2500 | 287797.6
| 8.17 | VAV-17 | No. | 1 | 290961.6 | 290961.6 | 2500 | 2500 | 293461.6
| 8.18 | VAV-18 | Nos. | 4 | 290961.6 | 1163846.4 | 2500 | 10000 | 1173846.4
| 8.19 | VAV-19 | No. | 1 | 290961.6 | 290961.6 | 2500 | 2500 | 293461.6
| 8.2 | VAV-20 | Nos. | 2 | 290961.6 | 581923.2 | 2500 | 5000 | 586923.2
| 8.21 | VAV-21 | No. | 1 | 290961.6 | 290961.6 | 2500 | 2500 | 293461.6
| 8.22 | VAV-22 | Nos. | 2 | 290961.6 | 581923.2 | 2500 | 5000 | 586923.2
| 8.23 | VAV-23 | No. | 1 | 290961.6 | 290961.6 | 2500 | 2500 | 293461.6
| 8.24 | VAV-24 | No. | 1 | 290961.6 | 290961.6 | 2500 | 2500 | 293461.6
| 8.25 | CAV-01 | No. | 1 | 59472 | 59472 | 2000 | 2000 | 61472
| 8.26 | CAV-02 | No. | 1 | 59472 | 59472 | 2000 | 2000 | 61472
| 8.27 | CAV-03 | No. | 1 | 59472 | 59472 | 2000 | 2000 | 61472
| 8.28 | CAV-04 | No. | 1 | 59472 | 59472 | 2000 | 2000 | 61472
| 8.29 | CAV-05 | No. | 1 | 59472 | 59472 | 2000 | 2000 | 61472
| 8.3 | CAV-06 | No. | 1 | 59472 | 59472 | 2000 | 2000 | 61472
| 8.31 | CAV-07 | No. | 1 | 62304 | 62304 | 2000 | 2000 | 64304
| 8.32 | CAV-08 | No. | 1 | 67968 | 67968 | 2000 | 2000 | 69968
| 8.33 | CAV-09 | No. | 1 | 67968 | 67968 | 2000 | 2000 | 69968
| 8.34 | CAV-10 | No. | 1 | 67968 | 67968 | 2000 | 2000 | 69968
9 |  | Supply, fabrication and installation of machine made G.I sheet metal duct different sections supply, return, fresh & exhaust air including plenums, splitter dampers, guide vanes, flexible duct connector, access door, transformation, plenums chambers, wooden frame, lindaptor type supports,, anchors, hangers complete in all respects ready to operate as per drawings, specification, instruction of Consultant. | Sqm | 1475 | 5200 | 7670000 | 650 | 958750 | 8628750
10 |  | Supply & installation of 20mm thick adhesive rubber foam (XLPE) insulation with aluminum foil over fresh air duct only, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqm | 1475 | 4800 | 7080000 | 600 | 885000 | 7965000
11 |  | Supply and installation of acoustical duct sound liner adhesive with aluminum facing 12mm thick in supply air duct complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Sqm | 120 | 4750 | 570000 | 600 | 72000 | 642000
12 |  | Supply, installation of Aluminum fabricated, powder coated Grills, Diffusers and Registers for supply air, return air, exhaust air & fresh air of different sizes (Grade A ), wooden frame, supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant.
| 12.1 | Supply & Return Air Registers / Diffuser with Damper
| i. | 250mm dia | Nos. | 13 | 6075 | 78975 | 750 | 9750 | 88725
| ii. | 300mm dia | Nos. | 39 | 7290 | 284310 | 750 | 29250 | 313560
| iii. | 350mm dia | Nos. | 7 | 8500 | 59500 | 1000 | 7000 | 66500
| iv. | 400mm dia | Nos. | 24 | 9250 | 222000 | 1000 | 24000 | 246000
| v. | 450mm dia | No. | 1 | 105000 | 105000 | 1000 | 1000 | 106000
| 12.2 | Supply & Return Air Grills | Sqm | 2 | 39500 | 79000 | 6000 | 12000 | 91000
| 12.3 | S.S. Wire Mesh with G.I Frame | Sqm | 2 | 18000 | 36000 | 4000 | 8000 | 44000
| 12.4 | Linear Slots 6,000 Series
| i. | 1 Slots slots of 20mm | Rm | 7 | 4450 | 31150 | 750 | 5250 | 36400
| ii. | 2 Slots slots of 20mm | Rm | 120 | 5250 | 630000 | 750 | 90000 | 720000
| 12.5 | Linear Bar Grill 4,000 Series
| i. | 150mm width | Rm | 10 | 6945 | 69450 | 750 | 7500 | 76950
13 |  | Supply & installation of flexible duct including hangers, jubilee clamp complete in all respects as per specification, drawings & as per instruction of consultant.
| 13.1 | 150mm dia | Rm | 150 | 1850 | 277500 | 400 | 60000 | 337500
14 |  | Supply & installation of butterfly damper for above flexible duct with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of consultant.
| 14.1 | 150mm dia | Nos. | 125 | 3000 | 375000 | 750 | 93750 | 468750
15 |  | Supply & installation of Volume Control Damper in 16 SWG G.I sheet metal with gas kits, nut bolts, complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Sqm | 1 | 35000 | 35000 | 4500 | 4500 | 39500
16 |  | Supply and installation of Fire Damper with linkage & fuse complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant.
| 16.1 | 500mm x 250mm | No. | 1 | 7000 | 7000 | 1000 | 1000 | 8000
17 |  | Supply and installation of Back Draft Damper in MS Sheet with gas kits, nut botls. complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant. | Sqm | 1 | 32000 | 32000 | 4500 | 4500 | 36500
18 |  | Painting & Identification work on supports, hangers, platform of condensing units etc complete in all respects with one coat of ICI make Red lead oxide primer & two coats of ICI make enamel paint complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Job. | 1 | 65000 | 65000 | 35000 | 35000 | 100000
19 |  | Testing, balancing and commissioning of water & air side of the system (from independent agency) complete in all respects including air measurement & balancing, temp, pressure & electrical data of related equipment etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job. | 1 | 0 | 0 | 80000 | 80000 | 80000
20 |  | Making of Shop drawings on Auto CAD (latest version) with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job. | 1 | 15000 | 15000 | 20000 | 20000 | 35000
|  | Total Cost of Works Rs. |  |  |  | 35926663 |  | 2838800 | 38765463
Note:
1) | Electric power wiring / supply to be provided at equipment with isolation box by electrical contractor.
2) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
3) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).
4) | Contractor should quote imported make DFCU & WCPU in BOQ / Tender Bids. Local make units (DFCU & WCPU) rates must be provided on letter head only.

## Novec
Bill of Quantities
Fire Suppression Novec-1230
U.E.P (17th Floor) | [8 empty] | Rev.00
Dolmen Sky Tower, Karachi. | [8 empty] | Date: 23-06-2023
S.No. |  | Description | Unit |  | Material |  | Labour |  | Total
|  |  |  | Qty | Rate | Amount | Rate | Amount | Amount Rs.
NOVEC 1230 SYSYEM
1 |  | CLEAN AGENT (FK-5-1-12 Stored In Cylinder - Ul Listed / Fm Approved)
Supply & installation of clean agent in engineered cylinders of FSS with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
| a. | Clean Agent (FK-5-1-12, Fluoroketone) | Kg. | 19 | 145250 | 2759750 | 4000 | 76000 | 2835750
| b. | Clean Agent (FK-5-1-12, Fluoroketone) | Kg. | 63 | 90243 | 5685309 | 2500 | 157500 | 5842809
| c. | Engineered cylinder with head valve, top plug adapter, siphon tube, pressure gauge, brackets and all other items, complete in all respect. | Nos. | 2 | 188429 | 376858 | 5000 | 10000 | 386858
2 |  | Supply & installation of MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant.
| i. | Dia 20 mm (Threaded fitting) | Rm | 6 | 1700 | 10200 | 400 | 2400 | 12600
| ii. | Dia 25 mm (Threaded fitting) | Rm | 4 | 2490 | 9960 | 600 | 2400 | 12360
| iii. | Dia 40 mm (Threaded fitting) | Rm | 6 | 3211 | 19266 | 700 | 4200 | 23466
3 |  | SPRINKLER HEADS
Supply & installation of nozzles with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
Brass Discharge Nozzle - 360 Degrees discharge pattern
| i. | Dia 20 mm | Nos. | 1 | 7000 | 7000 | 1500 | 1500 | 8500
| ii. | Dia 25 mm | Nos. | 2 | 9500 | 19000 | 1500 | 3000 | 22000
4 |  | INPUT & OUTPUT DEVICES
Supply & installation of input and output devices for the clean agent suppression system (integrated with BMS) with wiring, controls & fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant
| i. | Entinguishing Control Panel for the clean agent fire suppression system | Nos. | 2 | 188500 | 377000 | 35000 | 70000 | 447000
| ii. | Manual Abort / Emergency Cut Off Switch | Nos. | 4 | 10000 | 40000 | 1500 | 6000 | 46000
| iii. | Manual Release Switch - Single Action | Nos. | 4 | 12500 | 50000 | 1500 | 6000 | 56000
| iv. | Horn / Strobe | Nos. | 2 | 13700 | 27400 | 1500 | 3000 | 30400
| v. | Alarm Bell | Nos. | 2 | 18900 | 37800 | 1500 | 3000 | 40800
5 |  | Warning Signs (For eg. "DO NOT ENTER", "MANUAL DISCHARGE STATION", "ROOM PROTECTED") | No. | 2 | 15000 | 30000 | 1500 | 3000 | 33000
6 |  | ACTUATION DEVICES
Supply & installation of actuation devices with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
| i. | Solenoid Actuator for the specified cylinder size | Nos. | 2 | 45000 | 90000 | 2000 | 4000 | 94000
| ii. | Manual Control Head for manual actuation of cylinder with safety pull pin | Nos. | 2 | 50000 | 100000 | 5000 | 10000 | 110000
| iii. | Pressure Switch to indicated system discharge with an external manual reset button | Nos. | 2 | 35000 | 70000 | 2000 | 4000 | 74000
| iv. | Low Pressure Switch to monitor the pressure within the cylinder | Nos. | 2 | 35000 | 70000 | 2000 | 4000 | 74000
| v. | Photo Electric Smoke Detector | Nos. | 4 | 8850 | 35400 | 1500 | 6000 | 41400
| vi. | Wire Base 4" Detector Base | Nos. | 4 | 65000 | 260000 | 3000 | 12000 | 272000
7 |  | WIRING
| i. | Supply & installation of wiring of 2C, 1.5 Sq.mm fire resistant shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia MS conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Job. | 1 | 180000 | 180000 | 35000 | 35000 | 215000
8 |  | Making of Shop drawings on Auto CAD 2018 with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects as per instruction of consultant. | Job. | 1 | 10000 | 10000 | 15000 | 15000 | 25000
9 |  | Painting, identification and tagging to the installations and equipments, complete in all respects as per instruction of consultant. | Job. | 1 | 90000 | 90000 | 15000 | 15000 | 105000
10 |  | Flushing of entire fire pipe work according to (NFPA-13), complete in all respects as per instruction of consultant. | Job. | 1 | 0 | 0 | 35000 | 35000 | 35000
11 |  | Testing and commissioning of entire fire fighting and clean agent for fire suppression system complete in all respects as per instruction of consultant. | Job. | 1 | 0 | 0 | 90000 | 90000 | 90000
|  | Cost of Novec System Rs. |  |  |  | 10354943 |  | 578000 | 10932943

## Fire
Bill of Quantities
Fire Suppression Services
U.E.P (17th Floor) | [8 empty] | Rev.01
Dolmen Sky Tower, Karachi. | [8 empty] | Date: 23-06-2023
S.No. |  | Description | Unit | Qty | Material |  | Labour |  | Total
[5 empty] | Rate | Amount | Rate | Amount | Amount
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression system including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1 |  | MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
| 1.1 | Dia 25 mm (Threaded fitting) | Rm. | 430 | 2499 | 1074570 | 600 | 258000 | 1332570
| 1.2 | Dia 32 mm (Threaded fitting) | Rm. | 50 | 3211 | 160550 | 700 | 35000 | 195550
| 1.3 | Dia 40 mm (Threaded fitting) | Rm. | 50 | 3735 | 186750 | 800 | 40000 | 226750
| 1.4 | Dia 50 mm (Threaded fitting) | Rm. | 40 | 4844 | 193760 | 900 | 36000 | 229760
| 1.5 | Dia 65 mm (Welded joints fitting) | Rm. | 110 | 7381 | 811910 | 1150 | 126500 | 938410
| 1.6 | Dia 75 mm (Welded joints fitting) | Rm. | 40 | 9504 | 380160 | 1300 | 52000 | 432160
2 |  | Sprinkler Heads
| 2.1 | Sprinkler Upright type quick response K = 5.6 (Opening Temperature 68ºc) | Nos. | 31 | 3250 | 100750 | 750 | 23250 | 124000
| 2.2 | Sprinkler Pendent type quick response with CP cover plate K = 5.6 (Opening Temperature 57ºC) | Nos. | 146 | 7900 | 1153400 | 750 | 109500 | 1262900
3 |  | Fire extinguishers with fixing accessories.
| 3.1 | Type Class B&C FX-3 (6 Kg. CO2 Carbon Dioxide Gas) | Nos. | 5 | 37500 | 187500 | 1000 | 5000 | 192500
| 3.2 | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 5 | 14500 | 72500 | 1000 | 5000 | 77500
4 |  | Brass body Isolation valves.
| 4.1 | Size. 25 mm | Nos. | 2 | 9000 | 18000 | 1000 | 2000 | 20000
| 4.2 | Size. 40 mm | Nos. | 2 | 17000 | 34000 | 1500 | 3000 | 37000
| 4.3 | Size. 75 mm (C.I body with matching flanges) | Nos. | 2 | 54000 | 108000 | 4000 | 8000 | 116000
5 |  | Making of Shop drawings on Auto CAD 2018 with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects as per instruction of consultant. | Job. | 1 | 10000 | 10000 | 10000 | 10000 | 20000
6 |  | Painting, identification and tagging to the installations and equipments, complete in all respects as per instruction of consultant. | Job. | 1 | 135000 | 135000 | 60000 | 60000 | 195000
7 |  | Flushing of entire fire pipe work according to (NFPA-13), complete in all respects as per instruction of consultant. | Job. | 1 | 0 | 0 | 30000 | 30000 | 30000
8 |  | Testing and commissioning of entire fire fighting and clean agent for fire suppression system complete in all respects as per instruction of consultant. | Job. | 1 | 0 | 0 | 35000 | 35000 | 35000
|  | Total Cost of Fire Suppression Services Rs. |  |  |  | 4626850 |  | 838250 | 5465100
Note:
1) | Access panel provide by the client.
2) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
3) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).