## Summary
HVAC & Fire Fighting Works |  |  |  | 2025-03-12
GUL AHMED ENERGY LIMITED
PHASE # 2 7TH FLOOR, AL-TIJARAH CENTER KARACHI
CONSOLIDATED BILL (IPC 1ST 2ND & 3RD)
S.No | Description | Material | Labour | Amount
1 | HVAC Work | 7627310.3975 | 1808637.14 | 9435947.5375
2 | Fire Fighting | 2471443.765 | 380829.75 | 2852273.515
| Add varaitions | 0 | 0 | 6864988
| Grand Total Amount |  |  | 19153209.0525
| Add | 4.5% |  | 861894.4074
| Total receivalbes |  |  | 20015103.4599
| Received |  |  | #VALUE!
| Net receivables |  |  | #VALUE!

## HVAC
GUL AHMED ENERGY LIMITED
PHASE # 2 7TH FLOOR, AL-TIJARAH CENTER KARACHI
BILL OF QUANTITIES | [6 empty] | CONSOLIDATED BILL (IPC 1ST 2ND & 3RD)
[7 empty] | Material |  | Labour |  | Total Amount
S.# | ITEM DESCRIPTION | QTY | UNIT | SUPPLY Rate | INSTALLATION Rate | TOTAL (Rs.) | Total Qty | AMOUNT | Total Qty | AMOUNT
SECTION - A GENERAL REQUIREMENTS FOR HVAC SYSTEM
1 | Making of Shop Drawings with sectional details complete in all respect for complete HVAC Systems as per Specifications | 1 | Job | 8500 | 12750 | 21250 | 1 | 8500 | 1 | 12750 | 21250 | 90%
2 | Making of As Built Drawings with sectional details complete in all respect for complete HVAC Systems as per Specifications | 1 | Job | 8500 | 8500 | 17000 | 0 | 0 | 0 | 0 | 0
3 | Shifting of equipment from Ground Floor to respective locations.. | 1 | Job | 0 | 233750 | 233750 | 1 | 0 | 1 | 233750 | 233750 | 90%
4 | Excavation and backfilling the earth for pipe works as required to complete the HVAC Works as per Drawings and Specifications. | 1 | Job | 0 | 76500 | 76500 | 1 | 0 | 1 | 76500 | 76500
5 | Dismentaling and Re-Location of existing of VRF A/C Units as installed on site complete in all respects as per drawings. | 1 | Job | 17000 | 34000 | 51000 | 1 | 17000 | 1 | 34000 | 51000 | 90%
6 | Dismentaling of existing Fresh & Exhaust Air Ducts with air devices as installed on site complete in all respects. Preparation of Inventory list of dismantled items for client submission and handing over dismantled items to location as per client instruction. | 1 | Job | 0 | 51000 | 51000 | 1 | 0 | 1 | 51000 | 51000 | 90%
7 | Dismentaling of existing Damaged copper piping as installed on site complete in all respects. Preparation of Inventory list of dismantled items for client submission and handing over dismantled items to location as per client instruction. | 1 | Job | 0 | 76500 | 76500 | 1 | 0 | 1 | 76500 | 76500 | 90%
8 | Dismentaling of existing Damaged insulation as installed on site complete in all respects. Preparation of Inventory list of dismantled items for client submission and handing over dismantled items to location as per client instruction. | 1 | Job | 0 | 42500 | 42500 | 1 | 0 | 1 | 42500 | 42500 | 90%
| Contractor to list and price below with quantities any additional item(s) and/or quantities which are not included but required to complete the lumpsum tender price for this section of works. Should the tenderer fail to insert any item(s) and/or quantities here, it will be deemed that this lumpsum price for the tender includes all items and no subsequent cliams for any additional item will be entertained. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - B OPERATION & MAINTENANCE FOR HVAC SYSTEM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Operation and maintenance of HVAC System |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | One month test run | 1 | Job | 0 | 85000 | 85000 | 1 | 0 | 1 | 85000 | 85000 | 90%
b | Operation of mainteance of HVAC System for one year | 1 | Job | 0 | 1530000 | 1530000 | 0 | 0 | 0 | 0 | 0
c | Special tools and instruments for operation and maineance | 1 | Job | 140250 | 8500 | 148750 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - C COMMON WORKS RESULTS FOR HVAC SYSTEM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Wires, Cables, Conduites and Cable Tray |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply and installation of cables, conduites for power supply and earthing from isolators to AC equipment. Control cable between indoor and outdoor unit and control cable for Fresh Air Unit with cable tray. Complete in all respect as per drawings and specifications. | 1 | Job | 467500 | 76500 | 544000 | 1 | 467500 | 1 | 76500 | 544000 | 90%
| Hangers and Supports for HVAC Ducting |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | Supply and Installation of hangers and supports for HVAC ducting complete in all respect as per drawings and specifications. | 1 | Job | 106250 | 21250 | 127500 | 1 | 106250 | 1 | 21250 | 127500 | 90%
| Hangers and Supports for Refrigerant Piping |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
3 | Supply and Installation hangers and supports for refrigerant piping complete in all respect as per drawings and specifications. | 1 | Job | 153000 | 21250 | 174250 | 1 | 153000 | 1 | 21250 | 174250 | 90%
| Hangers and Supports for HVAC Equipment |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
4 | Supply and Installation of hangers and supports for HVAC equipment complete in all respect as per drawings and specifications. | 1 | Job | 68000 | 17000 | 85000 | 1 | 68000 | 1 | 17000 | 85000 | 90%
| Identification for HVAC Ducting, Piping and Equipment |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
5 | Supply and Installation of identification for HVAC ducting, piping and equipment complete in all respect as per drawings and specifications. | 1 | Job | 29750 | 12750 | 42500 | 1 | 29750 | 1 | 12750 | 42500 | 90%
| Fire Stopping |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
6 | Supply and Installation of Fire stopping complete in all respect as per drawings and specifications. | 1 | Job | 34000 | 8500 | 42500 | 1 | 34000 | 1 | 8500 | 42500 | 90%
| Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - D HVAC INSULATION |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Duct Insulation |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply and installation of 12 mm thick XLPE Insulation of density 28 kg/m3 with Aluminum jacketing for Internal G.I. sheet metal ducts complete in all respect as per schedule, specifications and drawings. | 1300 | Sq.ft | 301.75 | 42.5 | 447525 | 1560.57 | 470901.9975 | 1560.57 | 66324.225 | 537226.2225 | 90%
| Refrigerant pipe insulation |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | Supply and installation of 12 mm thick Pre-moulded Foam Pipe and valve Insulation complete in all respect as per schedule, specifications and drawings. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 3/8" Diameter | 80 | Rft | 191.25 | 51 | 19380 | 302.5 | 57853.125 | 480.5 | 24505.5 | 82358.625 | 90%
b | 1/4" Diameter | 230 | Rft | 182.75 | 51 | 53762.5 | 25 | 4568.75 | 41 | 2091 | 6659.75 | 90%
c | 1/2" Diameter | 180 | Rft | 233.75 | 51 | 51255 | 28.5 | 6661.875 | 80.5 | 4105.5 | 10767.375 | 90%
d | 5/8" Diameter | 90 | Rft | 293.25 | 68 | 32512.5 | 174.66 | 51219.045 | 364.66 | 24796.88 | 76015.925 | 90%
e | 3/4" Diameter | 140 | Rft | 293.25 | 68 | 50575 | 155.5 | 45600.375 | 246.5 | 16762 | 62362.375 | 90%
f | 7/8" Diameter | 20 | Rft | 340 | 85 | 8500 | 24.5 | 8330 | 24.5 | 2082.5 | 10412.5 | 90%
g | 1-1/8" Diameter | 60 | Rft | 391 | 85 | 28560 | 34.5 | 13489.5 | 67.5 | 5737.5 | 19227 | 90%
h | 1-3/8" Diameter | 15 | Rft | 459 | 85 | 8160 | 13.5 | 6196.5 | 48.5 | 4122.5 | 10319 | 90%
i | 1-7/8" Diameter | 40 | Rft | 561 | 85 | 25840 | 35 | 19635 | 75 | 6375 | 26010 | 90%
| Condensate Drain Insulation |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
3 | Supply and installation of 6 mm thick Pre-moulded Armaflex Pipe Insulation complete in all respect as per schedule, specifications and drawings. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 20 mm (3/4 inch) Diameter | 30 | Rft | 153 | 68 | 6630 | 189.6 | 29008.8 | 189.6 | 12892.8 | 41901.6 | 90%
b | 25 mm (1 inch) Diameter | 55 | Rft | 170 | 68 | 13090 | 119 | 20230 | 119 | 8092 | 28322 | 90%
c | 32 mm (1-1/4 inch) Diameter | 95 | Rft | 212.5 | 85 | 28262.5 | 0 | 0 | 0 | 0 | 0
d | 38 mm (1-1/2 inch) Diameter | 35 | Rft | 255 | 85 | 11900 | 17 | 4335 | 17 | 1445 | 5780 | 90%
e | 50 mm (2 inch) Diameter | 50 | Rft | 454.75 | 127.5 | 29112.5 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - E COMMISSIONING OF HVAC |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Testing, Adjusting and balancing for HVAC systems |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Testing, balancing and commissioning of HVAC system complete in all respect including one month test run, measurement and recording of pressure and electrical data and submission of technical/operation manual, LOG book for each related equipment as per specifications and drawings. | 1 | Job | 0 | 212500 | 212500 | 0 | 0 | 1 | 212500 | 212500
| Total Amount (Rs.) Sec - E (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - F REFRIGERANT PIPING |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Refrigerant piping |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply, Installation, testing & Commissioning of refrigerant piping with valves, fittings, Y-joint and specialities complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 3/8" Diameter | 80 | Rft | 688.5 | 170 | 68680 | 302.5 | 208271.25 | 480.5 | 81685 | 289956.25 | 90%
b | 1/4" Diameter | 230 | Rft | 361.25 | 170 | 122187.5 | 25 | 9031.25 | 41 | 6970 | 16001.25 | 90%
c | 1/2" Diameter | 180 | Rft | 1054 | 170 | 220320 | 28.5 | 30039 | 80.5 | 13685 | 43724 | 90%
d | 5/8" Diameter | 90 | Rft | 1428 | 191.25 | 145732.5 | 174.66 | 249414.48 | 364.66 | 69741.225 | 319155.705 | 90%
e | 3/4" Diameter | 140 | Rft | 1627.75 | 212.5 | 257635 | 155.5 | 253115.125 | 246.5 | 52381.25 | 305496.375 | 90%
f | 7/8" Diameter | 20 | Rft | 2067.2 | 212.5 | 45594 | 24.5 | 50646.4 | 24.5 | 5206.25 | 55852.65 | 90%
g | 1-1/8" Diameter | 60 | Rft | 2747.2 | 255 | 180132 | 34.5 | 94778.4 | 67.5 | 17212.5 | 111990.9 | 90%
h | 1-3/8" Diameter | 15 | Rft | 4037.5 | 255 | 64387.5 | 13.5 | 54506.25 | 48.5 | 12367.5 | 66873.75 | 90%
i | 1-7/8" Diameter | 40 | Rft | 4998 | 255 | 210120 | 35 | 174930 | 75 | 19125 | 194055 | 90%
| Condensate Drain piping |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | Supply, Installation, testing & Commissioning of Condensate Drain Piping UPVC Class-D piping with valves, fittings and specialities complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 20 mm (3/4 inch) Diameter | 30 | Rft | 212.5 | 85 | 8925 | 189.6 | 40290 | 189.6 | 16116 | 56406 | 90%
b | 25 mm (1 inch) Diameter | 55 | Rft | 276.25 | 85 | 19868.75 | 119 | 32873.75 | 119 | 10115 | 42988.75 | 90%
c | 32 mm (1-1/4 inch) Diameter | 95 | Rft | 331.5 | 85 | 39567.5 | 0 | 0 | 0 | 0 | 0
d | 38 mm (1-1/2 inch) Diameter | 35 | Rft | 399.5 | 106.25 | 17701.25 | 17 | 6791.5 | 17 | 1806.25 | 8597.75 | 90%
e | 50 mm (2 inch) Diameter | 50 | Rft | 522.75 | 127.5 | 32512.5 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - F (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - G HVAC DUCTS & CASING |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Medium/Low pressure G.I. sheet metal ducting |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply, Installation, testing & Commissioning of medium/low pressure G.I. sheet metal ducting complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 24 gauge | 2100 | Sq.ft | 382.5 | 68 | 946050 | 1190.57 | 455393.025 | 1560.57 | 106118.76 | 561511.785 | 0.9
| Access door for Fresh Air Unit |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | Supply, Installation, testing & Commissioning of access door for Fresh air unit and Cassette type units complete in all respect as per drawings and specifications. | 7 | Nos | 10200 | 850 | 77350 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - G (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - H AIR DUCT ACCESSORIES |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
| Dampers |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply, Installation, Testing & Commissioning of dampers complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Volume Control Damper |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 16"x6" | 4 | Nos | 4250 | 637.5 | 19550 | 2 | 8500 | 2 | 1275 | 9775 | 90%
b | 14"x8" | 1 | No | 4250 | 637.5 | 4887.5 | 1 | 4250 | 1 | 637.5 | 4887.5 | 90%
c | 12"x8" | 1 | No | 3400 | 637.5 | 4037.5 | 0 | 0 | 0 | 0 | 0
| Fire Damper |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
d | 16"x6" | 4 | Nos | 4250 | 637.5 | 19550 | 0 | 0 | 0 | 0 | 0
e | 14"x8" | 1 | No | 4250 | 637.5 | 4887.5 | 0 | 0 | 0 | 0 | 0
f | 12"x8" | 1 | No | 4250 | 637.5 | 4887.5 | 0 | 0 | 0 | 0 | 0
| Flexible Connectors |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | Supply, Installation, testing & Commissioning of flexible connectors between blower section and air duct complete in all respect as per drawings and specifications. | 1 | Job | 68000 | 12750 | 80750 | 1 | 68000 | 1 | 12750 | 80750 | 90%
| Flexible Duct |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
3 | Supply, Installation, testing & Commissioning of flexible duct complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 150 mm (6 inch) Diameter | 75 | Rft | 382.5 | 85 | 35062.5 | 0 | 0 | 0 | 0 | 0
b | 600 mm (24 inch) Diameter. For VRF outdoor unit | 40 | Rft | 2380 | 255 | 105400 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - H (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - I HVAC FANS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Blowers and fans |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply, Installation, testing & Commissioning of blowers and fans with SS impailer complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Centrifgual fans (cabinet type) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 750 Cfm & 1" ESP | 1 | No | 216750 | 8500 | 225250 | 1 | 216750 | 1 | 8500 | 225250
b | 260 Cfm & 0.5" ESP | 1 | No | 169150 | 5100 | 174250 | 1 | 169150 | 1 | 5100 | 174250
c | 240 Cfm & 0.5" ESP | 1 | No | 167450 | 5100 | 172550 | 1 | 167450 | 1 | 5100 | 172550
d | 200 Cfm & 0.5" ESP | 1 | No | 160650 | 4250 | 164900 | 1 | 160650 | 1 | 4250 | 164900
| Total Amount (Rs.) Sec - I (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
| SECTION - J AIR OUTLETS & INLETS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
| Diffusers, Registers, and Grilles |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
1 | Supply, Installation, testing & Commissioning of Diffusers, Registers and Grilles complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
| Fresh Air Diffuser (FAD) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 150x150 (6"x6") | 30 | Nos | 2550 | 425 | 89250 | 31 | 79050 | 31 | 13175 | 92225
b | 225x225 (9"x9) | 2 | Nos | 3400 | 637.5 | 8075 | 1 | 3400 | 1 | 637.5 | 4037.5
| Exhaust Air Register (EAR) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
c | 150x150 (6"x6") | 15 | Nos | 2550 | 425 | 44625 | 14 | 35700 | 14 | 5950 | 41650
d | 225x225 (9"x9) | 2 | Nos | 3400 | 637.5 | 8075 | 0 | 0 | 0 | 0 | 0
| Fresh air intake louver |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
e | 500x250 ( 20"x10") | 1 | No | 6800 | 850 | 7650 | 1 | 6800 | 1 | 850 | 7650 | 90%
f | 300x250 ( 12"x10") | 1 | No | 5950 | 850 | 6800 | 0 | 0 | 0 | 0 | 0
| Exhaust air louver |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
g | 600x250 (24"x10") | 1 | No | 7650 | 850 | 8500 | 0 | 0 | 0 | 0 | 0 | 90%
h | 300x200 (12"x8") | 2 | Nos | 4250 | 850 | 10200 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - J (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
| SECTION - K DECENTRALIZED UNITARY HVAC EQUIPMENTEquipment |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
| Mini Split Air-Conditioners |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply, testing & Commissioning of Mini Split Inverter type Air-Conditioners complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
a | 1.5 TR (For UPS Room) | 1 | No | 289000 | 6800 | 295800 | 0 | 0 | 1 | 6800 | 6800 | 90%
| Variable Refrigerant Flow (VRF) System |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | Supply, installation, testing & Commissioning of Inverter based Variable Refrigerant Flow (VRF) System complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Fresh air processing ducted indoor unit(s). |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | VRF-FAIU (3.5 TR) | 2 | Nos | 607750 | 12750 | 1241000 | 2 | 1215500 | 2 | 25500 | 1241000
| Wall Mounted indoor unit(s). |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 90%
b | VRF-WMIU (1.5 TR) | 4 | Nos | 297500 | 4250 | 1207000 | 4 | 1190000 | 4 | 17000 | 1207000
| Central Controller |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
c | Central Controller to control VRF air conditioning system, including BACnet BMS gateway, work station with 17 inch monitor and one high speed printer. | 1 | No | 1020000 | 127500 | 1147500 | 1 | 1020000 | 1 | 127500 | 1147500
| Total Amount (Rs.) Sec - K (CARRIED FORWARD TO SUMMARY) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 90%
| SECTION - L MAINTENANCE WORKS | [5 empty] | 0 |  | 0 | 0
| Outdoor Units | Below Work for outdoor units will be carried out by M/S Gree (Instruction received by ASPL) | [9 empty] | 90%
1 | Unit 1 (GMV-PDM-280 WNA/B-M): · Identified Issues: · Oil valve leak · 4-way valve leak · Assessment: · Both compressors are operational. · Electronic control cards are functioning correctly. · Urgent Attention Required: Oil valve and 4-way valve leaks observed, necessitating immediate repair. · Recommendation: Master servicing is advised to address all identified issues comprehensively. | 1 | Job |  |  | 0
2 | Unit 2 (GMV-PDM-400 WNA/B-M): · Identified Issues: · Solenoid valve leak · 4-way valve leak · Communication wire damage · Assessment: · Compressors are functioning within normal parameters. · Control cards are intact. · Urgent Attention Required: Solenoid valve leak, 4-way valve leak, and communication wire damage demand immediate attention to ensure system stability. · Recommendation: Master servicing is necessary to rectify all identified issues comprehensively. | 1 | Job |  |  | 0 | [5 empty] | 90%
3 | Unit 3 (GMV-PDM-450 WNA/B-M): · Identified Issues: · Condenser side leak · Three solenoid valves in poor condition · Oil valve leak · Assessment: · Compressors are operating within acceptable parameters. · Control cards are functional. · Urgent Attention Required: Condenser side leak and deteriorating solenoid valves pose a risk to system efficiency and performance. · Recommendation: Comprehensive master servicing is imperative to address all identified issues and ensure optimal system functionality. | 1 | Job |  |  | 0
4 | Unit 4 (GMV-PDM-280 WNA/B-M): · Identified Issues: · Condenser side leak · Oil valve leak · 4-way valve leak · Assessment: · Compressors are operational. · Control cards are functioning correctly. · Urgent Attention Required: Condenser side leak, oil valve leak, and 4-way valve leak necessitate immediate repair to prevent further damage. · Recommendation: Master servicing is advised to address all identified issues comprehensively. | 1 | Job |  |  | 0
5 | Unit 5 (GMV-PDM-280 WNA/B-M): · Identified Issues: · 4-way valve leak · Assessment: · Compressor is operational. · Control cards are intact. · Urgent Attention Required: 4-way valve leak observed, necessitating immediate repair to ensure system efficiency. · Recommendation: Master servicing is necessary to rectify the identified issue comprehensively. | 1 | Job |  |  | 0
| Indoor Units |  |  |  |  | 0
6 | GMVR71G/NAG-K (5 Units): · Identified Issues: · IT coils need replacement for all units. · Assessment: · The coils are deteriorated and no longer functioning optimally. · Urgent Attention Required: Replacement of IT coils is necessary to ensure proper heating and cooling functionality. · Recommendation: Immediate replacement of IT coils for all five units is advised. | 1 | Job |  |  | 0
7 | GMVR36G/NAG-K (2 Units): · Identified Issues: · Two indoor coils need replacement for both units. · Assessment: · The identified coils are damaged and affecting unit performance. · Urgent Attention Required: Replacement of two coils for each unit is necessary to restore optimal operation. · Recommendation: Immediate replacement of coils for both units is advised. | 1 | Job |  |  | 0
8 | GMVR71T/NAG-K (2 Units): · Identified Issues: · Two coils need replacement for both units. · Assessment: · The coils are in need of replacement due to damage or deterioration. · Urgent Attention Required: Replacement of two coils for each unit is necessary to maintain efficient operation. · Recommendation: Immediate replacement of coils for both units is advised. | 1 | Job |  |  | 0
9 | GMVR56G/NAG-K (3 Units): · Identified Issues: · Three coils need replacement for all units. · Assessment: · The coils are in poor condition and impacting unit performance. · Urgent Attention Required: Replacement of three coils for each unit is necessary to ensure proper functioning. · Recommendation: Immediate replacement of coils for all three units is advised | 1 | Job |  |  | 0
| Total Amount (Rs.) |  |  |  |  | 11923766 |  | 7627310.3975 |  | 1808637.14 | 9435947.5375

## Fire
GUL AHMED ENERGY LIMITED
PHASE # 2 7TH FLOOR, AL-TIJARAH CENTER KARACHI
BILL OF QUANTITIES | [6 empty] | CONSOLIDATED BILL (IPC 1ST 2ND & 3RD)
[7 empty] | Material |  | Labour |  | Total Amount
S.# | ITEM DESCRIPTION | QTY | UNIT | SUPPLY Rate | INSTALLATION Rate | TOTAL (Rs.) | Total Qty | AMOUNT | Total Qty | AMOUNT
SECTION - A GENERAL REQUIREMENTS FOR FIRE SUPPRESSION SYSTEM
1 | Making of Shop Drawings with sectional details complete in all respect for complete Fire suppression Systems as per Specifications | 1 | Job | 8500 | 12750 | 21250 | 1 | 8500 | 1 | 12750 | 21250
2 | Making of As Built Drawings with sectional details complete in all respect for complete Fire suppression Systems as per Specifications | 1 | Job | 8500 | 8500 | 17000 | 0 | 0 | 0 | 0 | 0
| Contractor to list and price below with quantities any additional item(s) and/or quantities which are not included but required to complete the lumpsum tender price for this section of works. Should the tenderer fail to insert any item(s) and/or quantities here, it will be deemed that this lumpsum price for the tender includes all items and no subsequent cliams for any additional item will be entertained. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - B OPERATION AND MAINTENANCE FOR FIRE SUPPRESSION SYSTEM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Operation and maintenance of fire suppression system for one year. | 1 | Job | 0 | 255000 | 255000 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - C COMMON WORK RESULTS FOR FIRE SUPPRESSION SYSTEM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Wire, cables, conduites and cable tray |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply and installation of of wire, cables, conduits and cable tray for power supply, earthing and controls of fire suppression system complete in all respect as per drawings and specifications. | 1 | Job | 42500 | 12750 | 55250 | 0 | 0 | 0 | 0 | 0
| Pressure gauges |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | Supply and installation of pressure gauges for fire suppression system complete in all respect as per specifications and drawings. | 2 | Nos | 9350 | 850 | 20400 | 1 | 9350 | 1 | 850 | 10200
| Valves |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
3 | Supply and installation of valves for water based fire suppression system complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Valves For Sprinkler Riser (Main) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 inch (75 mm ) diameter OS&Y Gate Valve | 1 | No | 120912.5 | 3400 | 124312.5 | 1 | 120912.5 | 1 | 3400 | 124312.5
| Pressure regulating valves |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 inch (75 mm ) dia, Class 150, Inlet Pressure 250 PSI | 1 | No | 386750 | 4250 | 391000 | 1 | 386750 | 1 | 4250 | 391000
| ZCV Test Drain valves |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 inch (25 mm) dia | 1 | No | 46750 | 1700 | 48450 | 1 | 46750 | 1 | 1700 | 48450
| Hangers and supports |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
7 | Supply and installation of hangers and supports for fire suppression piping and equipment complete in all respect as per drawings and specifications. | 1 | Job | 127500 | 25500 | 153000 | 1 | 127500 | 1 | 25500 | 153000
| Painting and identification works |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
8 | Painting and identification works of all components, supports, hangers & brackets etc. complete in all respect as per drawings and specifications. | 1 | Job | 29750 | 38250 | 68000 | 1 | 29750 | 1 | 38250 | 68000
| Fire stopping |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
9 | Supply and installation of fire stopping system complete in all respect as per drawings and specifications. | 1 | Job | 25500 | 8500 | 34000 | 1 | 25500 | 1 | 8500 | 34000
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - D TESTING, BALANCING & COMMISSIONING FOR FIRE SUPPRESSION SYSTEM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Testing, balancing and commissioning |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Testing, balancing and commissioning of fire suppression system complete in all respect including one month test run, measurement and recording of pressure and electrical data and submission of technical/operation manual, LOG book for each related equipment as per specifications and drawings. | 1 | Job | 0 | 34000 | 34000 | 0 | 0 | 0 | 0 | 0
2 | Pressure testing of existing fire suppression system network at 7 Bar. | 1 | Job | 12750 | 29750 | 42500 | 0.7 | 8925 | 0.7 | 20825 | 29750
3 | Inspection for operation of existing Fire hose cabinet. | 1 | Job | 0 | 34000 | 34000 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - E INSTRUMENTS AND CONTROLS FOR FIRE SUPPRESSION SYSTEM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Instruments and Controls for fire suppression system |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Zone control valves assembly complete with butterfly valve, water flow switch with supervisory switch (temper switch), pressure gauge, 40 mm sectional drain valve with union and corrosion resistant orifice, butterfuly control valve with supervisory switch as per specifications and drawings. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 3 inch (75 mm ) dia | 1 | No | 193800 | 8500 | 202300 | 1 | 193800 | 1 | 8500 | 202300
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - E (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - F FIRE SUPPRESSION WATER-SERVICE PIPING |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Fire Suppression Water-Service Piping |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| MS piping |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply and installation of ASTM A53 and A120 Schedule 40 MS piping with fittings and specials for fire protection system, including all cutting, fixing, laying through walls and roofs and making good complete in all respect as per drawings and specifications. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | 25 mm (1 inch) Diameter | 700 | Rft | 510 | 212.5 | 505750 | 407 | 207570 | 407 | 86487.5 | 294057.5
b | 32 mm (1-1/4 inch) Diameter | 60 | Rft | 637.5 | 255 | 53550 | 44.1 | 28113.75 | 44.1 | 11245.5 | 39359.25
c | 38 mm (1-1/2 inch) Diameter | 100 | Rft | 841.5 | 297.5 | 113900 | 34 | 28611 | 34 | 10115 | 38726
d | 50 mm (2 inch) Diameter | 120 | Rft | 985.15 | 340 | 159018 | 60.8 | 59897.12 | 60.8 | 20672 | 80569.12
e | 62 mm (2-1/2 inch) Diameter | 260 | Rft | 1529.15 | 382.5 | 497029 | 131.3 | 200777.395 | 131.3 | 50222.25 | 250999.645
f | 75 mm (3 inch) Diameter | 80 | Rft | 1963.5 | 425 | 191080 | 37 | 72649.5 | 37 | 15725 | 88374.5
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - F (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - G FIRE SUPPRESSION SPRINKLER SYSTEM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Wet-pipe sprinkler system |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply and installation of wet-pipe sprinkler system complete in all respect as per drawings and specifications |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
a | Concealed Sprinkler Head 1/2" 68 Deg, Standard Response, Brass Finish, complete with Escuteon plate 1/2" Crome Finish (k=5.6, orifice 1/2") | 90 | Nos | 6630 | 637.5 | 654075 | 65 | 430950 | 65 | 41437.5 | 472387.5
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total Amount (Rs.) Sec - G (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| SECTION - H FIRE EXTINGUISHING SYSTEM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Portable Fire Extinguishers |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Carbondi Oxide Fire Extinguishers |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1 | Supply and installation of 5KG Carbondi Oxide Fire Extinguishers complete in all respect as per drawings and specifications. | 10 | Nos | 24650 | 850 | 255000 | 10 | 246500 | 10 | 8500 | 255000
| Dry Powder Fire Extinguishers |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | Supply and installation of 4.5 KG Dry Powder Fire Exitinguishers complete in all respect as per drawings and specifications. | 10 | Nos | 12325 | 850 | 131750 | 10 | 123250 | 10 | 8500 | 131750
| K-Type Fire Extinguishers |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
3 | Supply and installation of 6 Liter K Type Fire Extinguishers complete in all respect as per drawings and specifications. | 1 | No | 45262.5 | 850 | 46112.5 | 1 | 45262.5 | 1 | 850 | 46112.5
| Ceiling Mounted Dry Powder Fire Extinguishers for Server & Ups Room |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
4 | Supply and installation of Ceiling Mounted Dry Powder Fire Extinguishers system complete in all respect as per drawings and specifications. | 3 | Nos | 23375 | 850 | 72675 | 3 | 70125 | 3 | 2550 | 72675
| Total Amount (Rs.) Sec - H (CARRIED FORWARD TO SUMMARY) |  |  |  |  | 4180402 |  | 2471443.765 |  | 380829.75 | 2852273.515