## Summary
Bank Al-Habib Limited
M/S Aisha Interiors
HVAC & Fire Fighting Work |  |  |  | 2023-12-14
12th Floor Centerpoint Karachi
SUMMARY OF BILL OF QUANTITIES
S.No | Description | Material | Labour | Amount
1 | HVAC Work 12th Floor | 20134650 | 2117550 | 22252200
2 | Fire Fighting 12th Floor | 3496680 | 444500 | 3941180
| Grand Total Amount | 23631330 | 2562050 | 26193380

## HVAC
Bill of Quantities
ACMV Works
Bank Al Habib (12th Floor) | [8 empty] | Rev.00
Centrepoint, Karachi | [7 empty] | Date: 08-12-2023
[5 empty] | Material |  | Labour |  | Total
Sr. No. |  | Description | Unit | Qty | Rate | Amount | Rate | Amount | Amount
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of Consultant
1 |  | Unloading, installation, testing and commissioning of (Owner Supplied) of air handling & fan coil units of different capacities complete in all respects, ready to operate including supply and installation of all accessories, supports, hanger steel base, vibration isolators, including interconnecting power & control wiring (terminal connection) with inlet & outlet chilled water connections, drain connection, flexible rubber duct connection / connector etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
|  | 12F-AHU-01 | Nos. | 2 | 50000 | 100000 | 60000 | 120000 | 220000
1.2 |  | 12F-DFCU-01 | No. | 1 | 8000 | 8000 | 5000 | 5000 | 13000
2 |  | Supply & installation of valves & accessories for DFCUs, FAHU & FAHUs with supports, hangers, flanges, gas kits, nut & bolts where it required, etc. complete in all respects as per specifications, drawings and as per instructions of consultant.
2.1 |  | Gate Valve
i. |  | 25mm dia | Nos. | 4 | 8250 | 33000 | 1000 | 4000 | 37000
ii. |  | 50mm dia | Nos. | 8 | 17500 | 140000 | 2000 | 16000 | 156000
2.2 |  | Strainers
i. |  | 25mm dia | No. | 1 | 7500 | 7500 | 1000 | 1000 | 8500
ii. |  | 50mm dia | Nos. | 2 | 17500 | 35000 | 2000 | 4000 | 39000
2.3 |  | Balancing Valve (with self sealing measuring nipples)
i. |  | 25mm dia | No. | 1 | 13500 | 13500 | 1000 | 1000 | 14500
ii. |  | 50mm dia | Nos. | 2 | 27500 | 55000 | 2000 | 4000 | 59000
2.4 |  | Thermometer 150mm Height Scale Type (with Thermo well) 0 ºC to 60 ºC | Nos. | 6 | 7200 | 43200 | 500 | 3000 | 46200
2.5 |  | Pressure Gauge with Ball Valve & Siphon, Liquid filled Dial type range 0 psi to 100 psi. (100mm dial Size) | Nos. | 6 | 9800 | 58800 | 1000 | 6000 | 64800
2.6 |  | 2-Way Motorized Valve with Actuator (0-100% modulating)
i. |  | 25mm dia | No. | 1 | 168000 | 168000 | 2000 | 2000 | 170000
ii. |  | 40mm dia | Nos. | 2 | 206000 | 412000 | 2000 | 4000 | 416000
2.7 |  | Digital Decorative Thermostat Controller (BMS Interfacable) with Duct Mounted Sensor | Nos. | 3 | 85000 | 255000 | 5000 | 15000 | 270000
2.8 |  | Fan Control Panel with incoming Ckt. Breaker, DOL starter upto 5.5 kW and auto S/D starter above 5.5 kW with protections and safeties for AHUs only | Nos. | 2 | 235000 | 470000 | 5000 | 10000 | 480000
2.9 |  | Control wiring from controller to sensors, motorized valve and Power wiring up to 5 meter radius | Job. | 3 | 10000 | 30000 | 8000 | 24000 | 54000
3 |  | Supply & installation of SCH-40 M.S.(As per ASME & API standard, Heavy Quality with standard SCH 40 wall thickness) pipes & fitting for chilled water circulation system complete with bends, tees, unions, sockets, specials, support, hangers & anchors, M.S. angle, U channel, roller support, bolts, rods, clamps, concrete fasteners etc as required to complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
3.1 |  | 25mm dia | Rm | 5 | 3000 | 15000 | 600 | 3000 | 18000
3.2 |  | 32mm dia | Rm | 1 | 4200 | 4200 | 700 | 700 | 4900
3.3 |  | 40mm dia | Rm | 1 | 4700 | 4700 | 800 | 800 | 5500
3.4 |  | 50mm dia | Rm | 70 | 6200 | 434000 | 1000 | 70000 | 504000
3.5 |  | 65mm dia | Rm | 15 | 8950 | 134250 | 1200 | 18000 | 152250
4 |  | Supply & installation of aluminum foil facing fiber glass (24 kg/m3 density) insulation (on chilled water pipes) with aluminum threaded tape, protected with aluminum cladding, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
4.1 |  | 25mm dia | Rm | 5 | 2550 | 12750 | 600 | 3000 | 15750
4.2 |  | 32mm dia | Rm | 1 | 2750 | 2750 | 700 | 700 | 3450
4.3 |  | 40mm dia | Rm | 1 | 2900 | 2900 | 800 | 800 | 3700
4.4 |  | 50mm dia | Rm | 70 | 3650 | 255500 | 1000 | 70000 | 325500
4.5 |  | 60mm dia | Rm | 15 | 4550 | 68250 | 1200 | 18000 | 86250
5 |  | Supply & istallation of uPVC (Sch 40.) drain pipe insulated with 10mm thick rubber foam insulation including clamps, bends, tees, drain plugs, sockets, protection treatment, PVC tape wrapping, supports & hangers complete in all respects as per specifications, drawings & as per instructions of consultant.
5.1 |  | 25mm dia | Rm | 10 | 1650 | 16500 | 300 | 3000 | 19500
5.2 |  | 32mm dia | Rm | 20 | 2400 | 48000 | 400 | 8000 | 56000
6 |  | Supply, installation, testing and commissioning of Variable Frequency Drive (VFD) with controls & wiring complete in all respects as per specifications, drawings and as per instructions of consultant.
6.1 |  | VFD-01 (4.5 kw approx) | Nos. | 2 | 415000 | 830000 | 15000 | 30000 | 860000
7 |  | Supply, installation, testing and commissioning of of VAV Boxes as per mentioned in schedule with digital thermostat controller, pressure sensor, control wiring, including supply & installation of flexible duct connection / connector, power wiring upto 5 meter with connection, support & hangers complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant.
7.1 |  | VAV-01 | Nos. | 2 | 140000 | 280000 | 5000 | 10000 | 290000
7.2 |  | VAV-02 | No. | 1 | 140000 | 140000 | 5000 | 5000 | 145000
7.3 |  | VAV-03 | No. | 1 | 140000 | 140000 | 5000 | 5000 | 145000
7.4 |  | VAV-04 | No. | 1 | 140000 | 140000 | 5000 | 5000 | 145000
7.5 |  | VAV-05 | No. | 1 | 140000 | 140000 | 5000 | 5000 | 145000
7.6 |  | VAV-06 | Nos. | 2 | 140000 | 280000 | 5000 | 10000 | 290000
7.7 |  | VAV-07 | No. | 1 | 140000 | 140000 | 5000 | 5000 | 145000
7.8 |  | VAV-08 | No. | 1 | 140000 | 140000 | 5000 | 5000 | 145000
7.9 |  | VAV-09 | No. | 1 | 140000 | 140000 | 5000 | 5000 | 145000
7.1 |  | VAV-10 | No. | 1 | 140000 | 140000 | 5000 | 5000 | 145000
7.11 |  | VAV-11 | No. | 1 | 140000 | 140000 | 5000 | 5000 | 145000
8 |  | Supply, installation of ventilation fans including power wiring upto 5 meter with connection, support & hangers complete in all respects ready to operate as per drawings, specification and as per instruction of consultant.
8.1 |  | TAF-01 | Nos. | 2 | 49560 | 99120 | 2000 | 4000 | 103120 | 41300 | 49560
8.2 |  | TAF-02 | Nos. | 6 | 56640 | 339840 | 2000 | 12000 | 351840 | 47200 | 56640
8.3 |  | TAF-03 | Nos. | 6 | 56640 | 339840 | 2000 | 12000 | 351840 | 47200 | 56640
8.4 |  | TAF-04 | Nos. | 8 | 134520 | 1076160 | 2000 | 16000 | 1092160 | 112100 | 134520
8.5 |  | TAF-05 | Nos. | 2 | 134520 | 269040 | 2000 | 4000 | 273040 | 112100 | 134520
9 |  | Supply, fabrication and installation of machine made G.I sheet metal duct different sections supply, return, fresh & exhaust air including plenums, splitter dampers, guide vanes, flexible duct connector / connection, access door, transformation, plenums chambers, wooden frame, hangers, supports & anchors etc, complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Sqm | 750 | 4750 | 3562500 | 800 | 600000 | 4162500
10 |  | Supply & installation of adhesive 20mm thick 25kg/m3 density rubber foam (XLPE) insulation with aluminum foil (except toilet exhaust duct), complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqm | 725 | 6100 | 4422500 | 550 | 398750 | 4821250
11 |  | Supply & installation of acoustical duct sound liner adhesive 25kg/m3 density, 12mm thick in supply air duct complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqm | 50 | 5750 | 287500 | 500 | 25000 | 312500
12 |  | Supply, Installation of Aluminum fabricated, powder coated Grills, Diffusers and Registers for supply air, return air, exhaust air & fresh air of different sizes (Grade A ) wooden frame, supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
12.1 |  | Supply, Return & Exhaust Air Register / Diffuser with Damper
i. |  | 150mm x 100mm | Nos. | 7 | 1500 | 10500 | 500 | 3500 | 14000
ii. |  | 300mm x 300mm | Nos. | 15 | 4500 | 67500 |  | 0 | 67500
12.2 |  | Supply & Return Air Grill
i. |  | 300mm x 250mm | No. | 1 | 4500 | 4500 | 500 | 500 | 5000
ii. |  | 350mm x 250mm | No. | 1 | 5000 | 5000 | 500 | 500 | 5500
12.3 |  | S.S Mesh with G.I Frame | Sqm | 3 | 3000 | 9000 | 1000 | 3000 | 12000
12.3 |  | Linear Slots 6,000 Series
i. |  | 2 Slots of 25mm | Rm | 100 | 5750 | 575000 | 500 | 50000 | 625000
ii. |  | 3 Slots of 25mm | Rm | 15 | 6250 | 93750 | 600 | 9000 | 102750
13 |  | Supply & installation of flexible duct including hangers, jubilee clamp complete in all respects as per specification, drawings & as per instruction of consultant.
13.1 |  | 150mm | Rm | 110 | 450 | 49500 | 100 | 11000 | 60500
14 |  | Supply & installation of butterfly damper for above flexible duct with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of consultant.
14.1 |  | 150mm | Nos. | 98 | 2450 | 240100 | 350 | 34300 | 274400
15 |  | Supply & installation of Volume Control Damper in 16 SWG G.I sheet metal with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of Consultant. | Sqm | 3 | 5000 | 15000 | 1000 | 3000 | 18000
16 |  | Supply & installation of Fire Damper with linkage & fuse complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant. | Sqm | 1 | 5500 | 5500 | 1000 | 1000 | 6500
17 |  | Supply, installation, testing & commissioning of automatic control mechanism / system (logic based) of AHUs, DFCU, VAVs & TAFs, including controls, interlooping, BMS interfacable thermostat temperature sensors, timers, contactors, relays, communication protocols, input & output modules, interconnecting wiring, power wiring, panel box etc, complete in all respects ready to operate as per instruction of | Job. | 1 | 2250000 | 2250000 | 150000 | 150000 | 2400000
|  | Supply & installation of BMS interfacable digital display HMI, addressable, wirelessly connected with wifi, communicate through mobile app / software remotely, including fault alarm / notification etc, complete in all respects ready to operate as per instruction of consultant. | Job. | 1 | 650000 | 650000 | 50000 | 50000 | 700000
18 |  | Supply, fabrication & installation of M.S platform for placement of AHUs (3x3 meter) with M.S checker plate, i-beam, L- brackets, C-channel, anchors, supports, red oxide enamel paint, etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Job. | 2 | 125000 | 250000 | 40000 | 80000 | 330000
19 |  | Testing, balancing and commissioning of water & air side of the system (from independent agency) complete in all respects including flow measurement & balancing, temp, pressure, electrical data of related equipment etc. as per specifications and as per instructions of Consultant | Job. | 1 | 0 | 0 | 100000 | 100000 | 100000
20 |  | Painting & Identification work on pipes & duct, supports, hangers etc. complete in all respects with one coat of ICI make Red lead oxide primer & two coats of ICI make enamel paint as per instruction of Consultant. | Job. | 1 | 25000 | 25000 | 25000 | 25000 | 50000
21 |  | Making of Shop drawings on Auto CAD (latest version) with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job. | 1 | 10000 | 10000 | 15000 | 15000 | 25000
|  | Total Cost of Works (with I.Tax) Rs. |  |  |  | 20134650 |  | 2117550 | 22252200
Note:
1) | Electric power wiring / supply to be provided at equipment with isolation box by electrical contractor.
2) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
3) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## Fire
Bill of Quantities
Fire Suppression Services
Bank Al Habib (12th Floor) | [8 empty] | Rev.00
Centrepoint, Karachi | [7 empty] | Date: 08-12-2023
[5 empty] | Material |  | Labour |  | Total
Sr. No. |  | Description | Unit | Qty | Rate | Amount | Rate | Amount | Amount
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire
suppression system including all equipment, pipe works and
accessories ready to operate as per specifications, drawings
and instructions of consultants.
1 |  | MS Sch-40 seamless pipes including all specials fittings UL
listed & FM approved, threaded, welded joints, flexible pipe,
flanges, coupling, masking plates, bends, tees, clamps,
supports and hangers, sleeves, masking plates chiseling,
cutting holes, making good where required, painting and
protection treatment etc. Complete in all respects.
| 1.1 | Dia 25 mm (Threaded fitting) | Rm. | 200 | 2550 | 510000 | 500 | 100000 | 610000
| 1.2 | Dia 32 mm (Threaded fitting) | Rm. | 20 | 3150 | 63000 | 600 | 12000 | 75000
| 1.3 | Dia 40 mm (Threaded fitting) | Rm. | 14 | 3750 | 52500 | 700 | 9800 | 62300
| 1.4 | Dia 50 mm (Threaded fitting) | Rm. | 32 | 4950 | 158400 | 850 | 27200 | 185600
| 1.5 | Dia 65 mm (Welded joints fitting) | Rm. | 56 | 7380 | 413280 | 1000 | 56000 | 469280
| 1.6 | Dia 100 mm (Welded joints fitting) | Rm. | 30 | 16500 | 495000 | 1500 | 45000 | 540000
2 |  | Sprinkler Heads
| 2.1 | Sprinkler Pendent type (concealed with face / Cover
|  | plate) K = 5.6 (Opening Temperature 57ºC) | Nos. | 86 | 8250 | 709500 | 750 | 64500 | 774000
3 |  | Fire extinguishers with fixing accessories.
| 3.1 | Type Class B&C FX-3 (6 Kg. CO2 Carbon Dioxide Gas) | Nos. | 2 | 27000 | 54000 | 1000 | 2000 | 56000
| 3.2 | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 2 | 14500 | 29000 | 1000 | 2000 | 31000
| 3.3 | Automatic fire extinguisher (10 Kg. Dry Chemical Powder). | No. | 1 | 35000 | 35000 | 1000 | 1000 | 36000
4 |  | Zone Control Valve assembly 100 mm dia complete with
following. (UL Listed)
| 4.1 | UL Listed Pressure reducing valve (PRV) 100 mm dia (01 No)
| 4.2 | OS & Y Gate valve 100 mm size (01 No) | No. | 1 | 892000 | 892000 | 10000 | 10000 | 902000
| 4.3 | Pressure Gauge (02 Nos)
| 4.4 | Water flow switch 100 mm dia (01 No)
| 4.5 | 50 mm dia test valve with sight glass & sectional drain valve
(01 No)
5 |  | Supply & installation of fire stop material (for passive fire
fighting / smoke barrier) in all openings and penetrations,
either in slab or wall, complete in all respects, ready to
operate as per fire stopper recommended material, and as
|  | per instruction of Consultant. | Job. | 1 | 35000 | 35000 | 15000 | 15000 | 50000
6 |  | Making of As-Built & Shop Drawings on AutoCAD 2018 or
latest version with sectional details complete in all respects as
|  | per instructions of consultant. | Job. | 1 | 10000 | 10000 | 10000 | 10000 | 20000
7 |  | Painting, identification and tagging to the installations and
|  | equipments. | Job. | 1 | 40000 | 40000 | 30000 | 30000 | 70000
8 |  | Flushing of entire fire pipe work according to (NFPA-13). | Job. | 1 | 0 | 0 | 30000 | 30000 | 30000
9 |  | Testing, and commissioning of entire fire fighting installation
|  | as per Consultant’s approval. | Job. | 1 | 0 | 0 | 30000 | 30000 | 30000
|  | Total Cost of FSS Rs. |  |  |  | 3496680 |  | 444500 | 3941180
Note:
1) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
2) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).