## Summary
2022-10-31
PAF AIR WAR COLLEGE, KARACHI
SUMMARY OF HVAC WORK
S# | Description | Material Amount | Labour Amount | Total Amount
1 | HVAC Ground Floor | 5407580 | 1575400 | 6982980
2 | HVAC 1st Floor | 14027970 | 2984300 | 17012270
3 | HVAC 2nd Floor | 23395650 | 5393500 | 28789150
4 | HVAC 3rd Floor | 14122550 | 3817600 | 17940150
TOTAL AMOUNT |  | 56953750 | 13770800 | 70724550
Note: Quoted price are Inclusive of Income Tax and other Taxes are charged seperately as per Govt. Rules.

## Ground Floor
PAF AIR WAR COLLEGE, KARACHI | [6 empty] | DATED: 9/15/2022
BILL OF QUANTITIES FOR SUPPLY & INSTALLATION AIR CONDITIONING WORK (GROUND FLOOR)
ITEM NO. | DESCRIPTION | QTY | UNIT | Rates |  | Amount |  | Total Amount
|  |  |  | Material | Labour | Material | Labour
AIR CONDITIONING WORK
1 | SUPPLY & INSTALLATION OF FAN COIL UNITS
1.1 | Supply & Installation of Chilled Water Ducted Type Fan Coil Units as per schedule and specification
a | Ducted type Fan Coil Unit 7.0 TR | 4 | No |  | 8000 | 0 | 32000 | 32000
| Ducted type Fan Coil Unit 3.25 TR | 2 | No |  | 6000 | 0 | 12000 | 12000
2 | G.I. Duct & Allied Works
2.1 | Supply, fabrication, and installation of G.I. Duct work using prime quality sheet metal including hanger & supports and all tees, bends, reducers, elbows, turning vanes, and splitter etc. complete as specified in the specifications, shown on the layout drawing and standards drawing. Following Gauge chart shall be followed as per below mentioned sizes: *- Gauge 26 = Duct size upto 12" *- Gauge 24 = Duct size 13" to 30" *- Gauge 22 = Duct size 31" to 60" *- Gauge 20 = Duct size 61" to 90"
a | Supply & Installation of Duct | 5800 | Sq. Ft | 325 | 90 | 1885000 | 522000 | 2407000
2.2 | Supply and installation of 1” thick, 24 kg/m3 density Glass Wool Insulation with 8 oz. Canvas cloth wrapping around duct with adhesive. All longitudinal and circumferential joints shall be sealed with 2” wide adhesive tape as specified in the specifications and shown on the drawing.
a | Supply & Isnt: Glass Wool Insulation on Ducts | 5800 | Sq. Ft | 180 | 60 | 1044000 | 348000 | 1392000
2.3 | Supply & Installation of 1” thick, 24 kg/m3 density Sound Liner in supply ducts up 5’ from fan discharge with 100% surface applied with adhesive and mechanical fastness with washes 1.25 dia on the inner side of the duct at 6” centre to centre complete in all respect as specified in the specifications.
a | Sound Liner | 400 | Sq. Ft | 250 | 40 | 100000 | 16000 | 116000
2.4 | Supply & Installation of Flexible duct connector minimum 3" wide as shown in the drawings and directed by the engineer in charge.
a | Flexible Duct Connector | 100 | RFt | 400 | 60 | 40000 | 6000 | 46000
2.5 | Duct Supports (Hanger, steel rods etc.) as per specs | 1 | Job | 70000 | 15000 | 70000 | 15000 | 85000
3 | Air Devices
3.1 | Supply & Installation of opposed blade Volume Control Dampers made from 16 SWG. G.I sheets as specified in the specifications, shown on the drawings.
a | VCDs | 20 | Sq. Ft | 3650 | 900 | 73000 | 18000 | 91000
3.2 | Supply & installation of Supply Air Diffusers / Return Air Grills powder coated complete as specified in the specifications, shown on the drawing.
a | Supply Air Diffusers | 40 | Sq. Ft | 3500 | 900 | 140000 | 36000 | 176000
b | Supply Air Diffusers with Dampers | 1 | Sq. Ft | 3850 | 900 | 3850 | 900 | 4750
c | Return Air Diffusers / Grills | 40 | Sq. Ft | 3850 | 900 | 154000 | 36000 | 190000
4 | Supply, Installation of Seamless MS SCH 40 Pipes complete in all respect
4.1 | Supply & installing seamless Schedule 40 pipe including all tees, bend, reducers, hangers etc. complete as specified in the specifications and directed by the engineer incharge.
a | 1'' Dia | 230 | Rft | 740 | 200 | 170200 | 46000 | 216200
b | 1- 1/4" Dia | 100 | Rft | 975 | 210 | 97500 | 21000 | 118500
c | 2" Dia | 30 | Rft | 1496 | 250 | 44880 | 7500 | 52380
d | Pipe Supports | 1 | Lot | 50000 | 20000 | 50000 | 20000 | 70000
5 | Pipe Insulation
5.1 | Supply & installing pre-formed glass wool insulation 64 Kg/m3 density factory applied vapour barrier. Complete and directed by the engineer incharge.
a | 1'' Dia | 230 | Rft | 460 | 90 | 105800 | 20700 | 126500
b | 1- 1/4" Dia | 100 | Rft | 610 | 90 | 61000 | 9000 | 70000
c | 2" Dia | 30 | Rft | 820 | 110 | 24600 | 3300 | 27900
6 | VALVES WITH FITTING AND COMPLETE ACCESSORIES
6.1 | GATE VALVE
a | Gate Valve 1''Ø | 6 | NOS | 6200 | 1000 | 37200 | 6000 | 43200
| Gate Valve 1- 1/4"Ø | 12 | NOS | 9500 | 1000 | 114000 | 12000 | 126000
6.2 | BALANCING VALVES
a | Balancing Valve 1''Ø | 2 | NOS | 13000 | 1000 | 26000 | 2000 | 28000
| Balancing Valve 1- 1/4"Ø | 4 | NOS | 15800 | 1000 | 63200 | 4000 | 67200
6.3 | STRAINERS
a | Strainer 1''Ø | 2 | NOS | 5500 | 1000 | 11000 | 2000 | 13000
| Strainer 1- 1/4"Ø | 4 | NOS | 9500 | 1000 | 38000 | 4000 | 42000
6.4 | 2-WAY MOTORIZED VALVE (0~100% Modulation)
a | 1''Ø | 2 | NOS | 65000 | 3500 | 130000 | 7000 | 137000
| 1- 1/4"Ø | 4 | NOS | 70000 | 3500 | 280000 | 14000 | 294000
7 | METER AND GAUGES
a | Temperature Gauge | 12 | NOS | 7500 | 1000 | 90000 | 12000 | 102000
b | Pressure Gauges with Gauge Cock & Outlet | 12 | NOS | 7300 | 1000 | 87600 | 12000 | 99600
8 | Drain Water System
8.1 | Supply, Installation, testing and commissioning of Condensate drain piping UPVC with 1/2" thick armaflex insulation or equivalent
a | 1-1/4" Dia | 150 | RFT | 425 | 60 | 63750 | 9000 | 72750
b | Drain Pipe Supports | 1 | Lot | 15000 | 5000 | 15000 | 5000 | 20000
9 | Balancing
| Air Balancing of the System with Reports | 1 | Job | 0 | 35000 | 0 | 35000 | 35000
10 | Other
10.1 | Supply, Installation, testing and commissioning of Gree 2.0 Ton Wall Mounted Split Air Conditioner with copper pipe, inslutation and electrical connection | 4 | No | 0 | 30000 | 0 | 120000 | 120000
10.2 | Supply, Installation, testing and commissioning of Gree 3.0 Ton Floor Standing type Split Air Conditioner with copper pipe, inslutation and electrical connection | 2 | No | 0 | 30000 | 0 | 60000 | 60000
10.3 | Digital Decorative Themostate Controller (BMS Interfaceable) | 6 | No | 42000 | 2000 | 252000 | 12000 | 264000
10.4 | Control Wiring from Controller to motorized valve etc. (10 ~ 20' approximate) | 6 | Job | 5000 | 1500 | 30000 | 9000 | 39000
10.5 | Electrical Connections of Fan Coil Unit | 6 | Job | 6000 | 1000 | 36000 | 6000 | 42000
10.6 | Painting of all equipment and piping ,supports etc | 1 | Job | 15000 | 5000 | 15000 | 5000 | 20000
10.7 | Proper Wall Cutting and other holes for pipes & ducts. | 1 | Job | 25000 | 5000 | 25000 | 5000 | 30000
10.8 | Charts & Tags | 1 | Job | 10000 | 5000 | 10000 | 5000 | 15000
10.9 | Shop drawings | 1 | Job | 10000 | 5000 | 10000 | 5000 | 15000
10.10.1 | As built Drawings 3 set and soft copy in CD | 1 | Job | 10000 | 5000 | 10000 | 5000 | 15000
10.10.2 | Cost of testing, commissioning, balancing adjusting and handing over of the complete plant | 1 | Job | 0 | 50000 | 0 | 50000 | 50000
| Installation Total |  |  |  |  | 5407580 | 1575400 | 6982980

## first Floor
PAF AIR WAR COLLEGE, KARACHI | [6 empty] | DATED: 17/09/2022
BILL OF QUANTITIES FOR SUPPLY & INSTALLATION AIR CONDITIONING WORK (1ST FLOOR)
ITEM NO. | DESCRIPTION | QTY | UNIT | Rates |  | Amount |  | Total Amount
|  |  |  | Material | Labour | Material | Labour
AIR CONDITIONING WORK
1 | SUPPLY & INSTALLATION OF FAN COIL UNITS
1.1 | Supply & Installation of Chilled Water Ducted Type Fan Coil Units as per schedule and specification
a | Ducted type Fan Coil Unit 8.0 TR | 3 | No |  | 7000 | 0 | 21000 | 21000
b | Ducted type Fan Coil Unit 5.5 TR | 2 | No |  | 7000 | 0 | 14000 | 14000
c | Ducted type Fan Coil Unit 4.0 TR | 4 | No |  | 7000 | 0 | 28000 | 28000
d | Wall Mounted type Fan Coil Unit 1.2 TR | 4 | No |  | 5000 | 0 | 20000 | 20000
e | Floor Ceiling type Fan Coil Unit 1.5 TR | 4 | No |  | 7000 | 0 | 28000 | 28000
f | Cassette type Fan Coil Unit 1.5 TR | 6 | No |  | 7000 | 0 | 42000 | 42000
g | Cassette type Fan Coil Unit 2.0 TR | 4 | No |  | 7000 | 0 | 28000 | 28000
2 | G.I. Duct & Allied Works
2.1 | Supply, fabrication, and installation of G.I. Duct work using prime quality sheet metal including hanger & supports and all tees, bends, reducers, elbows, turning vanes, and splitter etc. complete as specified in the specifications, shown on the layout drawing and standards drawing. Following Gauge chart shall be followed as per below mentioned sizes: *- Gauge 26 = Duct size upto 12" *- Gauge 24 = Duct size 13" to 30" *- Gauge 22 = Duct size 31" to 60" *- Gauge 20 = Duct size 61" to 90"
a | Supply & Installation of Duct | 8500 | Sq. Ft | 325 | 90 | 2762500 | 765000 | 3527500
2.2 | Supply and installation of 1” thick, 24 kg/m3 density Glass Wool Insulation with 8 oz. Canvas cloth wrapping around duct with adhesive. All longitudinal and circumferential joints shall be sealed with 2” wide adhesive tape as specified in the specifications and shown on the drawing.
a | Supply & Isnt: Glass Wool Insulation on Ducts | 8500 | Sq. Ft | 180 | 60 | 1530000 | 510000 | 2040000
2.3 | Supply & Installation of 1” thick, 24 kg/m3 density Sound Liner in supply ducts up 5’ from fan discharge with 100% surface applied with adhesive and mechanical fastness with washes 1.25 dia on the inner side of the duct at 12” centre to centre complete in all respect as specified in the specifications.
a | Sound Liner | 450 | Sq. Ft | 250 | 40 | 112500 | 18000 | 130500
2.4 | Supply & Installation of Flexible duct connector minimum 3" wide as shown in the drawings and directed by the engineer in charge.
a | Flexible Duct Connector | 250 | RFt | 400 | 60 | 100000 | 15000 | 115000
2.5 | Duct Supports (Hanger, steel rods etc.) as per specs | 1 | Job | 125000 | 65000 | 125000 | 65000 | 190000
3 | Air Devices
3.1 | Supply & Installation of opposed blade Volume Control Dampers made from 16 SWG. G.I sheets as specified in the specifications, shown on the drawings.
a | VCDs | 50 | Sq. Ft | 3650 | 900 | 182500 | 45000 | 227500
3.2 | Supply & installation of Supply Air Diffusers / Return Air Grills powder coated complete as specified in the specifications, shown on the drawing.
a | Supply Air Diffusers | 75 | Sq. Ft | 3500 | 900 | 262500 | 67500 | 330000
b | Supply Air Diffusers with Dampers | 0 | Sq. Ft | 3850 | 900 | 0 | 0 | 0
c | Return Air Diffusers | 75 | Sq. Ft | 3850 | 900 | 288750 | 67500 | 356250
d | Exhaust Air Diffusers | 20 | Sq. Ft | 3850 | 900 | 77000 | 18000 | 95000
4 | Supply, Installation of Seamless MS SCH 40 Pipes complete in all respect
4.1 | Supply & installing seamless Schedule 40 pipe including all tees, bend, reducers, hangers etc. complete as specified in the specifications and directed by the engineer incharge.
a | 3/4'' Dia | 450 | Rft | 400 | 140 | 180000 | 63000 | 243000
b | 1'' Dia | 450 | Rft | 740 | 200 | 333000 | 90000 | 423000
c | 1-1/4'' Dia | 420 | Rft | 975 | 210 | 409500 | 88200 | 497700
d | 1-1/2'' Dia | 20 | Rft | 1110 | 230 | 22200 | 4600 | 26800
e | 2" Dia | 520 | Rft | 1496 | 250 | 777920 | 130000 | 907920
f | Pipe Supports | 1 | Lot | 75000 | 15000 | 75000 | 15000 | 90000
5 | Pipe Insulation
5.1 | Supply & installing pre-formed glass wool insulation 64 Kg/m3 density factory applied vapour barrier. Complete and directed by the engineer incharge.
a | 3/4'' Dia | 450 | Rft | 270 | 80 | 121500 | 36000 | 157500
b | 1'' Dia | 450 | Rft | 460 | 90 | 207000 | 40500 | 247500
c | 1-1/4'' Dia | 420 | Rft | 610 | 90 | 256200 | 37800 | 294000
d | 1-1/2'' Dia | 20 | Rft | 670 | 100 | 13400 | 2000 | 15400
e | 2" Dia | 520 | Rft | 820 | 110 | 426400 | 57200 | 483600
6 | VALVES WITH FITTING AND COMPLETE ACCESSORIES
6.1 | GATE VALVE
a | Gate Valve 3/4''Ø | 54 | NOS | 4100 | 1000 | 221400 | 54000 | 275400
b | Gate Valve 1-1/4''Ø | 27 | NOS | 9500 | 1000 | 256500 | 27000 | 283500
6.2 | BALANCING VALVES
a | Balancing Valve 3/4''Ø | 36 | NOS | 9300 | 1000 | 334800 | 36000 | 370800
b | Balancing Valve 1-1/4''Ø | 18 | NOS | 15800 | 1000 | 284400 | 18000 | 302400
6.3 | STRAINERS
a | Strainer 3/4'' Dia | 18 | NOS | 3600 | 1000 | 64800 | 18000 | 82800
| Strainer 1-1/4'' Dia | 9 | NOS | 7000 | 1000 | 63000 | 9000 | 72000
6.4 | 2-WAY MOTORIZED VALVE
a | 3/4" | 18 | NOS | 52000 | 3500 | 936000 | 63000 | 999000
| 1-1/4" | 9 | NOS | 70000 | 3500 | 630000 | 31500 | 661500
7 | METER AND GAUGES
a | Temperature Gauge with installation accessories | 54 | NOS | 7500 | 1000 | 405000 | 54000 | 459000
b | Pressure Gauges with Gauge Cock & install access: | 54 | NOS | 7300 | 1000 | 394200 | 54000 | 448200
8 | Drain Water System
8.1 | Supply, Installation, testing and commissioning of Condensate drain piping UPVC with 1/2" thick armaflex insulation or equivalent
a | 1-1/4" Dia | 500 | RFT | 425 | 60 | 212500 | 30000 | 242500
a | 1-1/2" Dia | 100 | RFT | 565 | 60 | 56500 | 6000 | 62500
b | Drain Pipe Supports | 1 | Lot | 10000 | 3000 | 10000 | 3000 | 13000
9 | Balancing
| Air Balancing of the System with Reports | 1 | Job | 0 | 30000 | 0 | 30000 | 30000
10 | Other
10.1 | Digital Decorative Themostate Controller (BMS Interfaceable) | 27 | No | 42000 | 2000 | 1134000 | 54000 | 1188000
10.2 | Control Wiring from Controller to motorized valve etc. (10 ~ 25' approximate) | 27 | Job | 5000 | 1500 | 135000 | 40500 | 175500
10.3 | Electrical Connections of Fan Coil Unit | 27 | Job | 6000 | 1000 | 162000 | 27000 | 189000
| Supply, Installation, testing and commissioning of In line Ducted Exhaust Fan : 3000 CFM: 1.2" ESP. | 1 | No. | 375000 | 3000 | 375000 | 3000 | 378000
10.4 | Painting of all equipment and piping, supports etc | 1 | Job | 25000 | 5000 | 25000 | 5000 | 30000
10.5 | Dismentling of Installation of Ceiling for Isntallating Duct to new build partition rooms for reception and meetings | 1 | Job | 35000 | 5000 | 35000 | 5000 | 40000
10.6 | Charts & Tags | 1 | Job | 10000 | 5000 | 10000 | 5000 | 15000
10.7 | Shop drawings | 1 | Job | 10000 | 5000 | 10000 | 5000 | 15000
10.8 | As built Drawings 3 set and soft copy in CD | 1 | Job | 10000 | 5000 | 10000 | 5000 | 15000
10.9 | Cost of testing, commissioning, balancing adjusting and handing over of the complete plant | 1 | Job | 0 | 85000 | 0 | 85000 | 85000
[6 empty] | 14027970 | 2984300 | 17012270

## Second Floor
PAF AIR WAR COLLEGE, KARACHI | [6 empty] | DATED: 9/15/2022
BILL OF QUANTITIES FOR SUPPLY & INSTALLATION AIR CONDITIONING WORK (2ND FLOOR)
ITEM NO. | DESCRIPTION | QTY | UNIT | Rates |  | Amount |  | Total Amount
|  |  |  | Material | Labour | Material | Labour
AIR CONDITIONING WORK
1 | SUPPLY & INSTALLATION OF FAN COIL UNITS
1.1 | Supply & Installation of Chilled Water Ducted Type Fan Coil Units as per schedule and specification
a | Ducted type Fan Coil Unit 8.0 TR | 3 | No |  | 8000 | 0 | 24000 | 24000
b | Ducted type Fan Coil Unit 7.0 TR | 1 | No |  | 8000 | 0 | 8000 | 8000
c | Ducted type Fan Coil Unit 6.5 TR | 1 | No |  | 8000 | 0 | 8000 | 8000
d | Ducted type Fan Coil Unit 6.0 TR | 1 | No |  | 8000 | 0 | 8000 | 8000
e | Ducted type Fan Coil Unit 5.0 TR | 12 | No |  | 8000 | 0 | 96000 | 96000
f | Ducted type Fan Coil Unit 4.0 TR | 7 | No |  | 8000 | 0 | 56000 | 56000
g | Ducted type Fan Coil Unit 3.5 TR | 2 | No |  | 8000 | 0 | 16000 | 16000
h | Ducted type Fan Coil Unit 3.0 TR | 1 | No |  | 8000 | 0 | 8000 | 8000
i | Cassette type Fan Coil Unit 1.0 TR | 4 | No |  | 8000 | 0 | 32000 | 32000
j | Cassette type Fan Coil Unit 1.5 TR | 3 | No |  | 7000 | 0 | 21000 | 21000
2 | G.I. Duct & Allied Works
2.1 | Supply, fabrication, and installation of G.I. Duct work using prime quality sheet metal including hanger & supports and all tees, bends, reducers, elbows, turning vanes, and splitter etc. complete as specified in the specifications, shown on the layout drawing and standards drawing. Following Gauge chart shall be followed as per below mentioned sizes: *- Gauge 26 = Duct size upto 12" *- Gauge 24 = Duct size 13" to 30" *- Gauge 22 = Duct size 31" to 60" *- Gauge 20 = Duct size 61" to 90"
a | Supply & Installation of Duct | 16000 | Sq. Ft | 325 | 90 | 5200000 | 1440000 | 6640000
2.2 | Supply and installation of 1” thick, 24 kg/m3 density Glass Wool Insulation with 8 oz. Canvas cloth wrapping around duct with adhesive. All longitudinal and circumferential joints shall be sealed with 2” wide adhesive tape as specified in the specifications and shown on the drawing.
a | Supply & Isnt: Glass Wool Insulation on Ducts | 16000 | Sq. Ft | 180 | 60 | 2880000 | 960000 | 3840000
2.3 | Supply & Installation of 1” thick, 24 kg/m3 density Sound Liner in supply ducts up 6’ from fan discharge with 100% surface applied with adhesive and mechanical fastness with washes 1.25 dia on the inner side of the duct at 12” centre to centre complete in all respect as specified in the specifications.
a | Sound Liner | 1200 | Sq. Ft | 250 | 40 | 300000 | 48000 | 348000
2.4 | Supply & Installation of Flexible duct connector minimum 3" wide as shown in the drawings and directed by the engineer in charge.
a | Flexible Duct Connector | 750 | RFt | 400 | 60 | 300000 | 45000 | 345000
2.5 | Duct Supports (Hanger, steel rods etc.) as per specs | 1 | Job | 135000 | 75000 | 135000 | 75000 | 210000
3 | Air Devices
3.1 | Supply & Installation of opposed blade Volume Control Dampers made from 16 SWG. G.I sheets as specified in the specifications, shown on the drawings.
a | VCDs | 140 | Sq. Ft | 3650 | 900 | 511000 | 126000 | 637000
3.2 | Supply & installation of Supply Air Diffusers / Return Air Grills powder coated complete as specified in the specifications, shown on the drawing.
a | Supply Air Diffusers | 135 | Sq. Ft | 3500 | 900 | 472500 | 121500 | 594000
b | Supply Air Diffusers with Dampers | 60 | Sq. Ft | 3850 | 900 | 231000 | 54000 | 285000
c | Return Air Diffusers / Grills | 200 | Sq. Ft | 3850 | 900 | 770000 | 180000 | 950000
4 | Supply, Installation of Seamless MS SCH 40 Pipes complete in all respect
4.1 | Supply & installing seamless Schedule 40 pipe including all tees, bend, reducers, hangers etc. complete as specified in the specifications and directed by the engineer incharge.
a | 1'' Dia | 850 | Rft | 740 | 200 | 629000 | 170000 | 799000
b | 1-1/4'' Dia | 900 | Rft | 975 | 210 | 877500 | 189000 | 1066500
c | 1-1/2'' Dia | 350 | Rft | 1110 | 230 | 388500 | 80500 | 469000
d | 2" Dia | 600 | Rft | 1496 | 250 | 897600 | 150000 | 1047600
e | Pipe Supports | 1 | Rft | 135000 | 25000 | 135000 | 25000 | 160000
5 | Pipe Insulation
5.1 | Supply & installing pre-formed glass wool insulation 64 Kg/m3 density factory applied vapour barrier. Complete and directed by the engineer incharge.
a | 1'' Dia | 850 | Rft | 460 | 90 | 391000 | 76500 | 467500
b | 1-1/4'' Dia | 900 | Rft | 610 | 90 | 549000 | 81000 | 630000
c | 1-1/2'' Dia | 350 | Rft | 670 | 100 | 234500 | 35000 | 269500
d | 2" Dia | 600 | Rft | 820 | 110 | 492000 | 66000 | 558000
6 | VALVES WITH FITTING AND COMPLETE ACCESSORIES
6.1 | GATE VALVE
a | Gate Valve 3/4''Ø | 21 | NOS | 4100 | 1000 | 86100 | 21000 | 107100
b | Gate Valve 1-1/4''Ø | 84 | NOS | 9500 | 1000 | 798000 | 84000 | 882000
6.2 | BALANCING VALVES
a | Balancing Valve 3/4''Ø | 7 | NOS | 9300 | 1000 | 65100 | 7000 | 72100
b | Balancing Valve 1-1/4''Ø | 28 | NOS | 15800 | 1000 | 442400 | 28000 | 470400
6.3 | STRAINERS
a | Strainer 3/4'' Dia | 7 | NOS | 3600 | 1000 | 25200 | 7000 | 32200
| Strainer 1-1/4'' Dia | 28 | NOS | 7000 | 1000 | 196000 | 28000 | 224000
6.4 | 2-WAY MOTORIZED VALVE
a | 3/4" | 7 | NOS | 52000 | 3500 | 364000 | 24500 | 388500
| 1-1/4" | 28 | NOS | 70000 | 3500 | 1960000 | 98000 | 2058000
7 | METER AND GAUGES
a | Temperature Gauge with installtion accessories | 60 | NOS | 7500 | 1000 | 450000 | 60000 | 510000
b | Pressure Gauges with Gauge Cock & inst: access: | 60 | NOS | 7300 | 1000 | 438000 | 60000 | 498000
8 | Drain Water System
8.1 | Supply, Installation, testing and commissioning of Condensate drain piping UPVC with 1/2" thick armaflex insulation or equivalent
a | 1-1/4" Dia | 1350 | RFT | 425 | 60 | 573750 | 81000 | 654750
a | 1-1/2" Dia | 900 | RFT | 565 | 60 | 508500 | 54000 | 562500
b | Drain Pipe Supports | 1 | Lot | 125000 | 25000 | 125000 | 25000 | 150000
9 | Balancing
| Air Balancing of the System with Reports | 1 | Job | 0 | 225000 | 0 | 225000 | 225000
10 | Other
10.1 | Digital Decorative Themostate Controller (BMS Interfaceable) | 35 | No | 42000 | 2000 | 1470000 | 70000 | 1540000
10.2 | Control Wiring from Controller to motorized valve etc.etc. (10 ~ 25' approximate) | 35 | Job | 5000 | 1500 | 175000 | 52500 | 227500
10.3 | Electrical Connections of Fan Coil Unit | 35 | Job | 6000 | 1000 | 210000 | 35000 | 245000
10.4 | Painting of all equipment and piping ,supports etc | 1 | Job | 40000 | 15000 | 40000 | 15000 | 55000
10.5 | Dismentling of Installation of Ceiling for Isntallating Duct to new build partition rooms for reception and meetings | 1 | Job | 0 | 60000 | 0 | 60000 | 60000
10.6 | Charts & Tags | 1 | Job | 35000 | 7000 | 35000 | 7000 | 42000
10.7 | Shop drawings | 1 | Job | 25000 | 7000 | 25000 | 7000 | 32000
10.8 | As built Drawings 3 set and soft copy in CD | 1 | Job | 15000 | 10000 | 15000 | 10000 | 25000
10.9 | Cost of testing, commissioning, balancing adjusting and handing over of the complete plant | 1 | Job | 0 | 135000 | 0 | 135000 | 135000
[6 empty] | 23395650 | 5393500 | 28789150

## 3rd Floor
PAF AIR WAR COLLEGE, KARACHI | [6 empty] | DATED: 15/09/2022
BILL OF QUANTITIES FOR SUPPLY & INSTALLATION AIR CONDITIONING WORK (3RD FLOOR)
ITEM NO. | DESCRIPTION | QTY | UNIT | Rates |  | Amount |  | Total Amount
|  |  |  | Material | Labour | Material | Labour
AIR CONDITIONING WORK
1 | SUPPLY & INSTALLATION OF FAN COIL UNITS
1.1 | Supply & Installation of Chilled Water Ducted Type Fan Coil Units as per schedule and specification
a | Ducted Fan Coil Unit 2.5 TR | 4 | No |  | 8500 | 0 | 34000 | 34000
b | Ducted Fan Coil Unit 2.0 TR | 1 | No |  | 8000 | 0 | 8000 | 8000
c | Cassette Fan Coil Unit 1.0 TR | 3 | Nos. |  | 7500 | 0 | 22500 | 22500
d | Cassette Fan Coil Unit 1.5 TR | 2 | Nos. |  | 7500 | 0 | 15000 | 15000
e | Cassette Fan Coil Unit 1.0 TR | 1 | No |  | 7500 | 0 | 7500 | 7500
2 | G.I. Duct & Allied Works
2.1 | Supply, fabrication, and installation of G.I. Duct work using prime quality sheet metal including hanger & supports and all tees, bends, reducers, elbows, turning vanes, and splitter etc. complete as specified in the specifications, shown on the layout drawing and standards drawing. Following Gauge chart shall be followed as per below mentioned sizes: *- Gauge 26 = Duct size upto 12" *- Gauge 24 = Duct size 13" to 30" *- Gauge 22 = Duct size 31" to 60" *- Gauge 20 = Duct size 61" to 90"
a | Supply & Installation of Duct | 18500 | Sq. Ft | 325 | 90 | 6012500 | 1665000 | 7677500
2.2 | Supply and installation of 1” thick, 24 kg/m3 density Glass Wool Insulation with 8 oz. Canvas cloth wrapping around duct with adhesive. All longitudinal and circumferential joints shall be sealed with 2” wide adhesive tape as specified in the specifications and shown on the drawing.
a | Supply & Isnt: Glass Wool Insulation on Ducts | 18500 | Sq. Ft | 180 | 60 | 3330000 | 1110000 | 4440000
2.3 | Supply & Installation of 1” thick, 24 kg/m3 density Sound Liner in supply ducts up 5’ from fan discharge with 100% surface applied with adhesive and mechanical fastness with washes 1.25 dia on the inner side of the duct at 12” centre to centre complete in all respect as specified in the specifications.
a | Sound Liner | 150 | Sq. Ft | 250 | 40 | 37500 | 6000 | 43500
2.4 | Supply & Installation of Flexible duct connector minimum 3" wide as shown in the drawings and directed by the engineer in charge.
a | Flexible Duct Connector | 50 | RFt | 400 | 60 | 20000 | 3000 | 23000
2.5 | Duct Supports (Hanger, steel rods etc.) as per specs | 1 | Job | 225000 | 50000 | 225000 | 50000 | 275000
3 | Air Devices
3.1 | Supply & Installation of opposed blade Volume Control Dampers made from 16 SWG. G.I sheets as specified in the specifications, shown on the drawings.
a | VCDs | 75 | Sq. Ft | 3650 | 900 | 273750 | 67500 | 341250
3.2 | Supply & installation of Supply Air Diffusers / Return Air Grills powder coated complete as specified in the specifications, shown on the drawing.
a | Supply Air Diffusers | 75 | Sq. Ft | 3500 | 900 | 262500 | 67500 | 330000
b | Supply Air Diffusers with Dampers | 60 | Sq. Ft | 3850 | 900 | 231000 | 54000 | 285000
c | Return Air Diffusers / Grills | 125 | Sq. Ft | 3850 | 900 | 481250 | 112500 | 593750
4 | Supply, Installation of Seamless MS SCH 40 Pipes complete in all respect
4.1 | Supply & installing seamless Schedule 40 pipe including all tees, bend, reducers, hangers etc. complete as specified in the specifications and directed by the engineer incharge.
a | 3/4'' Dia | 200 | Rft | 400 | 140 | 80000 | 28000 | 108000
b | 1'' Dia | 80 | Rft | 975 | 210 | 78000 | 16800 | 94800
| 1-1/4'' Dia | 30 | Rft | 1110 | 230 | 33300 | 6900 | 40200
c | Pipe Supports | 1 | Lot | 50000 | 10000 | 50000 | 10000 | 60000
5 | Pipe Insulation
5.1 | Supply & installing pre-formed glass wool insulation 64 Kg/m3 density factory applied vapour barrier. Complete and directed by the engineer incharge.
a | 3/4'' Dia | 200 | Rft | 270 | 80 | 54000 | 16000 | 70000
a | 1'' Dia | 80 | Rft | 460 | 90 | 36800 | 7200 | 44000
| 1-1/4'' Dia | 30 | Rft | 610 | 90 | 18300 | 2700 | 21000
6 | VALVES WITH FITTING AND COMPLETE ACCESSORIES
6.1 | GATE VALVE
a | Gate Valve 3/4''Ø | 18 | NOS | 4100 | 1000 | 73800 | 18000 | 91800
b | Gate Valve 1''Ø | 15 | NOS | 6200 | 1000 | 93000 | 15000 | 108000
6.2 | BALANCING VALVES
a | Balancing Valve 3/4''Ø | 18 | NOS | 9300 | 1000 | 167400 | 18000 | 185400
b | Balancing Valve 1''Ø | 11 | NOS | 13000 | 1000 | 143000 | 11000 | 154000
6.3 | STRAINERS
a | Strainer 3/4' Dia | 6 | NOS | 3600 | 1000 | 21600 | 6000 | 27600
b | Strainer 1'' Dia | 5 | NOS | 5500 | 1000 | 27500 | 5000 | 32500
6.4 | 2-WAY MOTORIZED VALVE (0~100% Modulation)
a | 3/4" | 6 | NOS | 52000 | 3500 | 312000 | 21000 | 333000
b | 1" | 5 | NOS | 65000 | 3500 | 325000 | 17500 | 342500
7 | METER AND GAUGES
a | Temperature Gauge | 22 | NOS | 7500 | 1000 | 165000 | 22000 | 187000
b | Pressure Gauges with Gauge Cock & Outlet | 22 | NOS | 7300 | 1000 | 160600 | 22000 | 182600
8 | Drain Water System
8.1 | Supply, Installation, testing and commissioning of Condensate drain piping UPVC with 1/2" thick armaflex insulation or equivalent
a | 1-1/4" Dia | 350 | RFT | 425 | 60 | 148750 | 21000 | 169750
b | Drain Pipe Supports | 1 | Lot | 10000 | 50000 | 10000 | 50000 | 60000
9 | Balancing
| Air Balancing of the System with Reports | 1 | Job | 0 | 50000 | 0 | 50000 | 50000
10 | Other
10.1 | Digital Decorative Themostate Controller (BMS Interfaceable) | 22 | No | 42000 | 2000 | 924000 | 44000 | 968000
10.2 | Control Wiring from Controller to sensor, motorized valve etc. (10 ~ 20' approximate) | 22 | Job | 5000 | 1500 | 110000 | 33000 | 143000
10.3 | Electrical Connections of Fan Coil Unit | 22 | Job | 6000 | 1000 | 132000 | 22000 | 154000
10.4 | Painting of all equipment and piping ,supports etc | 1 | Job | 40000 | 15000 | 40000 | 15000 | 55000
10.5 | Dismentling of Installation of Ceiling for Isntallating Duct to new build partition rooms for reception and meetings | 1 | Job | 0 | 75000 | 0 | 75000 | 75000
10.6 | Charts & Tags | 1 | Job | 20000 | 5000 | 20000 | 5000 | 25000
10.7 | Shop drawings | 1 | Job | 15000 | 5000 | 15000 | 5000 | 20000
10.8 | As built Drawings 3 set and soft copy in CD | 1 | Job | 10000 | 7000 | 10000 | 7000 | 17000
10.9 | Cost of testing, commissioning, balancing adjusting and handing over of the complete plant | 1 | Job | 0 | 25000 | 0 | 25000 | 25000
| TOTAL COST |  |  |  |  | 14122550 | 3817600 | 17940150