## Grand Summary
Deutcshe bank
Advance work for TER and TR Room
HVAC & FIRE FIGHTING WORK |  |  |  | 2022-06-08
SUMMARY OF BILL OF QUANTITIES
ITEM NO. | DESCRIPTION | MATERIAL AMOUNT | INSTALLATION AMOUNT | TOTAL AMOUNT
1 | HVAC Work 15th Floor | 504500 | 47500 | 552000
2 | HVAC Work 16th Floor | 94000 | 4000 | 98000
3 | Fire Fighting Work 15th Floor | 6785500 | 232250 | 7017750
4 | Fire Fighting Work 16th Floor | 64000 | 47000 | 111000
5 | 01 Year Cost for operation | 0 | 175000 | 175000
| Sub Total Amount RS = | 7448000 | 505750 | 7953750
| Discount = |  |  | 553750
| Discounted Amount RS = |  |  | 7400000
Note: GST & SST will be charged seperately.

## HVAC 15th Floor
BILL OF QUANTITIES
Deutsche Bank Interiors, Karachi | [10 empty] | 2022-04-11
ACMV WORKS (15TH FLOOR) - Advance Package
Ser # | Description | Unit | Qty | Model Make | Delivery Time | Material |  | Labor/Installation |  | Total Cost (Supply + Labor) | Tenderer Remarks
[6 empty] | Supply Cost of Material (Unit) | Total Supply Cost | Labour / Installation Cost (Unit) | Total Labor Cost
1 | ACMV WORKS
1.1 | AIR DEVICES
Supply & installation of grills, diffusers and registers etc for supply, return, exhaust & fresh air of different sizes (Grade A) wooden frame, lindaptor supports and other accessories etc, complete in all respects ready to operate as per drawings, specification and as per instruction of consultant.
a | Supply Air Registers |  |  | UNI-AIR | 3 to 4 weeks | [5 empty] | Local Vender: M/s Shan Associates
i. | 600mm x 600mm | Nos. | 14 |  |  | 17000 | 238000 | 1500 | 21000 | 259000
b | Supply Air Registers (Stainless Steel 304)
i. | 600mm x 600mm | Nos. | 14 |  |  | 84000 | Rate only | 2000 | Rate only | ------
Note: Should be able to withstand weight of 2 persons
1.2 | FLOOR INSULATION
| Supply & installation of adhesive 25mm thick rubber foam (XLPE) insulation with aluminum foil, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqm | 45 | AEROFOAM | Ready Stock | 3500 | 157500 | 500 | 22500 | 180000 | Local Vender: M/s Global Technologies
1.3 | MOTORIZED FIRE DAMPER
Supply & installation of Motorized Fire Damper with gas kits, nut bolts, including pressure transmeter, controller & control wiring, complete in all respects, ready to operate as per specification, drawings & as per instruction of consultant.
a | 1150mm x 300mm | Nos. | 2 | UNI-AIR | 3 to 4 weeks | 54500 | 109000 | 2000 | 4000 | 113000 | Local Vender: M/s Shan Associates
Note: Fire damper to shut off in case of fire & also shut off when unit is turned off.
| TOTAL COST OF ACMV WORKS | [5 empty] | 504500 |  | 47500 | 552000
Note: > Contractor is instructed to visit the site, understand the nature of work and then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work. > Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## HVAC 16th Floor
BILL OF QUANTITIES
Deutsche Bank Interiors, Karachi | [10 empty] | 2022-04-11
ACMV WORKS (16TH FLOOR) - Advance Package
Ser # | Description | Unit | Qty | Model Make | Delivery Time | Material |  | Labor/Installation |  | Total Cost (Supply + Labor) | Tenderer Remarks
[6 empty] | Supply Cost of Material (Unit) | Total Supply Cost | Labour / Installation Cost (Unit) | Total Labor Cost
1 | ACMV WORKS
1.1 | MOTORIZED FIRE DAMPER
Supply & installation of Motorized Fire Damper with gas kits, nut bolts, including pressure transmeter, controller & control wiring, complete in all respects, ready to operate as per specification, drawings & as per instruction of consultant.
a | 450mm x 250mm | Nos. | 2 | UNI-AIR | 3 to 4 weeks | 47000 | 94000 | 2000 | 4000 | 98000 | Local Vender: M/s Shan Associates
Note: Fire damper to shut off in case of fire & also shut off when unit is turned off.
| TOTAL COST OF ACMV WORKS | [5 empty] | 94000 |  | 4000 | 98000
Note: > Contractor is instructed to visit the site, understand the nature of work and then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work. > Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## Fire 15th Floor
DATA CENTRE WORKS - BILL OF QUANTITIES
Deutsche Bank Interiors, Karachi | [9 empty] | 2022-04-11
FIRE SUPPRESSION SERVICES (15TH FLOOR) - Advance Package
Ser # | Description | Unit | Qty | Model Make | Delivery Time | Material |  | Labor/Installation |  | Total Cost (Supply + Labor) | Tenderer Remarks
[6 empty] | Supply Cost of Material (Unit) | Total Supply Cost | Labour Cost (Unit) | Total Labor Cost
1 | FIRE SUPPRESSION SERVICES
1.1 | CLEAN AGENT (FK-5-1-12 Stored In Cylinder - Ul Listed / Fm Approved)
Supply & installation of clean agent in engineered cylinders of FSS with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
a | Clean Agent (FK-5-1-12, Fluoroketone) | KG | 97 | Firex-UAE | 4 to 6 weeks | 48000 | 4656000 | 300 | 29100 | 4685100 | Local Vender: Secure Vision | 6528600
b | Engineered cylinder with head valve, top plug adapter, siphon tube, pressure gauge, brackets and all other items, complete in all respect. | No. | 1 | Firex-UAE |  | 1014000 | 1014000 | 32000 | 32000 | 1046000
1.2 | MS SCH-40 PIPES
Supply & installation of MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant.
a | 15mm dia | Rm | 4 | ==== | ==== | 1900 | 7600 | 460 | 1840 | 9440 | ====
b | 40mm dia | Rm | 3 | ==== |  | 3800 | 11400 | 790 | 2370 | 13770
c | 50mm dia | Rm | 6 | ==== |  | 5000 | 30000 | 990 | 5940 | 35940
1.3 | SPRINKLES
Supply & installation of nozzles with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
a | Brass Discharge Nozzle - 360 Degrees discharge pattern
i. | 13mm dia | No. | 1 | Firex-UAE | 4 to 6 weeks | 46000 | 46000 | 2000 | 2000 | 48000 | Local Vender: Secure Vision
ii. | 38mm dia | No. | 1 | Firex-UAE |  | 52000 | 52000 | 3000 | 3000 | 55000
1.4 | INPUT & OUTPUT DEVICES
Supply & installation of input and output devices for the clean agent suppression system (integrated with BMS) with wiring, controls & fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant
a | Entinguishing Control Panel for the clean agent fire suppression system | No. | 1 | Zeta - UK | 4 to 6 weeks | 248000 | 248000 | 25000 | 25000 | 273000 | Local Vender: Secure Vision
b | Manual Abort / Emergency Cut Off Switch | No | 1 | Local | 2 to 3 weeks | 45000 | 45000 | 2000 | 2000 | 47000 | Local Market
c | Manual Release Switch - Single Action | No | 1 | Local | 2 to 3 weeks | 39000 | 39000 | 2000 | 2000 | 41000 | Local Market
d | Horn / Strobe | No | 1 | Zeta - UK | 4 to 6 weeks | 17000 | 17000 | 2000 | 2000 | 19000 | Local Vender: Secure Vision
e | Alarm Bell | No | 1 | Zeta - UK | 4 to 6 weeks | 11500 | 11500 | 2000 | 2000 | 13500
1.5 | ACTUATION DEVICES
Supply & installation of actuation devices with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
a | Solenoid Actuator for the specified cylinder size | No | 1 | Firex-UAE | 4 to 6 weeks | 72000 | 72000 | 5000 | 5000 | 77000 | Local Vender: Secure Vision
b | Manual Control Head for manual actuation of cylinder with safety pull pin | No | 1 | Firex-UAE |  | 39000 | 39000 | 3000 | 3000 | 42000
c | Pressure Switch to indicated system discharge with an external manual reset button | No | 1 | Firex-UAE |  | 72000 | 72000 | 5000 | 5000 | 77000
d | Low Pressure Switch to monitor the pressure within the cylinder | No | 1 | Firex-UAE |  | 65000 | 65000 | 5000 | 5000 | 70000
1.6 | WIRING
| Supply & installation of wiring of 2C, 1.5 Sq.mm fire resistant shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia G.I conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Job | 1 |  |  | 300000 | 300000 | 25000 | 25000 | 325000
2 | MISCELLANEOUS WORKS
2.1 | FLUSHING, TESTING & COMMISSIONING
a | Flushing of entire fire pipe work according to (NFPA-13), complete in all respects as per instruction of consultant. | Job | 1 |  |  | 20000 | 20000 | 10000 | 10000 | 30000
b | Room Integrity Test for TER room as per NFPA 2001 standard with complete testing reports. | Job | 1 |  |  | 20000 | 20000 | 15000 | 15000 | 35000
c | Testing and commissioning of entire clean agent fire suppression system complete in all respects as per instruction of consultant. Moreover, Testing and Commissioning to be carried out as per the testing and commissioning annexure shared in the RFP. | Job | 1 |  |  | 0 | 0 | 35000 | 35000 | 35000
2.2 | PAINTING & IDENTIFICATION
| Painting, identification and tagging to the installations and equipments, complete in all respects as per instruction of consultant. | Job | 1 | ICI |  | 10000 | 10000 | 10000 | 10000 | 20000 | Local Market
2.3 | MAKING SHOP DRAWINGS
| Making of Shop drawings on Auto CAD 2018 with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects as per instruction of consultant. | Job | 1 |  |  | 10000 | 10000 | 10000 | 10000 | 20000
| TOTAL COST OF FIRE SUPPRESSION SERVICES | [5 empty] | 6785500 |  | 232250 | 7017750 | 0
Note:
1) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
2) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## Fire 16th Floor
DATA CENTRE WORKS - BILL OF QUANTITIES
Deutsche Bank Interiors, Karachi | [9 empty] | 2022-04-11
FIRE SUPPRESSION SERVICES (16TH FLOOR) - Advance Package
Ser # | Description | Unit | Qty | Model Make | Delivery Time | Material |  | Labor/Installation |  | Total Cost (Supply + Labor) | Tenderer Remarks
[6 empty] | Supply Cost of Material (Unit) | Total Supply Cost | Labour/ Installation Cost (Unit) | Total Labor Cost
1 | FIRE SUPPRESSION SERVICES
1.1 | FIRE EXTINGUISHERS
Supply & installation of fire extinguishers with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
a | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | No | 1 | NAFFCO - UAE |  | 20500 | 20500 | 500 | 500 | 21000 | Local Vender: Secure Vision
b | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | No | 1 |  |  | 12500 | 12500 | 500 | 500 | 13000
c | Automatic fire extinguisher (6 Kg. Dry Chemical Powder) | No | 1 |  |  | 21000 | 21000 | 1000 | 1000 | 22000
2 | MISCELLANEOUS WORKS
2.1 | TESTING & COMMISSIONING
a | Testing and commissioning of entire clean agent fire suppression system complete in all respects as per instruction of consultant. Moreover, Testing and Commissioning to be carried out as per the testing and commissioning annexure shared in the RFP. | Job | 1 |  |  | 0 | 0 | 35000 | 35000 | 35000
2.2 | MAKING SHOP DRAWINGS
| Making of Shop drawings on Auto CAD 2018 with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects as per instruction of consultant. | Job | 1 |  |  | 10000 | 10000 | 10000 | 10000 | 20000
| TOTAL COST OF FIRE SUPPRESSION SERVICES | [5 empty] | 64000 |  | 47000 | 111000 | 0
Note:
1) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
2) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## comparison
Fire Rates Analysis / Comparison
Des | PIONEER Rate | SECURE SYSTEM (with GST)
Clean Agent (FK-5-1-12, Fluoroketone) | 6528600 | 4522911
Engineered cylinder with head valve, top plug adapter
SPRINKLES
INPUT & OUTPUT DEVICES
ACTUATION DEVICES
Testing and commissioning

## BLANK BOQ (hidden)
UNILEVER PAKISTAN LTD
3RD FLOOR
Ser # | Description | Unit | Qty | Rate | Amount
1 | CIVIL WORK
1.1 | BLOCK MASONRY
Cement concrete block masonry set in 1:4 cement
mortar with 1:4:5 or 1:3:6 machine made block minimum 800 psi
(approved by the Architect) including racking out joints curing, etc.,
complete as per specifications and relevant drawings
| 6" thick (External) | Sft | 5665
| 4" thick (Internal) | Sft | 500
| 3" Thick brick cladding ( Lobby Feature Wall) | Sft | 200
1.2 | PLASTER
Plaster 0.75" thick 1:4 cement plaster to internal
walls, columns, beams, slabs, lintels, steps, etc., including making
chamfered shape edges or rounding off corners at junctions including
curing, etc., complete as per specifications and relevant drawings.
a | Internal Walls | Sft | 8000
b | External periphery walls | Sft | 6700
1.3 | DRY WALL PARTITION WALL
a | 100 mm MDF partition on 75 mm x 75mm partal wood framing @600 mm x 600mm c.c (approx),in ducco finish,treated with approved antitermite slagnum & zahbia primer on both ends of MDF , shall ensure the sample to be approved before purchase of material. The approved sample shall always be at site as detailed in the General Condition of Contract. | Sft | 7000
b | GLASS WALL PARTITION (Translucent Glass film)
| 12 mm thick imported tempared glass fixed, Champaign color aluminium U- channel along with the wall at top and bottom and polishing of exposed edges,with 3M Electro cut 314 Brand frosted film complete in all respects and as directed by the Architect. | Sft | 3100
1.4 | PAINT
Low VOC acrylic emulsion by JOTUN paint on walls of approved quality and shade including rubbing, filling and primer coat., complete in all respects.
a | Internal Fair Faced Textured paint (includes walls and ceiling) | Sft | 5000
b | Internal Walls | Sft | 18500
External Weathred shield
c | 3 coats, external weathered shield by JOTUN, ICI, Nelson paint complete in all respects of approved quality and shade including rubbing, filling and primer coat. | Sft | 6700
1.5 | FLOORING & SPECIAL FINISHES
1.5.1 | PORCELAIN TILES IN OFFICE SPACES
Porcelain tile of 12"x24" full body approved quality.Shade pattern set in 1:4 cement mortar including preparing proper base of 1:2:4 concrete mortar all as per specification and drawing complete in all respect. (MML Product supplied by Benitoz or Equivalent; color & size to be approved by the Architect, price will be Rs. 3000 / sqm)
a | Flooring | Sft | 1000
1.5.2 | PORCELAIN TILES IN WET AREA TILES
Porcelain tile of 12"x24" full body approved quality.Shade pattern set in 1:4 cement mortar including preparing proper base of 1:2:4 concrete mortar all as per specification and drawing complete in all respect. (MML Product supplied by Benitoz or Equivalent; color & size to be approved by the Architect, price will be Rs. 3000 / sqm)
a | Floor | Sft | 1350
b | Wall | Sft | 4500
1.5.3 | CORRIDOR TILES
Porcelain tile of Fiandre Marmi MaximumTravertino size 5'x10' full body approved quality.Shade pattern set in 1:4 cement mortar including preparing proper base of 1:2:4 concrete mortar all as per specification and drawing complete in all respect. (Fiandre Product supplied by Benitoz or Equivalent; color & size to be approved by the Architect, price will be Rs. 13000 / sqm)
a | Floor | Sft | 15750
1.5.4 | GRANITE COUNTER TOP
Granite counter top , including all beds and anchoring, finished as below: (with basin hole cutting and special finishes complete as per drawing ) The Granite will be installed on a GI frame with red oxide coating and the finished with black spray paint. Rs. 800 / sqft
b | Polished finish on Counter Tops | Sft | 260
1.5.5 | GRANITE STEPS
i | Granite to be installed on the Steps using dry bond methodology . Dry bond to be used is Ressichem T210 or Millwala's Tifix
ii | Grouting. Water proof grouting color to be specified by the Architect.
Included in the laying of the Granite will be preparation of floor using cement mix to achieve perfect alignment a required of the floor for the application of tiles. Rs. 800 / sqft
iii | 3" Flame torch finish on Staircase Tread 5'-0" | No | 17
iv | Polish finish on Staircase Riser | No | 21
1.6 | SPECIAL FINISHES
a | Branding and Display (refer to attachment) | Sft | 765
b | Green wall (refer to attachment) baseprice Rs. 2500 SQFT | Sft | 350
c | Ceramic wall cladding (refer to attachment) | Sft | 265
b | Internal Ceiling | Sft | 26000
1.7 | ALUMINUM WINDOW
EXTERNAL WINDOWS
Aluminum Windows using imported section and high quality hardware; that must be airtight with minimum infiltration and exfiltration properties. The Aluminum section will be powder coated, color to be approved by Architect.
(Double-Glazed assembly with U-value of 1.4 W/Sqm.K in 6mm Low-E Exterior Glass + 12mm Air Gap (with or without Argon filling) + 6mm local clear Internal Glass)
| Imported Aluminum windows of W1 size 6'-0" x 4'-6" on front façade. | No. | 7
| Imported Aluminum windows of W2 size 14'-0" x 4'-6" on front façade (Board Room) . | No. | 1
TOTAL COST OF CIVIL WORK
2 | INTERIOR FINISHES WORK
2.1 | CARPET FLOOR
| Carpet as specified by Architect (For spec find the attachment) SQFT Rs. 325 | Sft | 20000
2.2 | VINYL FLOORING
Seamless vinyl flooring by Tarkett or equivalent. Thinkness 4.5mm. (50 mm x 50 mm tile) Inteface level set collection availabe from pak carpets or equivalent. SQFT Rs .265
| Color and size as approved by the Architect. | Sft | 550
2.3 | RUBBER FLOORING
| (Gym Area) 8.2 MM Thickness (For spec find the attachment) | Sft | 150
2.3 | FALSE CEILING
a | CEMENT BOARD CEILING
| Cement Board false ceiling at edges allaround the rooms and corridors to as make-up space to ensure metal pan ceilings are not cut and are used as full tiles. (Rs:110) | Sft | 27500
b | STEEL MESH CEILING IN VITALITY ZONE (Hexazonal MS frame rapped with steel mesh) | Sft | 1600
c | ALUMINUM CEILING ( High-grade pre-coated aluminum alloy ) 0.5mm~1.0mm thinckness | Sft | 1250
2.4 | MDF CLADDING (2" thick partal wood frame rapped around 1/2" thick one side MDF sheet).
| Providing MDF cladding on all exposed columns. | Sft | 7000
2.8 | JOINERY
1.5" thick solid core commercial ply veneer flush door shutters (Formite 7195 - Baluchistan Laminates) SWG G.I 16 gauage door frames 2" x 7" so lignum painted 2"x5/8", approved quality of oxidized brass hinges, brass screw, tower bolts, imported locks top of the line quick set hydraulic door closer (brand-New Star Japanese) Wherever needed aluminum push plates on both sides door stopper and other hardware of brass including iron hold fasts, complete in all respects as per drawings and as directed by the Architect.
| Size 3'-0" X 7'-0" | No | 6
| Size 2'-6" X 7'-0" | No | 9
2.9 | METAL SCREEN
| Laser cut perforated ( High Strength Low Alloy HSLA steel ) corten metal sheet. | Sft | 950
2.7 | Metal framing joinery work for the perforated partition and S.S pipes feature. | Sft | 300
2.9 | SKIRTING
a | PVC skirting of 2" thick in dark grey color. | Rft | 3500
TOTAL COST OF INTERIOR FINISHES WORK
3 | IMPORTED PARTITION WALLS & DOOR
3.1 | WOODEN PARTITION | Sft | 5500
3.2 | 6 plus 6mm LAMINATED TEMPERED GLASS PARTITION | Sft | 2500
3.3 | 10mm TEMPERED GLASS DOOR IN PARTITION | No | 30
3.4 | WOODEN DOOR IN PARTITION | No | 2
TOTAL COST OF PARTITION WALL & DOORS
SUMMARY
1 | CIVIL WORK
2 | INTERIOR FINISHES WORK
3 | PARTITION WALLS & DOORS
TOTAL COST