## 15F
Deutsche Bank
Karachi |  | REV#01
15th Floor |  | Date: 11-05-2022
SCHEDULE OF DUCTED FAN COIL UNITS
Unit Tag No. |  | DFCU-01
Quantity | Nos | 1
Space Served |  | Lift Lobby
Fan
Supply Air Flow | CFM | 665
Fresh Air Flow | CFM | 65
External Static Pressure | Inch.WG | 0.3
Fan Rotation | RPM | 960
Max. Fan Outlet Velocity | FPM | 1200
Max. Sound Level from 3.3ft | dB | 50
Cooling Coil
Max. Coil Face Velocity | FPM | 450
Total Cooling Capacity | BTU / Hr | 20400
Total Sensible Capacity | BTU / Hr | 15442.8
Sensible Heat Ratio |  | 0.757
Entering Air Temperature(dB) | Deg ºF | 77.5
Entering Air Temperature(wB) | Deg ºF | 65.2
Leaving Air Temperature(dB) | Deg ºF | 55.9
Leaving Air Temperature(wB) | Deg ºF | 54.8
Chilled Water Ent. Temp. | Deg ºF | 46
Chilled Water Lvg. Temp. | Deg ºF | 56
Chilled Water Flow | US GPM | 4.08
Max. Water Velocity | FPS | 2.5
Unit Construction
Type of Unit |  | Ceiling Concealed Ducted Type
Minimum No. of Rows |  | 4
Built-in Air Vent for Coil |  | YES
Built-in Drain Point for Coil |  | YES
Electrical Data
Power Input (Approx) | kW | *
Volts | V | 220
Phase | Ǿ | 1
Cycle | Hz | 50
Motor Class |  | *
Motor Protection |  | Class F, IP 55
Accessories with Each Unit: |  | Digital Fan Speed Selector, Thermostat, Cleanable Filter with filter box
Notes:
A- Motor power input and class to be provided by the manufacturer along with data sheet.
B- Computer selection of each FCU to be provided by the suppliers for Consultant approval.

## 16F
Deutsche Bank
Karachi |  |  |  | REV#01
16th Floor |  |  |  | Date: 11-05-2022
SCHEDULE OF DUCTED FAN COIL UNITS
Unit Tag No. |  | DFCU-01 | DFCU-02 | DFCU-03
Quantity | Nos | 1 | 2 | 1
Space Served |  | Technology Room (T.R) | Lift Lobby | Small Meeting Room, Waiting
Fan
Supply Air Flow | CFM | 700 | 665 | 660
Fresh Air Flow | CFM | 0 | 65 | 90
External Static Pressure | Inch.WG | 0.3 | 0.3 | 0.35
Fan Rotation | RPM | 960 | 960 | 960
Max. Fan Outlet Velocity | FPM | 1200 | 1200 | 1200
Max. Sound Level from 3.3ft | dB | 50 | 50 | 50
Cooling Coil
Max. Coil Face Velocity | FPM | 450 | 450 | 450
Total Cooling Capacity | BTU / Hr | 13200 | 20400 | 22800
Total Sensible Capacity | BTU / Hr | 12975.6 | 15442.8 | 17464.8
Sensible Heat Ratio |  | 0.983 | 0.757 | 0.766
Entering Air Temperature(dB) | Deg ºF | 69.5 | 77.5 | 80.1
Entering Air Temperature(wB) | Deg ºF | 58.1 | 65.2 | 65.8
Leaving Air Temperature(dB) | Deg ºF | 51.9 | 55.9 | 54.4
Leaving Air Temperature(wB) | Deg ºF | 50.8 | 54.8 | 53.1
Chilled Water Ent. Temp. | Deg ºF | 46 | 46 | 46
Chilled Water Lvg. Temp. | Deg ºF | 56 | 56 | 56
Chilled Water Flow | US GPM | 2.64 | 4.08 | 4.56
Max. Water Velocity | FPS | 2.5 | 2.5 | 2.5
Unit Construction
Type of Unit |  | Ceiling Concealed Ducted Type | Ceiling Concealed Ducted Type | Ceiling Concealed Ducted Type
Minimum No. of Rows |  | 4 | 4 | 4
Built-in Air Vent for Coil |  | YES | YES | YES
Built-in Drain Point for Coil |  | YES | YES | YES
Electrical Data
Power Input (Approx) | kW | * | * | *
Volts | V | 220 | 220 | 220
Phase | Ǿ | 1 | 1 | 1
Cycle | Hz | 50 | 50 | 50
Motor Class |  | * | * | *
Motor Protection |  | Class F, IP 55 | Class F, IP 55 | Class F, IP 55
Accessories with Each Unit: |  | Digital Fan Speed Selector, Thermostat, Cleanable Filter with filter box | Digital Fan Speed Selector, Thermostat, Cleanable Filter with filter box | Digital Fan Speed Selector, Thermostat, Cleanable Filter with filter box
Notes:
A- Motor power input and class to be provided by the manufacturer along with data sheet.
B- Computer selection of each FCU to be provided by the suppliers for Consultant approval.