## Sheet1
BOQ OF OVERHAULING, REPAIRING AND REPLACEMENT WORKS OF AIR HANDLING UNITS(AHU) OF BA BUILDING KARACHI
S.NO | DESCRIPTION | Qty | Unit | Material Rate | Labour Rate | Material Amount | Labour Amount
4th FLOOR A/B AHU UNIT
1 | Replacement of Rubber isolator | 1 | Job | 30000 | 10000 | 30000 | 10000
2 | Complete Ahu floor Foundation,floor rusted coluum u channel with epoxy paint Replacement with insulation. | 1 | job | 20000 | 15000 | 20000 | 15000
3 | Replacement of motor bearing, Make SKF & FAG & motor foundation & belt guard safety cover | 1 | job | 30000 | 12000 | 30000 | 12000
4 | AHU motor complete overhauling without winding,blower repairing or replacement & balancing,shaft allighment,polishing & replacement of blower bearing,pillow block,make SKF & FAG with grease niple for relubrication.(And then show it by doing a grease injection test). | 1 | job | 90000 | 40000 | 90000 | 40000
5 | Water proof light inside AHU 40 watt | 2 | job | 5000 | 2000 | 10000 | 4000
6 | Replacement of evaporator drain tray & coil to coil tray & coil bottom & base Stainless Steel channel. | 1 | job | 30000 | 25000 | 30000 | 25000
7 | Coil descaling internal and external service | 1 | job | 20000 | 20000 | 20000 | 20000
8 | blower louvre epoxy paint with primer & hoiusing inside or outside | 1 | job | 25000 | 15000 | 25000 | 15000
9 | sound proof alluminium foil face EPDM foam insolation replacement inside.& complete inside alluminium cladding . | 1 | job | 224000 | 54000 | 224000 | 54000
10 | supply canvas duct connector inside/ AHU room replace fire proof insulation with anti fungus paint with another paint | 250 | sq/ft | 160 | 80 | 40000 | 20000
11 | Complete AHU paint outside & AHU room oil base mate finish NIPPON paint. | 1 | job | 85000 | 35000 | 85000 | 35000
12 | gate valves,globe valve,moterized valve & strainer descalling of chilled water line | 1 | job | 25000 | 20000 | 25000 | 20000
13 | Pressure gauge 0.2-100 PSIG made in USA fix with pipe nipple and socket,gauge cock siphon | 1 | job | 20000 | 3000 | 20000 | 3000
14 | Chilled water line supply & return aslo anti fungus paint & another paint with EPS thermocol insulation. | 1 | job | 15000 | 10000 | 15000 | 10000
15 | AHU belt replacement make continental | 1 | job | 20000 | 2000 | 20000 | 2000
16 | water balancing | 1 | job | 0 | 10000 | 0 | 10000
17 | supply & installation of complete filter frame & alluminium air filter | 1 | job | 160000 | 20000 | 160000 | 20000
18 | Miscellanous work | 1 | job | 15000 | 10000 | 15000 | 10000
19 | door hinges & lock | 1 | job | 5000 | 2000 | 5000 | 2000
20 | Drain pipe STEELEX UPVC SCH40 with fitting size 1.5'' | 50 | Rft | 550 | 200 | 27500 | 10000
21 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 35000 | 5000 | 35000 | 5000
22 | inlet/outlet chilled water line thermometer supply & installation | 1 | job | 20000 | 3000 | 20000 | 3000
Sub Total Amount Rs | [5 empty] | 946500 | 345000
MEZZAINE B FLOOR AHU UNIT
1 | Replacement of Rubber isolator | 1 | job | 30000 | 10000 | 30000 | 10000
2 | Complete Ahu floor Foundation,floor rusted colum u channel with epoxy paint Replacement with insulation. | 1 | job | 20000 | 15000 | 20000 | 15000
3 | Replacement of motor bearing, Make SKF & FAG & motor foundation &+B34:B38 belt guard safety cover | 1 | job | 30000 | 20000 | 30000 | 20000
4 | AHU motor complete overhauling without winding,blower repairing or replacement & balancing,shaft allighment,polishing & replacement of blower bearing,pillow block,make SKF & FAG with grease niple for relubrication.(And then show it by doing a grease injection test). | 1 | job | 90000 | 30000 | 90000 | 30000
5 | Water proof light inside AHU 40 watt | 2 | Nos | 5000 | 2000 | 10000 | 4000
6 | Replacement of evaporator drain tray & coil bottom & base Stainless Steel channel. | 1 | job | 25000 | 15000 | 25000 | 15000
7 | Coil descaling internal and external service | 1 | job | 20000 | 20000 | 20000 | 20000
8 | blower louvre epoxy paint with primer & hoiusing inside or outside | 1 | job | 30000 | 20000 | 30000 | 20000
9 | sound proof alluminium foil face EPDM foam insolation replacement inside.& complete inside alluminium cladding . | 1 | job | 103750 | 25000 | 103750 | 25000
10 | supply canvas duct connector inside/ AHU room replace fire proof insulation with anti fungus paint with another paint | 250 | sq/ft | 200 | 100 | 50000 | 25000
11 | Complete AHU paint outside & AHU room oil base mate finish NIPPON paint. | 1 | job | 90000 | 40000 | 90000 | 40000
12 | gate valves,globe valve,moterized valve & strainer descalling of chilled water line | 1 | job | 25000 | 20000 | 25000 | 20000
13 | Pressure gauge 0.2-100 PSIG made in USA fix with pipe nipple and socket,gauge cock siphon | 1 | job | 20000 | 3000 | 20000 | 3000
14 | Chilled water line supply & return aslo anti fungus paint & another paint with EPS thermocol insulation. | 1 | job | 15000 | 10000 | 15000 | 10000
15 | AHU belt replacement make continental | 1 | job | 20000 | 2000 | 20000 | 2000
16 | water balancing | 1 | job | 0 | 10000 | 0 | 10000
17 | supply & installation of complete filter frame & alluminium air filter | 1 | job | 70350 | 15000 | 70350 | 15000
18 | Miscellanous work | 1 | job | 10000 | 10000 | 10000 | 10000
19 | door hinges & lock | 1 | job | 5000 | 2000 | 5000 | 2000
20 | Drain pipe STEELEX UPVC SCH40 with fitting size 1.5'' | 50 | rft | 550 | 200 | 27500 | 10000
21 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 30000 | 5000 | 30000 | 5000
Sub Total Amount Rs | [5 empty] | 721600 | 311000
GROUND A FLOOR AHU UNIT
[6 empty] | 0 | 0
1 | Replacement of Rubber isolator | 1 | job | 30000 | 10000 | 30000 | 10000
2 | Complete Ahu floor Foundation,floor rusted colum u channel with epoxy paint Replacement with insulation. | 1 | job | 20000 | 15000 | 20000 | 15000
3 | Replacement of motor bearing, Make SKF & FAG & motor foundation & belt guard safety cover | 1 | job | 30000 | 12000 | 30000 | 12000
4 | AHU motor complete overhauling without winding,blower repairing or replacement & balancing,shaft allighment,polishing & replacement of blower bearing,pillow block,make SKF & FAG with grease niple for relubrication.(And then show it by doing a grease injection test). | 1 | job | 90000 | 40000 | 90000 | 40000
5 | Water proof light inside AHU 40 watt | 2 | Nos | 5000 | 2000 | 10000 | 4000
6 | Replacement of evaporator drain tray & coil bottom & base Stainless Steel channel. | 1 | job | 30000 | 25000 | 30000 | 25000
7 | Coil descaling internal and external service | 1 | job | 20000 | 20000 | 20000 | 20000
8 | blower louvre epoxy paint with primer & hoiusing inside or outside | 1 | job | 25000 | 15000 | 25000 | 15000
9 | sound proof alluminium foil face EPDM foam insolation replacement inside.& complete inside alluminium cladding . | 1 | job | 224000 | 54000 | 224000 | 54000
10 | supply canvas duct connector inside/ AHU room replace fire proof insulation with anti fungus paint with another paint | 250 | sq/ft | 160 | 80 | 40000 | 20000
11 | Complete AHU paint outside & AHU room oil base mate finish NIPPON paint. | 1 | job | 85000 | 35000 | 85000 | 35000
12 | gate valves,globe valve,moterized valve & strainer descalling of chilled water line | 1 | job | 25000 | 20000 | 25000 | 20000
13 | Pressure gauge 0.2-100 PSIG made in USA fix with pipe nipple and socket,gauge cock siphon | 1 | job | 20000 | 3000 | 20000 | 3000
14 | Chilled water line supply & return aslo anti fungus paint & another paint with EPS thermocol insulation. | 1 | job | 15000 | 10000 | 15000 | 10000
15 | AHU belt replacement make continental | 1 | job | 20000 | 2000 | 20000 | 2000
16 | water balancing | 1 | job | 0 | 10000 | 0 | 10000
17 | supply & installation of complete filter frame & alluminium air filter | 1 | job | 160000 | 20000 | 160000 | 20000
18 | Miscellanous work | 1 | job | 15000 | 10000 | 15000 | 10000
19 | door hinges & lock | 1 | job | 5000 | 2000 | 5000 | 2000
20 | Drain pipe STEELEX UPVC SCH40 with fitting size 1.5'' | 50 | rft/ft | 550 | 200 | 27500 | 10000
21 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 35000 | 5000 | 35000 | 5000
Sub Total Amount Rs | [5 empty] | 926500 | 342000

## Sheet2
BOQ OF REPAIRING AND REPLACEMENT AND MAINTENANCE WORKS OF CHILLERS AND COOLING TOWERS OVERHAULING OF BA BUILDING KARACHI
S.NO | DESCRIPTION | Qty | Unit | Material Rate | Labour Rate | Material Amount | Labour Amount
ROOF TOP PLANT ROOM (CHILLERS)
1 | Shell cooler evaporator & condenssor shell descaling required | 9 | Nos | 30000 | 20000 | 270000 | 180000
2 | Shell cooler old insulation removing and rust removing with flenge pipe coupler inlet outlet with epoxy primer and paint required & new EPDM aero flex pasting work. | 3 | Nos | 85000 | 45000 | 255000 | 135000
3 | Chiller Compressors Oil Analyses required. Labortery tested reports share, if required Compressors oil change/fill . | 6 | Nos | 0 | 10000 | 0 | 60000
4 | Chiller foundation & compreessor foundation & heat exchanger rust removing and new epoxy paint apply. | 6 | Nos | 15000 | 10000 | 90000 | 60000
5 | Heat Exchanger inlet/outlet gate valve 6" old valve removing and new valve installation make HATTERSLEY with flenges. | 12 | Nos | 165000 | 5000 | 1980000 | 60000
6 | Condenssor pump Non-Return Valves 8" old valve removing and new valve installation make HATTERSLEY with flenges. | 4 | Nos | 190000 | 6000 | 760000 | 24000
7 | Chilled water & condenssor water lines gate valves 8" descalling required. | 7 | Nos | 10000 | 10000 | 70000 | 70000
8 | Primary , Secondary & Condenssor pumps with foundation repairing rust removing & epoxy paint with primer required . | 10 | Nos | 10000 | 10000 | 100000 | 100000
9 | Automatic Air Vent Brass 1" make HATTERSLEY with fittings of chilled water lines. | 4 | Nos | 5000 | 1000 | 20000 | 4000
10 | New Booster tank required. | 1 | Nos | 665000 | 15000 | 665000 | 15000
11 | Plant room cieling external side reapairing fiber material & internal side cieling repairing jumboloan. | 1 | job | 90000 | 30000 | 90000 | 30000
12 | Plant room internal side walls and beam girders,colum girders & M/S pipe enamel paint required. | 1 | job | 50000 | 40000 | 50000 | 40000
13 | Provide & installation gate valve 8'' dia Hattersley make. & With EPS thermocol insulation,fabric,anti fungus paint with almunium cladding. | 2 | Nos | 245000 | 8000 | 490000 | 16000
14 | fifth floor rooftop main chilled water line riser to plant room supply & return EPS thermocol insulation,fabric,anti fungus paint with almunium cladding/foundation stand clamp with epoxy paint | 400 | Rft | 2150 | 400 | 860000 | 160000
15 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 20000 | 10000 | 20000 | 10000
16 | Main Washrooms Exhausts Removal of existing ducts from riser and shafts / supply and installation of new G.I sheet metal ducts complete in all respect / supply & installation of hangers and supports with epoxy paint | 1500 | Sq/ft | 350 | 80 | 525000 | 120000
Sub Total Amount Rs | [5 empty] | 6245000 | 1084000
[6 empty] | 0 | 0
| 5TH FLOOR ELEVATOR & BMS ROOM FAN COIL UNITS 04 NOS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1 | Evaporator Coil descaling internal and external with epoxy paint. | 1 | Job | 10000 | 10000 | 10000 | 10000
2 | supply & installation of alluminium air filter | 1 | Job | 10000 | 10000 | 10000 | 10000
3 | Replacement of motor bearing, Make SKF & FAG | 1 | Job | 10000 | 8000 | 10000 | 8000
4 | Chilled water line supply & return aslo anti fungus paint & another paint with EPS thermocol insulation. | 1 | Job | 15000 | 8000 | 15000 | 8000
5 | gate valve make hartsley 6" provide & installation. | 6 | Nos | 8000 | 1000 | 48000 | 6000
6 | supply & installation of complete filter frame,bag filter & alluminium air filter for Fresh Air Unit | 1 | job | 27500 | 6000 | 27500 | 6000
8 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 20000 | 8000 | 20000 | 8000
Sub Total Amount Rs | [5 empty] | 140500 | 56000
ROOF TOP (COOLING TOWERS )
1 | Complete metal structure frame and other metal accessories & sand blasting with high quality zinc hot deep galvanizing required. | 6 | nos | 100000 | 80000 | 600000 | 480000
2 | Motor with gear box complete overhauling without winding,make SKF & FAG with grease niple for relubrication.(And then show it by doing a grease injection test). | 6 | nos | 65000 | 25000 | 390000 | 150000
3 | New Fan blade,New hub with alligment & balancing required. | 6 | nos | 65000 | 10000 | 390000 | 60000
4 | Upper hot water distribution basin with new showering box fiber material need & lower cool basin & fan stack frame & metal fan guard replaced with hot deep galvanizing & inspection door & fiber material minor repairing required. | 12 | Job | 12000 | 5000 | 144000 | 60000
5 | Complete new fills with new fills foundation fiber metarial f & louvers required | 6 | nos | 715000 | 50000 | 4290000 | 300000
6 | Hydroplast showering pipe fittings joints leakege repairing & butterfly valve 4" replaced with flenge & main showering hyder flenge 8" replaced | 12 | nos | 17000 | 4000 | 204000 | 48000
7 | float ball valve stainless steel 1.5" need to be change. | 3 | nos | 27000 | 3000 | 81000 | 9000
8 | Gate valve brass 2" need to be change make HATTERSLEY. | 9 | nos | 12000 | 1500 | 108000 | 13500
9 | Schneider Motorized valve 8" Outlet side need to be change. | 3 | nos | 350000 | 6000 | 1050000 | 18000
10 | Schneider Motorized valve 6" Inlet side need to be change. | 3 | nos | 265000 | 4000 | 795000 | 12000
11 | Cooling tower outside area walk way platform and complete m/s pipe with pipe foundation need to be epoxy paint with primer required. | 1 | job | 90000 | 60000 | 90000 | 60000
12 | electrical wires proper dress up upvc pipe fitting. | 1 | job | 30000 | 10000 | 30000 | 10000
13 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 100000 | 20000 | 100000 | 20000
Sub Total Amount Rs | [5 empty] | 8272000 | 1240500

## Summary
Bank Al-Falah Head Office Karachi
Overhauling, Repairing & Replacement |  |  |  | 2022-10-07
of Air Handling Units
SUMMARY OF BOQ
S.No | Description | Material Amount | Labour Amount | Total Amount
i | 4th FLOOR A/B AHU UNIT | 946500 | 345000 | 1291500
ii | MEZZAINE B FLOOR AHU UNIT | 721600 | 311000 | 1032600
iii | GROUND A FLOOR AHU UNIT | 926500 | 342000 | 1268500
iv | ROOF TOP PLANT ROOM (CHILLERS) | 6245000 | 1084000 | 7329000
v | 5TH FLOOR ELEVATOR & BMS ROOM FAN COIL UNITS 04 NOS | 140500 | 56000 | 196500
vi | ROOF TOP (COOLING TOWERS | 8272000 | 1240500 | 9512500
| Sub Total Amount | 17252100 | 3378500 | 20630600
| SST 13% on labour | 0 | 439205 | 439205
| Grand Total | 17252100 | 3817705 | 21069805