## SUMMARY
IMITAZ SUPERMARKET KORANGI KARACHI
SUMMARY OF COST
S.No | Activity. | AMOUNT
A | HVAC WORKS | 9687950
B | PLUMBING WORKS | 1335200
C | FIRE FIGHTING WORK | 3142300
| TOTAL RS. | 14165450
| Discount 11.757% | 1665431.9565
| Total After Discount | 12500018.0435
| SST @ 15% | 1875002.7065
Total Cost of Work |  | 14375020.75

## HVAC
Bill Of Quantities
ACMV Works
Imtiaz Supermarket | [8 empty] | Rev.00
Korangi | [8 empty] | Date: 23-09-2024
[5 empty] | Material |  | Labour |  | Total
S.No. |  | Description | Unit | Qty | Rate | Amount | Rate | Amount | Amount Rs.
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of consultant
1 |  | Installation, testing & commissioning of electric screw chiller, complete in all respects, ready to operate with supply and fixing of all accessories including interconnecting wiring, control wiring, power wiring (terminal connection), pipe inlet outlet connections, etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 1.1 | CH - 01 | Nos. | 2 |  | 0 | 50000 | 100000 | 100000
2 |  | Installation, testing & commissioning of cooling tower complete in all respects, ready to operate with supply and fixing of all accessories including interconnecting wiring, control wiring, power wiring (terminal connection), pipes inlet outlet connections etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 2.1 | CT - 01 | Nos. | 2 |  | 0 | 200000 | 400000 | 400000
3 |  | Unloading, rigging, lifting, installation, testing and commissioning of air handling units of different capacities complete in all respects, ready to operate with supply and fixing of all accessories, including hanger steel base, vibration isolators, including interconnecting power & control wiring (terminal connection) with inlet & outlet chilled water connections, drain connection, flexible rubber duct connection / connector etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 3.1 | AHU-01 | Nos. | 7 |  | 0 | 35000 | 245000 | 245000
| 3.2 | FAHU-01 | Nos. | 6 |  | 0 | 25000 | 150000 | 150000
4 |  | Unloading, rigging, lifting, installation, testing and commissioning of fan coil units (FCUs & DFCUs) of different capacities complete in all respects, ready to operate with supply and fixing of all accessories, including hanger steel base, vibration isolators, including interconnecting power & control wiring ( (terminal connection) with inlet & outlet chilled water connections, drain connection, flexible rubber duct connection / connector etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 4.1 | CSU-01 | Nos. | 5 |  | 0 | 8000 | 40000 | 40000
| 4.2 | CSU-02 | Nos. | 4 |  | 0 | 8000 | 32000 | 32000
| 4.3 | CSU-03 | Nos. | 4 |  | 0 | 8000 | 32000 | 32000
| 4.4 | DFCU-01 | Nos. | 8 |  | 0 | 8000 | 64000 | 64000
| 4.5 | DFCU-02 | Nos. | 57 |  | 0 | 8000 | 456000 | 456000
| 4.6 | DFCU-03 | Nos. | 3 |  | 0 | 8000 | 24000 | 24000
5 |  | Supply & installation of valves & accessories of chillers with supports, hangers, flanges, gas kits, nut & bolts etc. complete in all respects as per specifications, drawings and as per instructions of consultant.
| 5.1 | Butterfly Valve (Gear Operated)
| i. | 6" dia | Nos. | 4 |  | 0 | 6000 | 24000 | 24000
| ii. | 8" dia | Nos. | 4 |  | 0 | 8000 | 32000 | 32000
| 5.2 | Flexible Connectors
| i. | 6" dia | Nos. | 4 |  | 0 | 5000 | 20000 | 20000
| ii. | 8" dia | Nos. | 4 |  | 0 | 6000 | 24000 | 24000
| 5.3 | Check Valve
| i. | 6" dia | Nos. | 2 |  | 0 | 6000 | 12000 | 12000
| ii. | 8" dia | Nos. | 2 |  | 0 | 8000 | 16000 | 16000
| 5.4 | Balancing Valve (with self sealing measuring nipples)
| i. | 6" dia | Nos. | 2 |  | 0 | 6000 | 12000 | 12000
| ii. | 8" dia | Nos. | 2 |  | 0 | 8000 | 16000 | 16000
| 5.5 | 2-Way Motorized Butterfly Valve with Actuator & controls
| i. | 6" dia | Nos. | 2 |  | 0 | 6000 | 12000 | 12000
| ii. | 8" dia | Nos. | 2 |  | 0 | 8000 | 16000 | 16000
| 5.6 | Thermometer 12" Height Scale Type (with Thermo well) 0 ºC to 60 ºC | Nos. | 8 |  | 0 | 1500 | 12000 | 12000
| 5.7 | Pressure Gauge with Ball Valve & Siphon, Liquid filled Dial type range 0 psi to 100 psi. (4" dial Size) | Nos. | 8 |  | 0 | 1500 | 12000 | 12000
| 5.8 | Air Vent with Ball Valve | Nos. | 2 |  | 0 | 1000 | 2000 | 2000
| 5.9 | Flow Switch | Nos. | 4 |  | 0 | 2000 | 8000 | 8000
6 |  | Supply & installation of valves & accessories of cooling towers with supports, hangers, flanges, gas kits, nut & bolts etc. complete in all respects as per specifications, drawings and as per instructions of consultant.
| 6.1 | Butterfly Valve (Gear Operated)
| i. | 4" dia | Nos. | Rate only |  |  | 4000
| ii. | 5" dia | Nos. | Rate only |  |  | 6000
| iii. | 6" dia | Nos. | 12 |  | 0 | 6000 | 72000 | 72000
| iv. | 8" dia | Nos. | 2 |  | 0 | 8000 | 16000 | 16000
| 6.2 | 2-Way Motorized Butterfly Valve with Actuator & controls
| i. | 8" dia | No. | 1 |  | 0 | 8000 | 8000 | 8000
| 6.3 | Air Vent with Ball Valve | Nos. | 2 |  | 0 | 1000 | 2000 | 2000
| 6.4 | Ball Valve
| i. | 1.25" dia (Make up) | Nos. | 4 |  | 0 | 1500 | 6000 | 6000
| ii. | 1.5" dia | Nos. | Rate only |  |  | 1500
| iii. | 2" dia (Quick Fill & Overflow / Drain) | Nos. | 8 |  | 0 | 2000 | 16000 | 16000
7 |  | Supply & installation of valves & accessories for AHUs, complete in all respects as per specifications, drawings and as per instructions of consultant.
| 7.1 | Ball Valve
| i. | 1.5" dia | Nos. | 52 |  | 0 | 1500 | 78000 | 78000
| ii. | 2" dia | Nos. | Rate only |  |  | 2000
| 7.2 | Strainers
| i. | 1.5" dia | Nos. | 13 |  | 0 | 1500 | 19500 | 19500
| ii. | 2" dia | Nos. | Rate only |  |  | 2000
| 7.3 | Balancing Valve (with self sealing measuring nipples)
| i. | 1.5" dia | Nos. | 13 |  | 0 | 1500 | 19500 | 19500
| ii. | 2" dia | Nos. | Rate only |  |  | 2000
| 7.4 | Thermometer 6" Height Scale Type (with Thermo well) 0 ºC to 60 ºC | Nos. | 26 |  | 0 | 1500 | 39000 | 39000
| 7.5 | Pressure Gauge with Ball Valve & Siphon, Liquid filled Dial type range 0 psi to 100 psi. (4" dial Size) | Nos. | 26 |  | 0 | 1000 | 26000 | 26000
| 7.6 | 2-Way Motorized Valve with Actuator (0-100% modulating)
| i. | 1.25" dia | Nos. | 13 |  | 0 | 1500 | 19500 | 19500
| ii. | 1.5" dia | Nos. | Rate only |  |  | 1500
| 7.7 | Digital Decorative Thermostat Controller (BMS Interfacable) with Duct Mounted Sensor | Nos. | 13 |  | 0 | 1500 | 19500 | 19500
| 6.9 | Fan Control Panel with incoming Ckt. Breaker, DOL starter for upto 5.5 kW and auto S/D Starter for above 5.5 kW with protections and safeties | Nos. | 13 |  | 0 | 5000 | 65000 | 65000
| 6.91 | Control wiring from controller to sensors, motorized valve and Power wiring from FCP to fan, up to 15' radius | Jobs | 13 |  | 0 | 7500 | 97500 | 97500
8 |  | Supply & installation of valves & accessories for DFCUs, complete in all respects as per specifications, drawings and as per instructions of consultant.
| 8.1 | Ball Valve
| i. | 1" dia | Nos. | 324 |  | 0 | 1000 | 324000 | 324000
| ii. | 1.25" dia | Nos. | Rate only |  |  | 1500
| 8.2 | Strainers
| i. | 1" dia | Nos. | 81 |  | 0 | 1000 | 81000 | 81000
| ii. | 1.25" dia | Nos. | Rate only |  |  | 1500
| 8.3 | Balancing Valve (with self sealing measuring nipples)
| i. | 1" dia | Nos. | 81 |  | 0 | 1000 | 81000 | 81000
| ii. | 1.25" dia | Nos. | Rate only |  |  | 1500
| 8.4 | Thermometer 6" Height Scale Type (with Thermo well) 0 ºC to 60 ºC | Nos. | Rate Only |  |  | 1500
| 8.5 | Pressure Gauge with Ball Valve & Siphon, Liquid filled Dial type range 0 psi to 100 psi. (4" dial Size) | Nos. | Rate Only |  |  | 1000
| 8.6 | 2-Way Motorized Valve with Actuator (0-100% modulating)
| i. | 1" dia | Nos. | 81 |  | 0 | 1000 | 81000 | 81000
| 8.7 | Digital Decorative Thermostat Controller (BMS Interfacable) with Duct Mounted Sensor | Nos. | 81 |  | 0 | 1000 | 81000 | 81000
| 8.8 | Control wiring from controller to sensors, motorized valve and Power wiring up to 15' radius | Jobs | 81 |  | 0 | 5000 | 405000 | 405000
9 |  | Supply & installation of valves & accessories for chilled water riser circuit with supports, hangers, flanges, gas kits, nut & bolts where it required, etc. complete in all respects as per specifications, drawings and as per instructions of consultant.
| 9.1 | Butterfly Valve (Lever Type)
| i. | 2.5" dia | Nos. | 4 |  | 0 | 2500 | 10000 | 10000
| 9.2 | Butterfly Valve (Gear Operated)
| ii. | 4" dia | Nos. | 16 |  | 0 | 3000 | 48000 | 48000
| 9.3 | Balancing Valve (with self sealing measuring nipples)
| i. | 2.5" dia | No. | 1 |  | 0 | 2500 | 2500 | 2500
| ii. | 4" dia | Nos. | 3 |  | 0 | 3000 | 9000 | 9000
| 9.4 | Strainers
| i. | 2.5" dia | No. | 1 |  | 0 | 2500 | 2500 | 2500
| ii. | 4" dia | Nos. | 3 |  | 0 | 3000 | 9000 | 9000
| 9.5 | Check Valve
| i. | 2.5" dia | No. | 1 |  | 0 | 2500 | 2500 | 2500
| ii. | 4" dia | Nos. | 3 |  | 0 | 3000 | 9000 | 9000
| 9.6 | Ball Valve for Drainage
| i. | 1.25" dia | Nos. | 2 |  | 0 | 1000 | 2000 | 2000
| ii. | 2" dia | Nos. | 6 |  | 0 | 1500 | 9000 | 9000
| 9.7 | Air vent with Ball Valve | Nos. | 4 |  | 0 | 1000 | 4000 | 4000
| 9.8 | Thermometer 6" Height Scale Type (with Thermo well) 0 ºC to 60 ºC | Nos. | 8 |  | 0 | 1000 | 8000 | 8000
| 9.9 | Pressure Gauge with Ball Valve & Siphon, Liquid filled Dial type range 0 psi to 100 psi. (4" dial Size) | Nos. | 8 |  | 0 | 1000 | 8000 | 8000
10 |  | Unloading, rigging, lifting, installation, testing and commissioning of water circulation pumps of different capacities including R.C.C. base (provided by client), making of Inertia Block (by ACMV Contractor), fixing of industrial grade spring vibration isolators (supplied with pumps), interconnecting wiring, control wiring, power wiring (terminal connection), inlet & outlet pipe connections, drain connection etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of Consultant.
| 10.1 | CHP- 01 | Nos. | 3 |  | 0 | 50000 | 150000 | 150000
| 10.2 | CWP- 01 | Nos. | 3 |  | 0 | 40000 | 120000 | 120000
11 |  | Supply & installation of valves & accessories for pumps with supports, hangers, flanges, gas kits, nut & bolts where it required, etc. complete in all respects as per specifications, drawings and as per instructions of consultant.
| 11.1 | Flexible rubber connectors
| a) | Single Bellow
| i. | 6" dia | Nos. | 3 |  | 0 | 3000 | 9000 | 9000
| ii. | 8" dia | Nos. | 3 |  | 0 | 5000 | 15000 | 15000
| b) | Double Bellow
| i. | 6" dia | Nos. | 3 |  | 0 | 3000 | 9000 | 9000
| ii. | 8" dia | Nos. | 3 |  | 0 | 5000 | 15000 | 15000
| 11.2 | Butterfly Valve (Gear Operated)
| i. | 6" dia | Nos. | 6 |  | 0 | 4000 | 24000 | 24000
| ii. | 8" dia | Nos. | 6 |  | 0 | 5000 | 30000 | 30000
| 11.3 | Check Valve
| i. | 6" dia | Nos. | 3 |  | 0 | 4000 | 12000 | 12000
| ii. | 8" dia | Nos. | 3 |  | 0 | 5000 | 15000 | 15000
| 11.4 | Automatic Air Vent with Ball valve | Nos. | 2 |  | 0 | 1000 | 2000 | 2000
| 11.5 | Compound Pressure Gauge with Ball Valves, Liquid filled Dial type
| i. | Range -ve 5 psi to 100 psi. | Nos. | 6 |  | 0 | 1000 | 6000 | 6000
| ii. | Range 0 psi to 100 psi. | Nos. | 6 |  | 0 | 1000 | 6000 | 6000
12 |  | Supply, installation, testing and commissioning of Variable Frequency Drive (VFD) for Pumps with controls & control wiring complete in all respects as per specifications, drawings and as per instructions of consultant.
| 12.1 | VFD-01 (for CHP-01) | Nos. | 3 |  | 0 | 10000 | 30000 | 30000
13 |  | Supply & installation of SCH-40 M.S.(As per ASME & API standard, Heavy Quality with standard SCH 40 wall thickness) pipes & fitting for water circulation system complete with bends, tees, unions, sockets, specials, MS Pipe support, hangers & anchors, M.S. angle, U channel, roller support, bolts, rods, clamps, concrete fasteners etc as required to complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
| A | Cooling Water
| 13.1 | 4" dia | Rft | Rate only |  |  | 400
| 13.2 | 5" dia | Rft | Rate only |  |  | 500
| 13.3 | 6" dia | Rft | 90 |  | 0 | 600 | 54000 | 54000
| 13.4 | 8" dia | Rft | 80 |  | 0 | 700 | 56000 | 56000
| 13.5 | 10" Dia | Rft | 250 |  | 0 | 800 | 200000 | 200000
| 13.6 | 12" Dia | Rft | Rate only |  |  | 1000
| B | Chilled Water
| 13.5 | 1" dia | Rft | 1830 |  | 0 | 180 | 329400 | 329400
| 13.6 | 1.25" dia | Rft | 340 |  | 0 | 200 | 68000 | 68000
| 13.7 | 1.5" dia | Rft | 330 |  | 0 | 225 | 74250 | 74250
| 13.8 | 2" dia | Rft | 360 |  | 0 | 250 | 90000 | 90000
| 13.9 | 2.5" dia | Rft | 850 |  | 0 | 300 | 255000 | 255000
| 13.1 | 3" dia | Rft | 410 |  | 0 | 325 | 133250 | 133250
| 13.11 | 4" dia | Rft | 130 |  | 0 | 400 | 52000 | 52000
| 13.12 | 5" dia | Rft | 70 |  | 0 | 500 | 35000 | 35000
| 13.13 | 6" dia | Rft | 135 |  | 0 | 600 | 81000 | 81000
| 13.14 | 8" Dia | Rft | 285 |  | 0 | 700 | 199500 | 199500
| 13.15 | 10" Dia | Rft | Rate only |  |  | 800
| 13.16 | 12" Dia | Rft | Rate only |  |  | 1000
14 |  | Supply, Installation of Pre Formed Polystyrene (Thermopore) insulation (32 kg/m3 density) for internal chilled water pipes, bends, tees, unions, sockets, valves and on specials protected with Kraft paper, wrapped with 8oz Canvas cloth than paint with Anti fungus paint complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of Consultant.
Chilled Water internal area
| 14.1 | 1" dia | Rft | 1830 |  | 0 | 60 | 109800 | 109800
| 14.2 | 1.25" dia | Rft | 340 |  | 0 | 70 | 23800 | 23800
| 14.3 | 1.5" dia | Rft | 330 |  | 0 | 80 | 26400 | 26400
| 14.4 | 2" dia | Rft | 360 |  | 0 | 100 | 36000 | 36000
| 14.5 | 2.5" dia | Rft | 850 |  | 0 | 125 | 106250 | 106250
| 14.6 | 3" dia | Rft | 410 |  | 0 | 150 | 61500 | 61500
| 14.7 | 4" dia | Rft | 100 |  | 0 | 175 | 17500 | 17500
| 14.8 | 5" dia | Rft | 70 |  | 0 | 200 | 14000 | 14000
| 14.9 | 6" dia | Rft | Rate only |  |  | 250
| 14.1 | 8" Dia | Rft | Rate only |  |  | 275
| 14.11 | 10" Dia | Rft | Rate only |  |  | 280
| 14.12 | 12" Dia | Rft | Rate only |  |  | 300
15 |  | Supply & installation of Pre Formed Polyurethane (Bituminous Kraft Paper Facing) (50 kg/m3 density) for chilled water pipes exposed to weather area with fittings, bends, tees, unions, sockets, valves & accessories and on specials complete in all respects as per schedule, specification, drawings and as per instruction of Consultant.
Chilled Water exposed to weather area & plantroom
| 15.1 | 4" dia | Rft | 30 |  | 0 | 175 | 5250 | 5250
| 15.2 | 5" dia | Rft | Rate only |  |  | 200
| 15.3 | 6" dia | Rft | 135 |  | 0 | 250 | 33750 | 33750
| 15.4 | 8" Dia | Rft | 285 |  | 0 | 300 | 85500 | 85500
| 15.5 | 10" Dia | Rft | Rate only |  |  | 325
| 15.6 | 12" Dia | Rft | Rate only |  |  | 350
16 |  | Supply, fabrication and installation of 26 (SWG) gauge G.I cladding over chilled water pipes insulation complete in all respects ready to operate as per specification, drawings and as per instruction of consultant.
| 16.1 | 4" dia | Rft | 30 |  | 0 | 150 | 4500 | 4500
| 16.2 | 5" dia | Rft | Rate only |  |  | 180
| 16.3 | 6" dia | Rft | 135 |  | 0 | 200 | 27000 | 27000
| 16.4 | 8" Dia | Rft | 285 |  | 0 | 250 | 71250 | 71250
| 16.5 | 10" Dia | Rft | Rate only |  |  | 290
| 16.6 | 12" Dia | Rft | Rate only |  |  | 335
17 |  | Supply & installation single split air conditioning units decorative type (inverter) of different capacities, including supply & installation of supports, brackets, rubber isolator, flashing, power wiring (upto 15 ft + connection), complete in all respects ready to operate as per drawings, specification & as per instruction of consultant.
| 17.1 | GF-AC-01 | Nos. | 2 |  | 0 | 5000 | 10000 | 10000
| 17.2 | 1F-AC-01 | Nos. | 1 |  | 0 | 5000 | 5000 | 5000
| 17.3 | 2F-AC-02 | Nos. | 1 |  | 0 | 5000 | 5000 | 5000
| 17.4 | 4F-AC-01 | Nos. | 2 |  | 0 | 5000 | 10000 | 10000
| 17.5 | 4F-AC-02 | Nos. | 1 |  | 0 | 5000 | 5000 | 5000
| 17.6 | 5F-AC-02 | Nos. | 1 |  | 0 | 5000 | 5000 | 5000
18 |  | Supply & installation of refrigerant pipes (liquid + gas) with 1/2" thick expended rubber foam insulation, PVC tape wrapping + control wiring in G.I. for external / PVC for internal from outdoor unit to indoor unit, including gas charging if required complete in all respects ready to operate as per drawings, specification & as per instruction of consultant.
| 18.1 | GF-AC-01 | Rft | 100 |  | 0 |  | 0 | 0
| 18.2 | 1F-AC-01 | Rft | 85 |  | 0 | 300 | 25500 | 25500
| 18.3 | 2F-AC-02 | Rft | 70 |  | 0 | 300 | 21000 | 21000
| 18.4 | 4F-AC-01 | Rft | 65 |  | 0 | 300 | 19500 | 19500
| 18.5 | 4F-AC-02 | Rft | 25 |  | 0 | 300 | 7500 | 7500
| 18.6 | 5F-AC-02 | Rft | 10 |  | 0 | 300 | 3000 | 3000
19 |  | Supply & installation of 18 SWG powder quoted G.I. sheet metal tray with cover for refrigerant pipes and control wiring exposed to weather area etc, complete in all respects including hangers, supports brackets complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqft | 200 |  | 0 | 80 | 16000 | 16000
20 |  | Supply & installation of air curtains including, supports, electrical connection etc, complete in all respects ready to operate as per drawings, specification & as per instruction of consultant.
| 20.1 | 3 Feet Length | Nos. | 3 |  | 0 | 1000 | 3000 | 3000
| 20.2 | 4 Feet Length | No. | 1 |  | 0 | 1000 | 1000 | 1000
21 |  | Unloading, rigging, lifting, placement, installation, testing and commissioning of Ventilation & Smoke Extraction Fans as per mentioned in schedule, including supply & installation of vibration isolator, power wiring from isolation box to unit (10' to 15' radius), flexible duct connection / connector, support & hangers complete in all respects ready to operate as per drawings, specification and as per instruction of consultant.
| 21.1 | GF-K-EAF-01 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.2 | GF-K-EAF-02 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.3 | GF-EAF-01 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.4 | GF-EAF-02 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.5 | GF-FAF-01 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.6 | GF-FAF-02 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.7 | 4F-EAF-01 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.8 | 4F-EAF-02 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.9 | 4F-EAF-03 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.1 | 4F-FAF-01 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.11 | 5F-EAF-01 | Nos. | 2 |  | 0 | 5000 | 10000 | 10000
| 21.12 | BF-SEF-01 | Nos. | 2 |  | 0 | 5000 | 10000 | 10000
| 21.13 | BF-SEF-02 | No. | 1 |  | 0 | 5000 | 5000 | 5000
| 21.14 | GF-SEF-01 | Nos. | 2 |  | 0 | 5000 | 10000 | 10000
| 21.15 | 1F-SEF-01 | Nos. | 4 |  | 0 | 5000 | 20000 | 20000
| 21.16 | 4F-SEF-01 | Nos. | 2 |  | 0 | 5000 | 10000 | 10000
22 |  | Supply, fabrication and installation of M.S sheet metal welded duct of 2.0 mm (16 Gauge) thickness for kitchen exhasut duct, complete in all respects including 300x150 access doors at all changes in direction, transformation, plenums chambers, connection pecs of hood round to square, supports & hangers etc. complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant.. | Sqft | 1600 |  | 0 | 80 | 128000 | 128000
23 |  | Supply, fabrication and installation of 2" thick rockwool (double layar) insulation of 50kg/m3 density with wire mesh reinforcement over M.S sheet metal ducts of kitchen exhaust air, complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Sqft | 1750 |  | 0 | 60 | 105000 | 105000
24 |  | Supply, Fabrication and installation of 26 SWG gauge G.I. cladding for over rockwool insulation etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Sqft | 1750 |  | 0 | 80 | 140000 | 140000
25 |  | Supply, fabrication and installation of pre-insulated ductwork of polyurethane foam panel with 52 Kg/m3 density, 20 mm thickness, coated on both sides with 80 micron thick aluminum foil complete with a 2 g/m2 layer for internal duct work including manufacturer's aluminum hardware glue, Hot Dipped galvanized hangers and supports, flexible duct connection, wooden frame, etc. Complete in all respects ready to operate as per drawings, specification and as per instruction of consultant. | Sqft | 21500 |  | 0 |  | 0 | 0
26 |  | Supply, fabrication and installation of machine made G.I sheet metal duct for exposed to weather area ducts, complete in all respects including splitter dampers, guide vanes, flexible duct connection, access door, transformation, plenums chambers, anchors supports & hangers, wooden frame complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Sqft | 6400 |  | 0 | 60 | 384000 | 384000
27 |  | Supply and Installation of aluminum foil facing fiber glass (24 kg/m3 density) insulation 1" thick for G.I. sheet metal ducts of different sections with Aluminum tape protected with 8oz canvas cloth than painted anti fungus paint compete in all respect as per specifications, drawings and as per instructions of Consultant. (where it required) | Sqft | Rate only |  |  | 40
28 |  | Supply & installation of 2" thick Pre Formed Polyurethane insulation (Bituminous Kraft Paper Facing, 50 kg/m3 density for external / exposed to weather area ducts, supply, return, fresh air duct, complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Sqft | Rate only |  |  | 50
29 |  | Supply, Fabrication and installation of 26 SWG gauge G.I. cladding for external / exposed to weather area ducts (except exhaust air) etc. complete in all respects ready to operate as per drawings, specification, instruction of Consultant. | Sqft | Rate only |  |  | 80
30 |  | Supply & installation of rubberfoam acoustical duct sound liner adhesive with1/2" thick in supply air duct complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. For AHUs & FAHUs only | Sqft | 4000 |  | 0 | 40 | 160000 | 160000
31 |  | Supply & installation of aluminum fabricated powder coated fresh & exhaust Air louvers including wooden frame, rain protection sheet bird mesh etc complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqin | 26400 |  | 0 | 2 | 52800 | 52800
32 |  | Supply & installation of aluminum fabricated, powder coated grills, diffusers and registers etc for supply, return, exhaust & fresh air of different sizes (Grade A) wooden frame, supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant.
| 32.1 | Supply & Return Air Registers / Diffuser with Damper | Sqin | 57700 |  | 0 | 2 | 115400 | 115400
| 32.2 | Supply & Fresh Air Grills | Sqin | 12500 |  | 0 | 2 | 25000 | 25000
| 32.3 | Return Air Grills with Access Panels 24"x24" | Nos. | 6 |  | 0 | 1000 | 6000 | 6000
| 32.4 | S.S Wire Mesh with G.I Frame | Sqin | 1000 |  |  | 21 | 21000 | 21000
| 32.5 | Linear Slot 6,000 Series
| i. | 2 Slots of 3/4" | Rft | 5 |  | 0 | 500 | 2500 | 2500
| 32.5 | Exhaust air Disc Valves
| i. | 6" Dia | Nos. | 16 |  | 0 | 600 | 9600 | 9600
33 |  | Supply & installation of flexible duct including hangers, jubilee clamp complete in all respects as per specification, drawings & as per instruction of consultant.
| 33.1 | 6" dia | Rft | 5 |  | 0 | 100 | 500 | 500
34 |  | Supply & installation of butterfly damper for above flexible duct with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of consultant.
| 34.1 | 6" dia | Nos. | 1 |  | 0 | 1000 | 1000 | 1000
35 |  | Supply, fabrication & installation of pre-insulated Volume Control Damper, blades to be constructed with extruded aluminum in airfoil shape with thermal isolation gape & shall have seals, pvc / aluminum profiles duct connection at both end etc. complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Sqin | 5000 |  | 0 | 3 | 15000 | 15000
36 |  | Supply & installation of Fire Damper with linkage & fuse complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant. | Sqin | 2000 |  | 0 | 3 | 6000 | 6000
37 |  | Supply & installation of uPVC (Sch 40.) drain pipe insulated with 3/8" thick rubber foam insulation including clamps, bends, tees, drain plugs, sockets, protection treatment, PVC tape wrapping complete in all respects as per specifications, drawings & as per instructions of Consultant.
| 37.1 | 1" dia | Rft | 750 |  | 0 | 75 | 56250 | 56250
| 37.2 | 1.25" dia | Rft | 675 |  | 0 | 100 | 67500 | 67500
| 37.3 | 1.5" dia | Rft | 100 |  | 0 | 125 | 12500 | 12500
| 37.2 | 2" dia | Rft | 70 |  | 0 | 150 | 10500 | 10500
38 |  | Supply & installation of uPVC (Sch 80.) class 'D' pipe for cooling tower makeup, quick filling and drain from overhead tank and boosting pumps to cooling tower compete with ball valves, clamps, bends, tees, drain plugs, sockets, protection treatment including PVC tape wrapping complete in all respects ready to operate, as per drawings and as per instructions of consultant. | Lot | 1 |  | 0 | 50000 | 50000 | 50000
39 |  | Supply, installation, testing & commissioning of valve accessories for Decouple Connection to be installed as per site conditions complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant.
| 39.1 | Butterfly Valve (Gear Operated) |  |  |  | 0 |  | 0 | 0
| i. | 4" dia | Nos. | 3 |  | 0 | 5000 | 15000 | 15000
| 39.2 | 2-Way Motorized Valve with Actuator (0-100% Modulation)
| i. | 4" dia | No. | 1 |  | 0 | 10000 | 10000 | 10000
| 39.3 | Pressure Differential Switch | No. | 1 |  | 0 | 2000 | 2000 | 2000
40 |  | Supply, rigging, lifting, installation and testing of centrifugal sediment separator for Cooling water open circuit @ 40 micron, inlet / outlet as per drawing, including valves & accessories complete with all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Set | 1 |  | 0 | 50000 | 50000 | 50000
41 |  | Supply, Installation, testing, commissioning of By pass chemical feeder with inlet/outlet connections including valves & accessories, funnel for chemical feeding, initial chemicals for chilled water circuit complete in all respects ready to operate as per schedule, specifications, drawings and as per instructions of Consultant. | Set | 1 |  | 0 | 5000 | 5000 | 5000
42 |  | Supply, Installation, testing & commissioning of Chemical dozing plant including 2 Nos. automatic dozing pumps, Liquid Chemical tanks with level indicator, initial chemicals for cooling water circuit etc. complete in all respects ready to operate as per schedule, specifications, drawings and as per instructions of Consultant. | Set | 1 |  | 0 | 10000 | 10000 | 10000
43 |  | Chemical required for one year operation of chilled & cooling water circuit including Initial Flashing Dozing, Initial Dozing & maintaining dozing for one year plant operation as per instructions of Consultant. | Lot. | 1 |  | 0 | 0 | 0 | 0
44 |  | Supply, installation, testing and commissioning of boosting pump set one standby of required size and capacity with pressurized vertical type diaphragm tank, auto / manual operation control panel pre wired, power on/off breaker, including gate valve, check valve, float valve, pressure gauge etc complete in all respects ready to operate as per schedule, specifications, drawings and as per instructions of Consultant. | Set | 2 |  | 0 | 25000 | 50000 | 50000
45 |  | Supply, Installation, Testing and Commissioning of allied electrical works for ACMV Systems including Motor Control Centre, MCCs complete in all respects including weather proof sheet metal cabinet, bus bars, internal wiring, earth strip, connector strip, MCB, MCCB, Control fuses, magnetic connector, Overload relay, indication lights, voltmeter, ammeter, under voltage, phase reversible, phase failure device, selector switch, related civil works etc. complete in all respects as per schedule, specifications, drawings & as per instructions of Consultant.
| 45.1 | MCC for Plant Room Equipment | Lot | 1 |  | 0 | 100000 | 100000 | 100000
| 45.2 | MCC for Roof Equipment | Lot | 1 |  | 0 | 100000 | 100000 | 100000
46 |  | Supply, installation, testing and commissioning of interconnecting wiring, control wiring, power wiring from MCC, DB, panel to equipment (equipment as shown in SLD) with isolation switches near the equipment, including civil works related to complete wiring works etc. complete in all respects as per schedule, specifications, drawings & as per instructions of Consultant | Lot | 1 |  |  | 450000 | 450000 | 450000
47 |  | Supply, installation, testing and commissioning of perforated cable trays made with 1.63mm SWG (16 Guage) painted G.I Sheet, including hanger, bracket, proper bends, cover of trays shall be made with 1.22mm SWG (18 guage) painted G.I sheet, complete in all respects, ready to operate as per schedule, specification, drawings and as per instruction of Consultant. | Job | 1 |  |  | 300000 | 300000 | 300000
48 |  | Supply & Intallation of CO CONTROL PANEL, Multizone control panel capable of receiving input signal from the CO sensors and transmitting output signal to smoke extract fans etc, complete in all respects, ready to operate as per schedule, specification, drawings and as per instruction of Consultant. | Job | 1 |  |  | 90000 | 90000 | 90000
49 |  | Supply & Intallation of wall mounted CO Sensors, complete in all respects, ready to operate as per schedule, specification, drawings and as per instruction of Consultant. | Nos. | 6 |  | 0 | 2000 | 12000 | 12000
50 |  | Integration of smoke control system using I/O modules with the fire alarm control panel of building with fire resistant wiring & fixing accessories, complete in all respects, ready to operate as per drawings, specification and instruction of consultant. | Job. | 1 |  | 0 | 0 | 0 | 0
51 |  | Supply & installation of additional MS Pipe support, hangers & anchors for plant room & riser pipes including M.S. angle, U channel, Roller Support, bolts, rods, clamps, Concrete fasteners etc. complete in complete in all respects as per specification, drawings & as per instruction of Consultant. | Job. | 1 |  | 0 | 200000 | 200000 | 200000
52 |  | Painting & Identification work on chilled water pipes & exhaust duct, supports, hangers etc. complete in all respects with one coat of ICI make Red lead oxide primer & two coats of ICI make enamel paint as per instruction of Consultant. | Job. | 1 |  | 0 | 200000 | 200000 | 200000
53 |  | Testing, balancing and commissioning of water side of the system (from independent agency) complete in all respects including flow measurement & balancing, temp, pressure, electrical data of related equipment etc. as per specifications and as per instructions of Consultant. | Job. | 1 |  | 0 | 150000 | 150000 | 150000
54 |  | Testing, balancing and commissioning of air side of the system complete (from independent agency) in all respects including air measurement & balancing, temp, pressure & electrical data of related equipment etc. as per specifications and as per instructions of Consultant. | Job. | 1 |  | 0 | 150000 | 150000 | 150000
55 |  | Making of Shop drawings on Auto CAD latest version with section details and equipment foundation details, as per instruction of Consultant. | Job. | 1 |  | 0 | 20000 | 20000 | 20000
56 |  | Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment as per instruction of Consultant. | Job. | 1 |  | 0 | 20000 | 20000 | 20000
|  | Total Cost with income tax Rs. | [6 empty] | 9687950
Note: > The owner reserves the right to supply any or all materials for any item themselves. Therefore, please quote the labour rates accordingly. | [9 empty] | 14165450
> M.S platform & RCC foundation for placement for equipment will be owner scope.
> Kitchen Hoods supply & installation will be owner scope. | [9 empty] | 12500000 |  | WHT | 4.5%
> Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> Contractor is instructed to visit the site, understand the nature of work and then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work. | [9 empty] | 1665450
> Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works). | [9 empty] | 0.11757
This is reference of Telephonic discussion regarding labour work for the project Imtiaz Super market Korangi Karachi mutually agreed amount settled are as follows:
[10 empty] | Amount Done | 12500000
[10 empty] | SST 15% | 1875000 | 1500000
[10 empty] | Amount with SST | 14375000
[10 empty] | Less WHT 4.5% | 646875
[10 empty] | Net Amount | 13728125

## Plumbing
Bill of Quantities
Plumbing & Sanitary Services
Imtiaz Super Market | [8 empty] | Rev.00
Korangi, Karachi. | [8 empty] | Date: 23-09-2024
S.No. |  | Description | Unit | Qty | Material |  | Labour |  | Total
[5 empty] | Rate | Amount | Rate | Amount | Amount Rs.
SECTION - 01, PLUMBING FIXTURES
Supply and Installation of plumbing fixtures & faucets complete in all respects including all accessories, support, hangers, etc. ready to use as per specifications, drawings and instructions of Consultant.
1.1 |  | European style coupled water closet floor mounted with seat cover, flush tank C.P. (chrome plated) connector, thimble, etc.
| i. | Type - EWC | Nos. | 7 |  | 0 | 7000 | 49000 | 49000
1.2 |  | Asian style water closet Orissa type with flush tank C.P. (chrome plated) connector, uPVC Class "E" flush pipe, thimble, P-Trap, etc.
| i. | Type - AWC | Nos. | 4 |  | 0 | 6000 | 24000 | 24000
1.3 |  | Toilet Hand Spray with flexible chain & telephone type shower Including tee stop cock etc. complete in all respect.
| i. | Type - TS (for EWC) | Nos. | 7 |  | 0 | 1500 | 10500 | 10500
1.4 |  | Toilet Hand Spray with flexible chain & telephone type shower Including double bib cock etc. complete in all respect.
| i. | Type - TS (for AWC) | Nos. | 4 |  | 0 | 1000 | 4000 | 4000
1.5 |  | Wash basin (WB) including bottle trap, waste, stop cocks, etc.
| i. | Type - WB | No. | 1 |  | 0 | 5000 | 5000 | 5000
| ii. | Type - WB (Vanity) | Nos. | 8 |  | 0 | 5000 | 40000 | 40000
1.6 |  | Wash basin hot and cold water mixer, etc.
| i. | Type - WB | No. | 1 |  | 0 | 2000 | 2000 | 2000
| ii. | Type - WB (Vanity) | Nos. | 8 |  | 0 | 2000 | 16000 | 16000
1.7 |  | Stainless steel kitchen sink including stop cocks, P-trap / Bottle trap, waste pipe etc complete in all respects.
| i. | SK - 1, 34" x 20" single bowl and single drainer. | Nos. | 4 |  | 0 | 2000 | 8000 | 8000
| ii. | SK - 2, 46" x 20" double bowl and single drainer. | Nos. | 2 |  | 0 | 2000 | 4000 | 4000
1.8 |  | Sink hot and cold water mixer, etc.
| i. | SK - 1 | Nos. | 4 |  | 0 | 2000 | 8000 | 8000
| ii. | SK - 2 | Nos. | 2 |  | 0 | 2000 | 4000 | 4000
1.9 |  | S.S Grease Trap 7.5 Kg inlet/outlet connections 2" dia complete in all respects. | Nos. | 3 |  | 0 | 5000 | 15000 | 15000
1.1 |  | Toilet accessories complete set.
| i. | Soap Dispenser | Nos. | 5 |  | 0 | 500 | 2500 | 2500
| ii. | Towel Rail | Nos. | 5 |  | 0 | 500 | 2500 | 2500
| iii. | Paper Holder | Nos. | 7 |  | 0 | 500 | 3500 | 3500
| iv. | Coat Hooks | Nos. | 22 |  | 0 | 500 | 11000 | 11000
| v. | Hand Dryer | Nos. | 5 |  | 0 | 500 | 2500 | 2500
Sub Total Rs.
SECTION-02 WATER SUPPLY SYSTEM.
Supply, installation, testing and commissioning of complete pipe work for cold and hot water system including all accessories required to complete systems ready to operate as per specification, drawings & instruction of Consultant.
2.1 |  | Polypropylene Random PP-R pipes PN 20 and fittings with fusion jointing along with all types of unions, tees, bends, sockets, clamps, hangers, supports, sleeves, masking plates, chiseling, making holes making good, excavation, bedding backfilling as required complete in all respect.
| i. | Dia. OD 25 mm | Rft. | 700 |  | 0 | 100 | 70000 | 70000
| ii. | Dia. OD 40 mm | Rft. | 110 |  | 0 | 150 | 16500 | 16500
| iii. | Dia. OD 50 mm | Rft. | 70 |  | 0 | 160 | 11200 | 11200
| iv. | Dia. OD 63 mm | Rft. | 70 |  | 0 | 200 | 14000 | 14000
| v. | Dia. OD 75 mm | Rft. | 10 |  | 0 | 225 | 2250 | 2250
2.2 |  | Same as item # 2.1 but for hot water supply with Polypropylene Random PP-R (PN -25) with Aluminium foil.
| i. | Dia OD 25 mm | Rft. | 200 |  | 0 | 115 | 23000 | 23000
2.3 |  | Open cell rubber foam insulation 3/8" thick & pvc tape wrapping for hot water pipes.
| i. | Dia OD 25 mm | Rft. | 200 |  | 0 | 25 | 5000 | 5000
2.4 |  | uPVC Sch-80 pipe for water supply including specials fittings sockets tees, elbows, bends, reducers, clamps, hangers, plugs and unions etc supported on walls or suspended from roof slab, including protective as per drawing and specifications complete in all respects. (Filled & Supply)
| i. | Dia. 1-1/4" | Rft. | 190 |  | 0 | 75 | 14250 | 14250
| ii. | Dia. 2" | Rft. | 70 |  | 0 | 100 | 7000 | 7000
| iii. | Dia. 3" | Rft. | 140 |  | 0 | 150 | 21000 | 21000
2.5 |  | Brass body gate valves / ball valves with unions.
| i. | Size 3/4" | Nos. | 31 |  | 0 | 1000 | 31000 | 31000
| ii. | Size 1-1/4" | Nos. | 4 |  | 0 | 1000 | 4000 | 4000
| iii. | Size 1-1/2" | Nos. | 2 |  | 0 | 1500 | 3000 | 3000
| iv. | Size 2" | Nos. | 3 |  | 0 | 1500 | 4500 | 4500
| v. | Size 3" (CI boby with matching flanges nuts & bolts) | Nos. | 5 |  | 0 | 3000 | 15000 | 15000
2.6 |  | Brass body gate checkl valves with unions.
| i. | Size 2" | No. | 1 |  | 0 | 2000 | 2000 | 2000
| ii. | Size 3" (CI boby with matching flanges nuts & bolts) | No. | 1 |  | 0 | 3000 | 3000 | 3000
2.7 |  | Bib cock brass body for washing area.
| i. | Size 3/4" | Nos. | 2 |  | 0 | 1000 | 2000 | 2000
2.8 |  | Hot water storage heater (Electric) suitable for 30 psi working pressure including thermostat, inlet/outlet connection. Pressure relief valve.
| i. | HWE-50 (50 Litres Storage Capacity) | Nos. | 11 |  | 0 | 2000 | 22000 | 22000
2.9 |  | Pressure boosting pumps set with VFD, motors electrical panel including incoming, outgoing MCCBs, pressure transmeter, pumps starters, lead/lag relay, dry run protection, 100 litres diaphragm pressure tank, inter connecting pipe work, valves, mounted on common steel base, lnlet/outlet connection electrical power cable, foundation as per schedule. (1 duty & 1 standby)
| i. | PBP-01 @ 25 gpm 2.5 bar pressure cut-in & 3.5 cut-out. | Set | 1 |  | 0 | 25000 | 25000 | 25000
2.1 |  | Submersible bore water transfer pumps set ncluding float switch, water proof cable, ball valve, check valve with union, lifting chain. automatic control system for tank low and high level, auto stop with overflow, complete in all respects. (1 duty & 1 standby)
| i. | WTP-01 @ 85 gpm 100 feet head. | Set. | 1 |  | 0 | 2000 | 2000 | 2000
2.11 |  | Motor control electrical panel for Duplex (2 Nos.) submersible pumps including auto Lead/Lag sequencing of pumps, pump starters, auto on / off, float switches, high level alarm, power and control wiring, automatic for above mentioned pumps, control system for auto filling of water to fill the O/H tank, auto stop with overflow, dry run protection, Control wiring from panel to U/G & O/H tank in G.I conduits complete in all respects as per instruction of consultant. | Job. | 1 |  | 0 | 15000 | 15000 | 15000
Sub Total Rs.
SECTION-03 SOIL, WASTE VENT AND RAIN WATER DRAINAGE SYSTEM
Supply, fixing, testing and commissioning of equipment, pipe work required to complete the soil, waste, vent and rain water systems in all respects with accessories ready to operate as per specifications, drawings and instructions of Consultant.
3.1 |  | uPVC pipes of approved make along with specials, fittings, bends, wye, tees, sockets, flexible connectors, sleeves, masking plates, chiseling, making hole, excavation, backfilling making good where as required jointing with rubber ring seal.
| i. | Dia. 1-1/2" | Rft. | 200 |  | 0 | 100 | 20000 | 20000
| ii. | Dia. 2" | Rft. | 490 |  | 0 | 150 | 73500 | 73500
| iii. | Dia. 4" | Rft. | 1120 |  | 0 | 200 | 224000 | 224000
| iv. | Dia. 6" | Rft. | 60 |  | 0 | 250 | 15000 | 15000
| v. | Dia. 2" Class "D" (for sump pit discharge pipe) | Rft. | 70 |  | 0 | 150 | 10500 | 10500
3.2 |  | Floor trap including S.S grating floor trap, inlet outlet connection complete in all respects.
| i. | FT- with 4" P - trap | Nos. | 30 |  | 0 | 1000 | 30000 | 30000
3.3 |  | Cleanout for soil, waste pipes of approved make.
| i. | For 4" dia. Pipe with SS floor cover plate (FCO) | Nos. | 8 |  | 0 | 1000 | 8000 | 8000
3.4 |  | uPVC rain water grating of approved design with dome type grating including requisite number of holes in wall plinth or floor for pipe connection and making good the same as necessary to the structure complete including gasket and clamp complete.
| i. | RWG - 4" size | Nos. | 5 |  | 0 | 1500 | 7500 | 7500
3.5 |  | uPVC cowl for vent pipe of the following dia. including all accessories complete.
| i. | Size. 2" | Nos. | 3 |  | 0 | 500 | 1500 | 1500
| ii. | Size. 4" | Nos. | 3 |  | 0 | 500 | 1500 | 1500
| iii. | Size. 6" | No. | 1 |  | 0 | 500 | 500 | 500
Sub Total Rs.
SECTION-04 EXTERNAL SEWER & MANHOLES
Supply, fixing, testing and commissioning of equipment, pipe work required to complete the sewerage disposal services in all respects with accessories ready to operate as per specifications, drawings and instructions of Consultant.
4.1 |  | uPVC pipes class 'D' for Sewer drainage with push fit rubber joints including excavation in any type of soil, dewatering if required bedding, back filling with selected material, removing of extra materials.
| i. | Dia. 6" size | Rft. | 200 |  | 0 | 300 | 60000 | 60000
4.2 |  | Construction of Gully Trap with material including, excavation, 4" size uPVC P-trap CC base CI cover with frame, CC benching water proof internal plaster inlet/out connections etc.
| i. | Type GT, Size 10"x10" | Job. | 4 |  | 0 | 3000 | 12000 | 12000
4.3 |  | Construction of grating with material including, excavation, uPVC P-trap CC base MS grating with frame, CC benching water proof internal plaster inlet/out connections etc.
| i. | Size 8" wide | Rft. | 55 |  | 0 | 2000 | 110000 | 110000
4.4 |  | Construction of manholes with material including, excavation, base top RCC slab CI cover with frame, GI steps, CC benching water proof internal plaster inlet/out connections etc.
| i. | Size. 24" X 24" | Nos. | 6 |  | 0 | 15000 | 90000 | 90000
4.5 |  | Construction of sump pit tank with material including, excavation, base top slab bedding, GI steps, CI double covers, internal CC water proof plasters, uPVC tees, CC benching, inlet/outlet connection etc, complete in all respect.
| i. | Size 4'-0" x 4'-0" x 4'-0" water depth | Job. | 2 |  | 0 | 25000 | 50000 | 50000
4.6 |  | Submersible pump for waste water drainage including float switch, water proof cable, ball valves, check valves with union & lifting chain. (1 duty & 1 standby)
| i. | SP-01 @ 40 gpm 30 feet head. | Nos. | 2 |  | 0 | 1000 | 2000 | 2000
4.7 |  | Motor Control panel for Duplex (2 Nos.) submersible pumps including auto Lead/Lag sequencing of pumps, pump starters, auto on / off, float switches, high level alarm, power and control wiring. | Job | 2 |  | 0 | 5000 | 10000 | 10000
Sub Total Rs.
SECTION-05 SUNDRIES
Contractor will priced the sundries items for all Plumbing & Sanitary (P&S) services as per specifications, drawings and instruction of consultant.
5.1 |  | Submittals, samples, shop drawings, inspections, As-Built drawings, operation and maintenance manuals and the like as required by specification. | Job. | 1 |  | 0 | 0 | 0 | 0
5.2 |  | Painting, identification and tagging to the P&S installations and equipments. | Job. | 1 |  | 0 | 35000 | 35000 | 35000
5.3 |  | Testing, and commissioning entire P&S installation as per Engineer's approval. | Job. | 1 |  | 0 | 50000 | 50000 | 50000
Sub Total Rs.
|  | TOTAL OF ALL SECTIONS RS. | [6 empty] | 1335200

## FIre
BiIl of Quantities
Fire Suppression Services
Imtiaz Super Market | [8 empty] | Rev.00
Korangi, Karachi. | [8 empty] | Date: 23-09-2024
S.No. |  | Description | Unit | Qty | Material |  | Labour |  | Total
[5 empty] | Rate | Amount | Rate | Amount | Amount Rs.
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression system including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1 |  | Fire hose cabinet double height 32" x 60" x 14", stainless steel front, powder coated back including 1" dia x 100 Rft. rubber hose reel, nozzle guide, lock shield valve, pressure regulating valve automatic 180 deg. swing type, with 2-fire extinguishers as shown on drawing.
| i. | Type FHC | Nos. | 14 |  |  | 6000 | 84000 | 84000
2 |  | Fire hose cabinet size 42" x 36" x 12" for spare hose pipes including 4 Nos. 2-1/2" x 100 Rft. synthetic hose pipe, jet/spray/fog nozzle with aluminum instantaneous coupling, 2-Nos. fire blanket 6'-0" X 6'-0", fireman's axe, 2-pairs of fire proof gloves, front breakable glass, lock and all other accessories as specified, complete in all respects as per drawings, specified.
| i. | Type FHC-S | No. | 1 |  |  | 6000 | 6000 | 6000
3 |  | Fire department breeching connection 2 ways as per BSS 5041-3 including cabinet with breakable glass, SS frame & drain plug. | Nos. | 2 |  |  | 5000 | 10000 | 10000
4 |  | Landing valves size 2-1/2" dia complete in all respects. | Nos. | 10 |  |  | 3000 | 30000 | 30000
5 |  | MS Sch-40 seamless pipes including all specials fittings UL listed FM approved, threaded, welded joints, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, supports and hangers, sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
| i. | Dia 1" (Threaded fitting) | Rft. | 3910 |  |  | 180 | 703800 | 703800
| ii. | Dia 1-1/4" (Threaded fitting) | Rft. | 1200 |  |  | 200 | 240000 | 240000
| iii. | Dia 1-1/2" (Threaded fitting) | Rft. | 540 |  |  | 225 | 121500 | 121500
| iv. | Dia 2" (Threaded fitting) | Rft. | 510 |  |  | 250 | 127500 | 127500
| v. | Dia 2-1/2" (Welded joints fitting) | Rft. | 560 |  |  | 275 | 154000 | 154000
| vi. | Dia 3" (Welded joints fitting) | Rft. | 760 |  |  | 300 | 228000 | 228000
| vii. | Dia 4" (Welded joints fitting) | Rft. | 840 |  |  | 350 | 294000 | 294000
| viii. | Dia 6" (Welded joints fitting) | Rft. | 260 |  |  | 400 | 104000 | 104000
6 |  | Sprinkler Heads
| i. | Sprinkler Upright type standard response K = 5.6 (Opening Temperature 68ºC) | Nos. | 600 |  |  | 600 | 360000 | 360000
| ii. | Sprinkler Pendent type concealed with cover plate, quick respose K = 5.6 (Opening Temperature 57ºC) | Nos. | 66 |  |  | 500 | 33000 | 33000
| iii. | Sprinkler Side wall type quick response K = 5.6 (Opening Temperature 57ºC) | No. | 1 |  |  | 500 | 500 | 500
7 |  | Fire extinguishers with fixing accessories.
| i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 10 |  |  | 500 | 5000 | 5000
| ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 10 |  |  | 500 | 5000 | 5000
| iii. | Type Class K FX-5 (6 Litre Wet chemical fire extinguisher). | No. | 1 |  |  | 500 | 500 | 500
| iv. | Automatic fire extinguisher (10 Kg. Dry Chemical Powder) | Nos. | 4 |  |  | 500 | 2000 | 2000
| v. | 100 Litres Capacity (Foam Extinguisher Trolley) | No. | 1 |  |  | 500 | 500 | 500
| vi. | 30 Kg. Capacity (CO2 Extinguisher Trolley) | Nos. | 2 |  |  | 2000 | 4000 | 4000
8 |  | Zone Control Valve assembly 4" dia complete with following.
| i. | UL Listed Pressure reducing valve (PRV) 4" dia
| ii. | OS & Y Gate valve 4" size
| iii. | Check valve 4" size | Nos. | 5 |  |  | 8000 | 40000 | 40000
| iv. | Pressure Gauge
| v. | Water flow switch 4" dia
| vi. | 2" dia test valve with sight glass & sectional drain valve.
9 |  | Alarm Check valve assembly with alarm gong and pipe work. with retarding chamber.
| i. | Size. 6" | No. | 1 |  |  | 1000 | 1000 | 1000
10 |  | Pressure relief valve size 4" dia | No. | 1 |  |  | 1000 | 1000 | 1000
11 |  | Automatic air relief valve, 1" connection | No. | 1 |  |  | 1000 | 1000 | 1000
12 |  | Automatic air relief valve, 1" connection with ball valve. | Nos. | 4 |  |  | 1000 | 4000 | 4000
13 |  | Pressure gauge with ball valve. | Nos. | 4 |  |  | 1000 | 4000 | 4000
14 |  | Float Switch for low water level cut off. | No. | 1 |  |  | 1000 | 1000 | 1000
15 |  | Anti vortex suction plates for 6" dia. suction pipe | No. | 1 |  |  | 5000 | 5000 | 5000
16 |  | Flow meter 6" dia. | No. | 1 |  |  | 5000 | 5000 | 5000
17 |  | OS & Y Gate valve matching flanges with tempering switch.
| i. | Size. 3" | Nos. | 3 |  |  | 3000 | 9000 | 9000
| ii. | Size. 4" | No. | 1 |  |  | 4000 | 4000 | 4000
| iii. | Size. 6" | Nos. | 5 |  |  | 5000 | 25000 | 25000
18 |  | Throttling type butterfly valve with matching flanges.
| i. | Size. 6" | Nos. | 2 |  |  | 5000 | 10000 | 10000
19 |  | C.I body check valve with matching flanges.
| i. | Size. 4" | No. | 1 |  |  | 4000 | 4000 | 4000
| ii. | Size. 6" | Nos. | 2 |  |  | 5000 | 10000 | 10000
20 |  | Fire Pumps Set 500 gpm @ 9.5 bar comprising of 1 No. multistage in line Jockey Pump + 1 No. main horizontal pump with electrical motor + 1 No. Standby horizontal pump with diesel engine, diesel storage tank including pump controllers mounted on common MS skid, inter connecting pipes, wiring, OS&Y valve, check valves and all accessories as per requirement of NFPA 20, drawings and engineer instruction. | Set. | 1 |  |  | 100000 | 100000 | 100000
21 |  | Supervisory Fire Control Panel for sensing and monitoring of flow and monitoring OS&Y valves switching with true alarm including batteries and charger. | Job. | 1 |  |  | 50000 | 50000 | 50000
22 |  | MS insulated 6" dia Diesel Engine Flue pipe with 2" Rockwool insulation up to outside the building as per Consultant's approval. | Job. | 1 |  |  | 45000 | 45000 | 45000
23 |  | Allied electrical work including power cables to pumps motors, control cables and wires from sensing monitoring and indicating devices such flow switches and valves to Electrical Control Panel and Fire Control Panel and supervisory switch including GI/PVC conduits and tray, termination, luxes and all accessories complete in all respects. Note: Contractor shall perform allied electrical works within the pump room. Power to the pump room shall be provided by the client. | Job. | 1 |  |  | 35000 | 35000 | 35000
24 |  | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1 |  |  | 10000 | 10000 | 10000
25 |  | Making of As-Built & Shop Drawings on AutoCAD 2018 or latest version with sectional details complete in all respects as per instructions of consultant. | Job. | 1 |  |  | 20000 | 20000 | 20000
26 |  | Painting, identification and tagging to the installations and equipments. | Job. | 1 |  |  | 150000 | 150000 | 150000
27 |  | Flushing of entire fire pipe work according to (NFPA-13). | Job. | 1 |  |  | 45000 | 45000 | 45000
28 |  | Testing, and commissioning of entire fire fighting installation as per Consultant's approval. | Job. | 1 |  |  | 50000 | 50000 | 50000
|  | Total Cost of FSS Works Rs. | [6 empty] | 3142300
Note:
> | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).