## BiIl of Quantities
BiIl of Quantities
Fire Suppression Services
Imtiaz Super Market | [8 empty] | Rev.00
Korangi, Karachi. | [8 empty] | Date: 23-09-2024
S.No. |  | Description | Unit | Qty | Material |  | Labour |  | Total
[5 empty] | Rate | Amount | Rate | Amount | Amount Rs.
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression system including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1 |  | Fire hose cabinet double height 32" x 60" x 14", stainless steel front, powder coated back including 1" dia x 100 Rft. rubber hose reel, nozzle guide, lock shield valve, pressure regulating valve automatic 180 deg. swing type, with 2-fire extinguishers as shown on drawing.
| i. | Type FHC | Nos. | 14 |  |  | 6000 | 84000 | 84000
2 |  | Fire hose cabinet size 42" x 36" x 12" for spare hose pipes including 4 Nos. 2-1/2" x 100 Rft. synthetic hose pipe, jet/spray/fog nozzle with aluminum instantaneous coupling, 2-Nos. fire blanket 6'-0" X 6'-0", fireman's axe, 2-pairs of fire proof gloves, front breakable glass, lock and all other accessories as specified, complete in all respects as per drawings, specified.
| i. | Type FHC-S | No. | 1 |  |  | 6000 | 6000 | 6000
3 |  | Fire department breeching connection 2 ways as per BSS 5041-3 including cabinet with breakable glass, SS frame & drain plug. | Nos. | 2 |  |  | 5000 | 10000 | 10000
4 |  | Landing valves size 2-1/2" dia complete in all respects. | Nos. | 10 |  |  | 3000 | 30000 | 30000
5 |  | MS Sch-40 seamless pipes including all specials fittings UL listed FM approved, threaded, welded joints, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, supports and hangers, sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
| i. | Dia 1" (Threaded fitting) | Rft. | 3910 |  |  | 180 | 703800 | 703800
| ii. | Dia 1-1/4" (Threaded fitting) | Rft. | 1200 |  |  | 200 | 240000 | 240000
| iii. | Dia 1-1/2" (Threaded fitting) | Rft. | 540 |  |  | 225 | 121500 | 121500
| iv. | Dia 2" (Threaded fitting) | Rft. | 510 |  |  | 250 | 127500 | 127500
| v. | Dia 2-1/2" (Welded joints fitting) | Rft. | 560 |  |  | 275 | 154000 | 154000
| vi. | Dia 3" (Welded joints fitting) | Rft. | 760 |  |  | 300 | 228000 | 228000
| vii. | Dia 4" (Welded joints fitting) | Rft. | 840 |  |  | 350 | 294000 | 294000
| viii. | Dia 6" (Welded joints fitting) | Rft. | 260 |  |  | 400 | 104000 | 104000
6 |  | Sprinkler Heads
| i. | Sprinkler Upright type standard response K = 5.6 (Opening Temperature 68ºC) | Nos. | 600 |  |  | 600 | 360000 | 360000
| ii. | Sprinkler Pendent type concealed with cover plate, quick respose K = 5.6 (Opening Temperature 57ºC) | Nos. | 66 |  |  | 500 | 33000 | 33000
| iii. | Sprinkler Side wall type quick response K = 5.6 (Opening Temperature 57ºC) | No. | 1 |  |  | 500 | 500 | 500
7 |  | Fire extinguishers with fixing accessories.
| i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 10 |  |  | 500 | 5000 | 5000
| ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 10 |  |  | 500 | 5000 | 5000
| iii. | Type Class K FX-5 (6 Litre Wet chemical fire extinguisher). | No. | 1 |  |  | 500 | 500 | 500
| iv. | Automatic fire extinguisher (10 Kg. Dry Chemical Powder) | Nos. | 4 |  |  | 500 | 2000 | 2000
| v. | 100 Litres Capacity (Foam Extinguisher Trolley) | No. | 1 |  |  | 500 | 500 | 500
| vi. | 30 Kg. Capacity (CO2 Extinguisher Trolley) | Nos. | 2 |  |  | 2000 | 4000 | 4000
8 |  | Zone Control Valve assembly 4" dia complete with following.
| i. | UL Listed Pressure reducing valve (PRV) 4" dia
| ii. | OS & Y Gate valve 4" size
| iii. | Check valve 4" size | Nos. | 5 |  |  | 8000 | 40000 | 40000
| iv. | Pressure Gauge
| v. | Water flow switch 4" dia
| vi. | 2" dia test valve with sight glass & sectional drain valve.
9 |  | Alarm Check valve assembly with alarm gong and pipe work. with retarding chamber.
| i. | Size. 6" | No. | 1 |  |  | 1000 | 1000 | 1000
10 |  | Pressure relief valve size 4" dia | No. | 1 |  |  | 1000 | 1000 | 1000
11 |  | Automatic air relief valve, 1" connection | No. | 1 |  |  | 1000 | 1000 | 1000
12 |  | Automatic air relief valve, 1" connection with ball valve. | Nos. | 4 |  |  | 1000 | 4000 | 4000
13 |  | Pressure gauge with ball valve. | Nos. | 4 |  |  | 1000 | 4000 | 4000
14 |  | Float Switch for low water level cut off. | No. | 1 |  |  | 1000 | 1000 | 1000
15 |  | Anti vortex suction plates for 6" dia. suction pipe | No. | 1 |  |  | 5000 | 5000 | 5000
16 |  | Flow meter 6" dia. | No. | 1 |  |  | 5000 | 5000 | 5000
17 |  | OS & Y Gate valve matching flanges with tempering switch.
| i. | Size. 3" | Nos. | 3 |  |  | 3000 | 9000 | 9000
| ii. | Size. 4" | No. | 1 |  |  | 4000 | 4000 | 4000
| iii. | Size. 6" | Nos. | 5 |  |  | 5000 | 25000 | 25000
18 |  | Throttling type butterfly valve with matching flanges.
| i. | Size. 6" | Nos. | 2 |  |  | 5000 | 10000 | 10000
19 |  | C.I body check valve with matching flanges.
| i. | Size. 4" | No. | 1 |  |  | 4000 | 4000 | 4000
| ii. | Size. 6" | Nos. | 2 |  |  | 5000 | 10000 | 10000
20 |  | Fire Pumps Set 500 gpm @ 9.5 bar comprising of 1 No. multistage in line Jockey Pump + 1 No. main horizontal pump with electrical motor + 1 No. Standby horizontal pump with diesel engine, diesel storage tank including pump controllers mounted on common MS skid, inter connecting pipes, wiring, OS&Y valve, check valves and all accessories as per requirement of NFPA 20, drawings and engineer instruction. | Set. | 1 |  |  | 100000 | 100000 | 100000
21 |  | Supervisory Fire Control Panel for sensing and monitoring of flow and monitoring OS&Y valves switching with true alarm including batteries and charger. | Job. | 1 |  |  | 50000 | 50000 | 50000
22 |  | MS insulated 6" dia Diesel Engine Flue pipe with 2" Rockwool insulation up to outside the building as per Consultant's approval. | Job. | 1 |  |  | 45000 | 45000 | 45000
23 |  | Allied electrical work including power cables to pumps motors, control cables and wires from sensing monitoring and indicating devices such flow switches and valves to Electrical Control Panel and Fire Control Panel and supervisory switch including GI/PVC conduits and tray, termination, luxes and all accessories complete in all respects. Note: Contractor shall perform allied electrical works within the pump room. Power to the pump room shall be provided by the client. | Job. | 1 |  |  | 35000 | 35000 | 35000
24 |  | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1 |  |  | 10000 | 10000 | 10000
25 |  | Making of As-Built & Shop Drawings on AutoCAD 2018 or latest version with sectional details complete in all respects as per instructions of consultant. | Job. | 1 |  |  | 20000 | 20000 | 20000
26 |  | Painting, identification and tagging to the installations and equipments. | Job. | 1 |  |  | 150000 | 150000 | 150000
27 |  | Flushing of entire fire pipe work according to (NFPA-13). | Job. | 1 |  |  | 45000 | 45000 | 45000
28 |  | Testing, and commissioning of entire fire fighting installation as per Consultant's approval. | Job. | 1 |  |  | 50000 | 50000 | 50000
|  | Total Cost of FSS Works Rs. | [6 empty] | 3142300
Note:
> | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).