## Grand Summary
CITIBANK
PROJECT: CITIBANK OFFICES, DOLMEN SKY TOWERS KARACHI
(ISSUED FOR TENDER)
Date: 12-01-2024
ID WORKS BOQ/SPECIFICATIONS SUMMARY
| Divisions | Description of Work | Amounts
| 1 | ACMV | 36361434.5
| 2 | Plumbing | 5569660
| 3 | Fire Suppression | 5313366
| 4 | Clean Agent | 4234900
|  | Grand Total (in PKR): | 51479360.5
Note:
i. | Contractor to verify and coordinate DRAWINGS + BOQ, Discrepancies to be noted to architect. Since it is a lumpsum contract cost variation will not be entertained after awards of work.
ii. | Quantities are indicative and to the best of our understanding however, vendor to verify all quantities during RFP to ensure nothing is missed.
iii. | Any item that may be required for a successful closure of project, kindly add it as a separate line item during RFP.
iv. | Rates should be inclusive of WHT.
v. | All certifications and documentations to be submitted by GC for respective items as required by LEEDs.

## ACMV BOQ
Bill of Quantities
ACMV Works
CITI BANK | [11 empty] | Rev.00
13th Floor, Dolmen Sky Tower, Karachi. | [11 empty] | Date: 15-01-2024
[6 empty] | MATERIAL |  | LABOUR |  | TOTAL | LEAD TIME | BRAND/MAKE
S.NO. |  | DESCRIPTION | UNIT | BOQ QTY | VERIFIED QTY | RATE | AMOUNT | RATE | AMOUNT | AMOUNT Rs.
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of consultant
1 |  | Supply, installation, testing and commissioning of ducted fan coil unit of different capacities complete in all respects, ready to operate including supply and installation of all accessories, lindaptor supports, hanger steel base, vibration isolators, including interconnecting power & control wiring (terminal connection) with inlet & outlet chilled water connections, drain connection, flexible rubber duct connection / connector etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 1.1 | DFCU-01 (Lift Lobbies) | Nos. | 2 |  | 390000 | 780000 | 30000 | 60000 | 840000 | 8 to 10 weeks | SABRO / TRANE
| 1.2 | DFCU-02 (Communication Room) | No. | 1 |  | 390000 | 390000 | 30000 | 30000 | 420000 | 8 to 10 weeks | SABRO / TRANE
2 |  | Supply, installation, testing and commissioning of of water cooled pacakge unit complete in all respects, ready to operate including supply and installation of all accessories, lindaptor supports, hanger steel base, vibration isolators, including interconnecting power & control wiring (terminal connection) with inlet & outlet cooling water connections, drain connection, flexible rubber duct connection / connector etc. complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant. | [6 empty] | 0
| 2.1 | WCPU-01 (Security Room) | No. | 1 |  | 928125 | 928125 | 15000 | 15000 | 943125 | 18 to 20 weeks | DAIKIN
| 2.2 | WCPU-02 (Communication Room) | Nos. | 2 |  | 1722875 | 3445750 | 25000 | 50000 | 3495750 | 18 to 20 weeks | DAIKIN
3 |  | Supply, installation, testing and commissioning of of VAV & CAV Boxes as per mentioned in schedule with digital thermostat controller, pressure sensor, control wiring, including supply & installation of flexible duct connection / connector, power wiring upto 5 meter with connection, lindaptor support & hangers complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. |  |  |  |  | 0 |  | 0
| A | VAVs |  |  |  |  | 0 |  | 0
| i. | VAV-01 | Nos. | 2 |  | 238888 | 477776 | 8000 | 16000 | 493776 | 8 to 10 weeks | IMS / JES
| ii. | VAV-02 | No. | 10 |  | 238888 | 2388880 | 8000 | 80000 | 2468880
| iii. | VAV-03 | No. | 2 |  | 238888 | 477776 | 8000 | 16000 | 493776
| iv. | VAV-04 | No. | 2 |  | 241755 | 483510 | 8000 | 16000 | 499510
| v. | VAV-05 | No. | 2 |  | 241755 | 483510 | 8000 | 16000 | 499510
| B | CAVs | [6 empty] | 0
| i. | CAV-01 | Nos. | 1 |  | 165000 | 165000 | 8000 | 8000 | 173000
| ii. | CAV-02 | Nos. | 6 |  | 165000 | 990000 | 8000 | 48000 | 1038000
| iii. | CAV-03 | Nos. | 10 |  | 165000 | 1650000 | 8000 | 80000 | 1730000
| iv. | CAV-04 | Nos. | 7 |  | 165000 | 1155000 | 8000 | 56000 | 1211000
4 |  | Supply & installation of valves & accessories for DFCU & WCPU etc. complete in all respects as per specifications, drawings and as per instructions of consultant. |  |  |  |  | 0 |  | 0
| A | for DFCUs |  |  |  |  | 0 |  | 0 |  | 2 to 3 weeks | GALA
| 4.1 | Ball Valve |  |  |  |  | 0 |  | 0
| i. | 25mm dia | Nos. | 12 |  | 8250 | 99000 | 1000 | 12000 | 111000
| 4.2 | Strainers |  |  |  |  | 0 |  | 0
| i. | 25mm dia | Nos. | 3 |  | 8250 | 24750 | 1000 | 3000 | 27750
| 4.3 | Balancing Valve (with self sealing measuring nipples) |  |  |  |  | 0 |  | 0
| i. | 25mm dia | Nos. | 3 |  | 19500 | 58500 | 1000 | 3000 | 61500
| 4.4 | Thermometer 150mm Height Scale Type (with Thermo well) 0 ºC to 60 ºC | Nos. | 6 |  | 12000 | 72000 | 1000 | 6000 | 78000 | 2 to 3 weeks | WEISS / WEKSLER
| 4.5 | Pressure Gauge with Ball Valve & Siphon, Liquid filled Dial type range 0 psi to 100 psi. (100mm dial Size) | Nos. | 6 |  | 11500 | 69000 | 1000 | 6000 | 75000 | 2 to 3 weeks | WEISS / WEKSLER
| 4.6 | 2-Way Motorized Valve with Actuator (0-100% modulating) |  |  |  |  | 0 |  | 0
| i. | 25mm dia | Nos. | 3 |  | 65000 | 195000 | 3000 | 9000 | 204000 |  | Honeywell
| 4.7 | Auto Air Vents |  |  |  |  | 0 |  | 0
| i. | 25mm dia | Nos. | 3 |  | 9000 | 27000 | 1000 | 3000 | 30000
| 4.8 | Digital Decorative Thermostat Controller (BMS Interfacable) with Duct Mounted Sensor - Timer Limit Setting required | Nos. | 3 |  | 65000 | 195000 | 3000 | 9000 | 204000
| 4.9 | Timer Relay for Time Setting as per Landlord's Chilled Water Schedule | No. | 0 |  |  | 0 |  | 0 | 0
| 5 | Control wiring from controller to sensors, motorized valve and power wiring, up to 5 meter radius | Job. | 3 |  | 20000 | 60000 | 5000 | 15000 | 75000 | 2 to 3 weeks | FAST / INDUS
| B | for WCPU |  |  |  |  | 0 |  | 0
| 5.1 | Ball Valve |  |  |  |  | 0 |  | 0
| i. | 25mm dia | Nos. | 4 |  | 8250 | 33000 | 1000 | 4000 | 37000 | 2 to 3 weeks | GALA
| ii. | 32mm dia | Nos. | 8 |  | 11500 | 92000 | 1000 | 8000 | 100000
| 5.2 | Strainers |  |  |  |  | 0 |  | 0
| i. | 25mm dia | No. | 1 |  | 7500 | 7500 | 1000 | 1000 | 8500
| ii. | 32mm dia | Nos. | 2 |  | 9800 | 19600 | 1000 | 2000 | 21600
| 5.21 | Balancing Valve (with self sealing measuring nipples) |  |  |  |  | 0 |  | 0
| i. | 25mm dia | No. | 1 |  | 18000 | 18000 | 1500 | 1500 | 19500
| ii. | 32mm dia | Nos. | 2 |  | 21500 | 43000 | 1500 | 3000 | 46000
| 5.22 | Flexible Connectors |  |  |  |  | 0 |  | 0
| i. | 25mm dia | Nos. | 2 |  | 11500 | 23000 | 1000 | 2000 | 25000
| ii. | 32mm dia | Nos. | 4 |  | 14250 | 57000 | 1000 | 4000 | 61000
| 5.23 | Auto Air Vents |  |  |  |  | 0 |  | 0
| i. | 25mm dia | Nos. | 2 |  | 9000 | 18000 | 1000 | 2000 | 20000
| ii. | 32mm dia | Nos. | 4 |  | 13250 | 53000 | 1000 | 4000 | 57000
| 5.24 | Thermometer 150mm Height Scale Type (with Thermo well) 0 ºC to 60 ºC |  |  |  |  | 0 |  | 0 |  | 2 to 3 weeks | WEISS / WEKSLER
| i. | 25mm dia | Nos. | 2 |  | 12000 | 24000 | 1000 | 2000 | 26000
| ii. | 32mm dia | Nos. | 4 |  | 11500 | 46000 | 1000 | 4000 | 50000
| 5.25 | Pressure Gauge with Ball Valve & Siphon, Liquid filled Dial type range 0 psi to 100 psi. (100mm dial Size) |  |  |  |  | 0 |  | 0 |  | 2 to 3 weeks | WEISS / WEKSLER
| i. | 25mm dia | Nos. | 2 |  | 17500 | 35000 | 2000 | 4000 | 39000
| ii. | 32mm dia | Nos. | 4 |  | 21500 | 86000 | 2000 | 8000 | 94000
| 5.26 | Pressure Switch - Setting as per Landlord's Condenser Water Flowrate | Nos. | 3 |  | 27000 | 81000 | 3000 | 9000 | 90000 | 2 to 3 weeks | DANFOSS
| 5.27 | Control wiring from controller to sensors and power wiring, up to 5 meter radius | Job. | 3 |  | 15000 | 45000 | 5000 | 15000 | 60000 | 2 to 3 weeks | FAST / INDUS
5 |  | Supply & installation of SCH-40 M.S.(As per ASME & API standard, Heavy Quality with standard SCH 40 wall thickness) pipes & fitting for chilled & cooling water circulation system complete with bends, tees, unions, sockets, specials, lindaptor support, hangers & anchors, M.S. angle, U channel, roller support, bolts, rods, clamps, concrete fasteners, wooden sleeves at wall opening, etc as required to complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. |  |  |  |  | 0 |  | 0
| 5.1 | 25mm dia | Rm | 180 |  | 2523.5 | 454230 | 1000 | 180000 | 634230 | 2 to 3 weeks | PROTEK
| 5.2 | 32mm dia | Rm | 10 |  | 3296 | 32960 | 1200 | 12000 | 44960
| 5.3 | 40mm dia | Rm | 5 |  | 4017 | 20085 | 1300 | 6500 | 26585
| 5.4 | 50mm dia | Rm | 25 |  | 4892.5 | 122312.5 | 1400 | 35000 | 157312.5
6 |  | Supply & installation of adhesive 20mm thick 25kg/m3 density rubber foam (XLPE) insulation with aluminum foil, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. |  |  |  |  | 0 |  | 0
| 6.1 | 25mm dia (chilled water pipes only) | Rm | 120 |  | 2008.5 | 241020 | 150 | 18000 | 259020 | 2 to 3 weeks | XLPE AEROFOAM
7 |  | Supply, fabrication and installation of machine made G.I sheet metal duct different sections supply, return, fresh & exhaust air including plenums, splitter dampers, guide vanes, flexible duct connector / connection, access door, transformation, plenums chambers, wooden frame, lindaptor supports, anchors & hangers complete in all respects ready to operate as per drawings, specification, instruction and approval of consultant. | Sqm | 1250 |  | 5047 | 6308750 | 1000 | 1250000 | 7558750 | 2 to 3 weeks | ISL
8 |  | Supply & installation of adhesive 20mm thick 25kg/m3 density rubber foam (XLPE) insulation with aluminum foil (except toilet exhaust duct), complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqm | 1200 |  | 5665 | 6798000 | 500 | 600000 | 7398000 | 2 to 3 weeks | XLPE AEROFOAM
9 |  | Supply & installation of acoustical duct sound liner rubberfoam adhesive 12mm thick 30kg/m3 density in supply air & return air duct etc, complete in all respects ready to operate as per drawings, specification and as per instruction of consultant. | Sqm | 100 |  | 5800 | 580000 | 500 | 50000 | 630000 | 2 to 3 weeks | AFFICO
10 |  | Supply & installation of aluminum fabricated, powder coated grills, diffusers and registers etc for supply, return, exhaust & fresh air of different sizes (Grade A) wooden frame, lindaptor supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. |  |  |  |  | 0 |  | 0
| 10.1 | Supply & Return Air Register & Diffuser with Damper a. 450mm x450 mm b. 600mm x 600mm | Sqm | 9 |  | 40000 | 360000 | 2000 | 18000 | 378000 | 6 to 8 weeks | MEHRAN / AIR GUIDE
| 10.2 | Supply Air Round Diffuser with Damper |  |  |  |  | 0 |  | 0
| i. | 250mm dia | Nos. | 4 |  | 5500 | 22000 | 1000 | 4000 | 26000
| ii. | 300mm dia | Nos. | 7 |  | 6500 | 45500 | 1000 | 7000 | 52500
| iii. | 350mm dia | Nos. | 16 |  | 7250 | 116000 | 1000 | 16000 | 132000
| 10.3 | Grill for Supply, Return, Transfer Air & Cross Talk Silencer outside | Sqm | 6 |  | 32000 | 192000 | 2000 | 12000 | 204000
| 10.4 | S.S Wire Mesh with G.I Frame | Sqm | 1 |  | 15000 | 15000 | 2000 | 2000 | 17000
| 11.4 | Fresh Air Louver 100mm x 100mm | No. | 1 |  | 1500 | 1500 | 500 | 500 | 2000
| 11.5 | Linear Slots 6000 Series with bird mesh |  |  |  |  | 0 |  | 0
| i. | 1 Slot of 20mm | Rm | 45 |  | 4000 | 180000 | 500 | 22500 | 202500
| ii. | 2 Slots of 20mm | Rm | 15 |  | 4750 | 71250 | 500 | 7500 | 78750
| 11.6 | Disc Valves |  |  |  |  | 0 |  | 0
| i. | 150mm dia | Nos. | 20 |  | 3000 | 60000 | 750 | 15000 | 75000
11 |  | Supply & installation of flexible duct including hangers, jubilee clamp complete in all respects as per specification, drawings & as per instruction of consultant. |  |  |  |  | 0 |  | 0
| 11.1 | 150mm dia | Rm | 70 |  | 1750 | 122500 | 500 | 35000 | 157500 | 3 to 4 weeks | AFS / FLEXIVA
| 11.2 | 200mm dia | Rm | 2 |  | 1900 | 3800 | 600 | 1200 | 5000
12 |  | Supply & installation of butterfly damper for above flexible duct with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of consultant. |  |  |  |  | 0 |  | 0
| 12.1 | 150mm dia | Nos. | 60 |  | 3000 | 180000 | 500 | 30000 | 210000 | 6 to 8 weeks | MEHRAN / AIR GUIDE
| 12.2 | 200mm dia | No. | 1 |  | 3200 | 3200 | 500 | 500 | 3700
13 |  | Supply & installation of Volume Control Damper in 16 SWG G.I sheet metal with gas kits, nut bolts, etc, complete in all respects ready to operate as per specification, drawings and as per instruction, approval of consultant. | Sqm | 6 |  | 32000 | 192000 | 2000 | 12000 | 204000 | 6 to 8 weeks | MEHRAN / AIR GUIDE
14 |  | Supply and installation of Back Draft Damper in MS Sheet with gas kits, nut botls. complete in all respects ready to operate as per specification, drawings & as per instruction of consultant. |  |  |  |  | 0 |  | 0 |  | 6 to 8 weeks | MEHRAN / AIR GUIDE
| 14.1 | 200mm x 200mm | Nos. | 2 |  | 4000 | 8000 | 1000 | 2000 | 10000
| 14.2 | 500mm x 400mm | Nos. | 2 |  | 7500 | 15000 | 1000 | 2000 | 17000
15 |  | Supply & installation of fire damper with linkage & fuse complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant. |  |  |  |  | 0 |  | 0 |  | 6 to 8 weeks | MEHRAN / AIR GUIDE
| 15.1 | 750mm x 500mm | No. | 1 |  | 15750 | 15750 | 1000 | 1000 | 16750
| 15.2 | 1100mm x 300mm | No. | 1 |  | 13200 | 13200 | 1000 | 1000 | 14200
16 |  | Supply, installation of Motorized Damper with gas kits, nut bolts, including pressure transmeter, controller, control wiring & power wiring upto 5 meter, complete in all respects, ready to operate as per specification, drawings & as per instruction of Consultant. |  |  |  |  | 0 |  | 0 |  | 6 to 8 weeks | BELIMO
| 16.1 | 1100mm x 300mm | Nos. | 2 |  | 165000 | 330000 | 5000 | 10000 | 340000
15 |  | Supply & istallation of uPVC (Sch 40.) drain pipe insulated with 10mm thick rubber foam insulation including clamps, bends, tees, drain plugs, sockets, protection treatment, PVC tape wrapping, lindaptor supports & hangers complete in all respects as per specifications, drawings & as per instructions of Consultant. |  |  |  |  | 0 |  | 0
| 15.1 | 25mm dia | Rm | 70 |  | 1450 | 101500 | 200 | 14000 | 115500
| 15.2 | 32mm dia | Rm | 15 |  | 1900 | 28500 | 300 | 4500 | 33000 | 2 to 3 weeks | DADEX
16 |  | Exhaust Air Fans for Ventilation | Nos. | 2 |  | 42000 | 84000 | 1000 | 2000 | 86000
17 |  | Supply, installation, testing & commissioning of automatic control mechanism / system (logic based) of both WCPUs & DFCUs, including controls, BMS interfacable thermostat temperature sensors, timers, contactors, relays, communication protocols, input & output modules, interconnecting wiring, power wiring, panel box etc, complete in all respects ready to operate as per instruction of consultant, (refer to I/O summary for details). | Job. | 1 |  | 550000 | 550000 | 35000 | 35000 | 585000 | 6 to 8 weeks | JES/ IMS
18 |  | Supply & installation of BMS interfacable digital display HMI, addressable, wirelessly connected with wifi, communicate through mobile app / software remotely, including fault alarm / notification etc, complete in all respects ready to operate as per instruction of consultant. | Job. | 1 |  | 475000 | 475000 | 35000 | 35000 | 510000 | 6 to 8 weeks | JES/ IMS
19 |  | Painting & Identification work on pipes, all ducts, valves & accessories, supports, hangers etc. complete in all respects with one coat of ICI make Red lead oxide primer & two coats of ICI make enamel paint as per instruction of Consultant. | Job. | 1 |  | 40000 | 40000 | 40000 | 40000 | 80000 |  | BERGER
20 |  | Testing, balancing and commissioning of water & air side of the system (from independent agency) complete in all respects including flow measurement & balancing, temp, pressure, electrical data of related equipment etc. as per specifications and as per instructions of Consultant. | Job. | 1 |  | 0 | 0 | 100000 | 100000 | 100000
21 |  | Air Quality Test (from independent agency) complete in all respects, as per specifications and as per instructions of consultant. | Job. | 1 |  | 15000 | 15000 | 25000 | 25000 | 40000
22 |  | Making of Shop drawings on Auto CAD latest version with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment as per instruction of consultant. | Job. | 1 |  | 15000 | 15000 | 15000 | 15000 | 30000
|  | Total Cost of ACMV Works (with I.Tax) Rs. |  |  |  |  | 33109734.5 |  | 3251700 | 36361434.5
Note: > Contractor is instructed to visit the site, understand the nature of work and then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## Sheet1
CITI BANK
Material | Lead Time | Make | Origin
DFCU | 8 to 10 weeks | SABRO / TRANE | PAKISTAN / CHINA
WCPU | 18 to 20 weeks | DAIKIN | JAPAN
VAVS | 8 to 10 weeks | BARCOL / HONEYWELL | NEITHERLAND / USA
Plumbing Fixtures | 6 to 8 weeks | GROHE | GERMANY
Fire Extinghuisers | 8 to 10 weeks | Sheild / FIREX / LIFFCO | UK / UAE / UAE
Sprinklers | 8 to 10 weeks | Sheild / FIREX / LIFFCO | UK / UAE / UAE

## Plumbing Summary
Executive Summary
Plumbing & Sanitary Services
CITI BANK OFFICES |  |  |  | Rev.00
13th Floor, Dolmen Sky Tower, Karachi. |  |  |  | Date: 15-01-2024
S. No. | Description | Material Amount | Labour Amount | Total Amount Rs.
1 | SECTION - 01
PLUMBING FIXTURES
2 | SECTION-02
WATER SUPPLY SYSTEM
3 | SECTION-03
SOIL, WASTE VENT AND RAIN WATER DRAINAGE SYSTEM
4 | SECTION-04
SUNDRIES
Total Cost of Plumbing Works (with I.Tax) Rs.
Note:
1) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
2) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).
| iv. | Dia. 1-1/4"
| v. | Dia. 1-1/2"
Size 1"
| iv. | Size 1-1/4"

## Plumbing BOQ
Bill of Quantities
Plumbing & Sanitary Services
CITI BANK OFFICES | [11 empty] | Rev.00
13th Floor, Dolmen Sky Tower, Karachi. | [11 empty] | Date: 15-01-2024
S.No. |  | Description | Unit | BOQ QUANTITY | VERIFIED QUANTITY | Material |  | Labour |  | Total | BRAND/MAKE | LEAD TIME
[6 empty] | Rate | Amount | Rate | Amount | Amount Rs.
SECTION - 01, PLUMBING FIXTURES.
Supply and installation of plumbing fixtures & faucets complete in all respects including all accessories, support, hangers, etc. ready to use as per specifications, drawings and instructions of Consultant.
1.1 |  | European style W.C. wall hung type with seat cover, concealed flush tank with frame, cover plate, automatic sensor base type flushing system and wall mounted fixing accessories etc. (Low flow water maximum flow rates ~2/4 lpf dual flush).
| i. | Type - EWC-WH | Nos. | 10 |  | 115000 | 1150000 | 10000 | 100000 | 1250000 | GROHE | 6 to 8 weeks
1.2 |  | European style W.C wall hung type with seat cover, concealed flush tank with frame, cover plate, automatic sensor base type flushing system, S.S bracket and fixing accessories etc. (Low flow water maximum flow rates ~2/4 lpf dual flush).
| i. | Type - EWC-WH | Nos. | 2 |  | 115000 | 230000 | 10000 | 20000 | 250000 | GROHE | 6 to 8 weeks
1.3 |  | Toilet Hand Spray with flexible chain & telephone type shower Including tee stop cock etc. complete in all respect.
| i. | Type - TS | Nos. | 12 |  | 7500 | 90000 | 1500 | 18000 | 108000 | GROHE | 6 to 8 weeks
1.4 |  | Wash basin (WB) half pedestal wall mounted including bottle trap, waste, stop cocks, etc.
| i. | Type - WB | Nos. | 4 |  | 42000 | 168000 | 3000 | 12000 | 180000 | GROHE | 6 to 8 weeks
| ii. | Type - WB (Vanity) | Nos. | 6 |  | 41500 | 249000 | 3000 | 18000 | 267000
1.5 |  | Wash basin hot and cold water mixer, automatic sensor base type system etc. (Low flow water maximum flow rates 0.35 gpm).
| i. | Type - WB | Nos. | 4 |  | 72000 | 288000 | 2000 | 8000 | 296000 | GROHE | 6 to 8 weeks
| ii. | Type - WB (Vanity) | Nos. | 6 |  | 72000 | 432000 | 2000 | 12000 | 444000 | GROHE | 6 to 8 weeks
1.6 |  | Stainless steel kitchen sink including stop cocks, P-trap / bottle trap, waste pipe etc complete in all respects.
| i. | SK - 1 double bowl | No. | 1 |  | 57000 | 57000 | 5000 | 5000 | 62000 | GROHE | 6 to 8 weeks
1.7 |  | Sink hot and cold water mixer (Low flow water maximum flow rates 1 gpm).
| i. | For SK - 1 | Nos. | 1 |  | 35000 | 35000 | 3000 | 3000 | 38000 | GROHE | 6 to 8 weeks
1.8 |  | Installation of S.S Grease Trap 7.5 Kg inlet/outlet connections 50 mm dia complete in all respects. | Nos. | 2 |  | 185000 | 370000 | 3000 | 6000 | 376000
1.9 |  | Mixer for hot & cold water automatic sensor base type system for Ablution.
| i. | Type - M | Nos. | 6 |  | 87000 | 522000 | 2000 | 12000 | 534000 | GROHE | 6 to 8 weeks
1.1 |  | Toilet accessories complete set.
| i. | Soap Dispenser | Nos. | 8 |  | 9500 | 76000 | 500 | 4000 | 80000 | GROHE | 6 to 8 weeks
| ii. | Grab Rail for Handicapped Toilets | Nos. | 2 |  | 7000 | 14000 | 500 | 1000 | 15000 | GROHE | 6 to 8 weeks
| iii. | Paper Holder | Nos. | 12 |  | 12500 | 150000 | 500 | 6000 | 156000 | GROHE | 6 to 8 weeks
| iv. | Coat Hooks | Nos. | 24 |  | 6500 | 156000 | 500 | 12000 | 168000 | GROHE | 6 to 8 weeks
| v. | Automatic Hand Dryer (With 03 Point Wiring - Phase/Neutral/Earth) | Nos. | 6 |  | 22000 | 132000 | 1000 | 6000 | 138000 | GROHE | 6 to 8 weeks
Sub Total Rs.
SECTION-02 WATER SUPPLY SYSTEM.
Supply, installation, testing and commissioning of complete pipe work for cold and hot water system including all accessories required to complete systems ready to operate as per specification, drawings & instruction of Consultant.
2.1 |  | Polypropylene Random PP-R pipes PN 20 and fittings with fusion jointing along with all types of unions, tees, bends, sockets, clamps, lindapter supports hangers, sleeves, masking plates, chiseling, making holes making good, excavation, bedding backfilling as required complete in all respect.
| i. | Dia. OD 25 mm | Rm. | 20 |  | 1450 | 29000 | 300 | 6000 | 35000 | DADEX / RAKHTHERM | 2 to 3 weeks
| ii. | Dia. OD 32 mm | Rm. | 10 |  | 1600 | 16000 | 400 | 4000 | 20000
| iii. | Dia. OD 40 mm | Rm. | 8 |  | 1780 | 14240 | 500 | 4000 | 18240
| iv. | Dia. OD 50 mm | Rm. | 4 |  | 1950 | 7800 | 600 | 2400 | 10200
2.2 |  | Same as item # 2.1 but for hot water supply with Polypropylene Random PP-R (PN -25) with Aluminium foil.
| i. | Dia OD 25 mm | Rm. | 50 |  | 2550 | 127500 | 400 | 20000 | 147500
| ii. | Dia. OD 32 mm | Rm. | 30 |  | 3200 | 96000 | 500 | 15000 | 111000
| iii. | Dia. OD 40 mm | Rm. | 8 |  | 4000 | 32000 | 600 | 4800 | 36800
| iv. | Dia. OD 50 mm | Rm. | 2 |  | 5000 | 10000 | 700 | 1400 | 11400
2.3 |  | Open cell rubber foam insulation 3/8" thick & pvc tape wrapping for hot water pipes.
| i. | Dia OD 25 mm | Rm. | 50 |  | 550 | 27500 | 50 | 2500 | 30000 | Super loan
| ii. | Dia. OD 32 mm | Rm. | 30 |  | 680 | 20400 | 60 | 1800 | 22200
| iii. | Dia. OD 40 mm | Rm. | 8 |  | 775 | 6200 | 70 | 560 | 6760
| iv. | Dia. OD 50 mm | Rm. | 2 |  | 1700 | 3400 | 80 | 160 | 3560
2.4 |  | Brass body gate valves / ball valves with unions.
| i. | Size 50 mm ( 1-1/2" ) | Nos. | 4 |  | 14500 | 58000 | 2000 | 8000 | 66000
2.5 |  | Brass body Bib cock.
| i. | Size 20 mm ( 3/4" ) | Nos. | 3 |  | 7500 | 22500 | 1000 | 3000 | 25500 | SCON VALVE | 3 to 4 weeks
2.6 |  | Hot water storage heater (Electric) suitable for 30 psi working pressure including thermostat, inlet/outlet connection. Pressure relief valve.
| i. | HWE-50 (50 Litres Storage Capacity) | Nos. | 2 |  | 85000 | 170000 | 5000 | 10000 | 180000 | ARISTON
Sub Total Rs.
SECTION-03 SOIL, WASTE VENT AND RAIN WATER DRAINAGE SYSTEM
Supply, fixing, testing and commissioning of equipment, pipe work required to complete the soil, waste, vent and rain water systems in all respects with accessories ready to operate as per specifications, drawings and instructions of Consultant.
3.1 |  | uPVC pipes of approved make along with specials, fittings, bends, wye, tees, sockets, lindapter supports hangers, flexible connectors, sleeves, masking plates, chiseling, making hole, excavation, backfilling making good where as required jointing with rubber ring seal.
| i. | Dia. 50 mm | Rm. | 10 |  | 1500 | 15000 | 500 | 5000 | 20000 | DADEX
| ii. | Dia. 75 mm | Rm. | 10 |  | 4250 | 42500 | 1000 | 10000 | 52500
| iii. | Dia. 100 mm | Rm. | 10 |  | 5900 | 59000 | 1000 | 10000 | 69000
3.2 |  | Floor drain including S.S grating with floor trap, inlet outlet connection complete in all respects.
| i. | FD- 75 mm | Nos. | 20 |  | 4500 | 90000 | 500 | 10000 | 100000 | ALPINE
3.3 |  | S.S grating for floor trap, inlet outlet connection complete in all respects.
| i. | G- 600 x 600 mm | Nos. | 18 |  | 4000 | 72000 | 500 | 9000 | 81000 | ALPINE
3.4 |  | Cleanout for soil, waste pipes of approved make.
| i. | For 75 mm Pipe with SS floor cover plate (FCO) | Nos. | 10 |  | 4500 | 45000 | 1000 | 10000 | 55000
| ii. | For 100 mm Pipe with SS floor cover plate (FCO) | Nos. | 4 |  | 5000 | 20000 | 1000 | 4000 | 24000 | H3 HAMMER
3.5 |  | uPVC cowl for vent pipe of the following dia. including all accessories complete.
| i. | Size. 50 mm | Nos. | 2 |  | 1000 | 2000 | 500 | 1000 | 3000
| iI. | Size. 75 mm | Nos. | 2 |  | 1500 | 3000 | 500 | 1000 | 4000
| ii. | Size. 100 mm | Nos. | 2 |  | 2000 | 4000 | 500 | 1000 | 5000
Sub Total Rs.
SECTION-04 SUNDRIES
Contractor will priced the sundries items for all Plumbing & Sanitary (P&S) services as per specifications, drawings and instruction of consultant.
4.1 |  | Submittals, samples, shop drawings, inspections, As-Built drawings, operation and maintenance manuals and the like as required by specification. | Job. | 1 |  | 25000 | 25000 | 5000 | 5000 | 30000
4.2 |  | Testing, and commissioning entire P&S installation (including landlord's existing PPR piping) as per Engineer's approval. | Job. | 1 |  | 0 | 0 | 40000 | 40000 | 40000
Sub Total Rs.
|  | TOTAL OF ALL SECTIONS RS. |  |  |  |  | 5137040 |  | 432620 | 5569660

## Fire Summary
Executive Summary
Fire Suppression Services
CITI BANK OFFICES |  |  |  |  | Rev.00
13th Floor, Dolmen Sky Tower, Karachi. |  |  |  |  | Date: 15-01-2024
S.no |  | Description | Material | Labour | Total Rs.
FIRE FIGHTING SERVICES
1 |  | MS Sch-40 seamless pipes with fittings.
2 |  | Sprinkler Heads.
3 |  | Fire extinguishers with fixing accessories.
4 |  | Fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations.
5 |  | Shop drawings and Making of As Built drawings.
6 |  | Painting & identification.
7 |  | Flushing of entire fire pipe work.
8 |  | Testing and commissioning.
Total Cost of FSS Works (with I.Tax) Rs.
Note:
1) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
2) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## Fire BOQ
Bill of Quantities
Fire Suppression Services
CITI BANK OFFICES | [11 empty] | Rev.00
13th Floor, Dolmen Sky Tower, Karachi. | [11 empty] | Date: 15-01-2024
S.No. |  | Description | Unit | BOQ QTY | VERIFIED QTY | Material |  | Labour |  | Total | BRAND/MAKE | LEAD TIME
[6 empty] | Rate | Amount | Rate | Amount | Amount Rs.
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression services including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1 |  | MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and wooden sleeves at wall opening, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
| i. | Dia 25 mm (Threaded fitting) | Rm. | 480 |  | 2626.5 | 1260720 | 600 | 288000 | 1548720 | PROTEK | 3 to 4 weeks
| ii. | Dia 32 mm (Threaded fitting) | Rm. | 40 |  | 3296 | 131840 | 700 | 28000 | 159840
| iii. | Dia 40 mm (Threaded fitting) | Rm. | 60 |  | 3811 | 228660 | 800 | 48000 | 276660
| iv. | Dia 50 mm (Threaded fitting) | Rm. | 60 |  | 4475.35 | 268521 | 900 | 54000 | 322521
| v. | Dia. 65 mm (Welded joints fitting) | Rm. | 90 |  | 7467.5 | 672075 | 1000 | 90000 | 762075
| vi. | Dia. 75 mm (Welded joints fitting) | Rm. | 30 |  | 8755 | 262650 | 1200 | 36000 | 298650
| viI. | Dia. 100 mm (Welded joints fitting) | Rm. | 10 |  | 11845 | 118450 | 1500 | 15000 | 133450
2 |  | Sprinkler Heads | [5 empty] | 0 | 0
| i. | Sprinkler Upright type quick response K = 5.6 (Opening Temperature 57ºC) | Nos. | 120 |  | 3150 | 378000 | 500 | 3650 | 381650 | Sheild / FIREX / LIFFCO | 8 to 10 weeks
| ii. | Sprinkler Pendent type quick response K = 5.6 (Opening Temperature 57ºC) | Nos. | 60 |  | 3200 | 192000 | 500 | 3700 | 195700 | Sheild / FIREX / LIFFCO | 8 to 10 weeks
| iii. | Sprinkler Pendent type concealed with C.P cover plate quick response K = 5.6 (Opening Temperature 57ºC) | Nos. | 23 |  | 7500 | 172500 | 600 | 8100 | 180600 | Sheild / FIREX / LIFFCO | 8 to 10 weeks
3 |  | Fire extinguishers with fixing accessories. | [5 empty] | 0 | 0
| i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 7 |  | 32000 | 224000 | 500 | 32500 | 256500 | Sheild / FIREX / LIFFCO | 8 to 10 weeks
| ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 7 |  | 13000 | 91000 | 500 | 13500 | 104500 | Sheild / FIREX / LIFFCO | 8 to 10 weeks
4 |  | Supply & Installation of Corrugated Stainless Steel Flexible Connector Ø 1" X 3 ft (UL/FM) (Braided) | Nos. | 23 |  | 10500 | 241500 | 500 | 11000 | 252500 | SEUNG JIN IND | 8 to 10 weeks
5 |  | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1 |  | 35000 | 35000 | 5000 | 40000 | 75000
6 |  | Making of Shop drawings on Auto CAD 2018 with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects as per instruction of consultant. | Job. | 1 |  | 10000 | 10000 | 10000 | 20000 | 30000
7 |  | Painting, identification and tagging to the installations and equipments, complete in all respects as per instruction of consultant. | Job. | 1 |  | 115000 | 115000 | 40000 | 155000 | 270000 | BERGER
8 |  | Flushing of entire fire pipe work according to (NFPA-13), complete in all respects as per instruction of consultant. | Job. | 1 |  | 0 | 0 | 25000 | 25000 | 25000
9 |  | Testing and commissioning of entire fire fighting and clean agent for fire suppression system complete in all respects as per instruction of consultant. | Job. | 1 |  | 0 | 0 | 40000 | 40000 | 40000
|  | Total Cost of FSS Works (with I.Tax) Rs. |  |  |  |  | 4401916 |  | 911450 | 5313366

## Clean Agent FSS (Comms Room)
Bill of Quantities
Fire Suppression Services
CITI BANK OFFICES | [10 empty] | Rev.00
13th Floor, Dolmen Sky Tower, Karachi. | [10 empty] | Date: 15-01-2024
S.No. |  | Description | Unit | BOQ QUANTITY | Material |  | Labour |  | Total | BRAND/MAKE | LEAD TIME
[5 empty] | Rate | Amount | Rate | Amount | Amount Rs.
NOVEC 1230 SYSYEM
1 |  | CLEAN AGENT (FK-5-1-12 Stored In Cylinder - Ul Listed / Fm Approved)
Supply & installation of clean agent in engineered cylinders of FSS with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
| a. | Clean Agent (FK-5-1-12, Fluoroketone) | Kg. | 60 | 45840 | 2750400 | 2000 | 120000 | 2870400 | FIREX / SHIELD / NAFFCO
| b. | Engineered cylinder with head valve, top plug adapter, siphon tube, pressure gauge, brackets and all other items, complete in all respect. | Nos. | 1 | 350000 | 350000 | 10000 | 10000 | 360000 |  | 10 to 12 Weeks
2 |  | Supply & installation of MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant.
| i. | Dia 40 mm (Threaded fitting) | Rm | 8 | 4000 | 32000 | 1000 | 8000 | 40000 | PROTEK | 2 to 3 weeks
3 |  | SPRINKLER HEADS
Supply & installation of nozzles with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
Brass Discharge Nozzle - 360 Degrees discharge pattern.
| i. | Dia 40 mm | Nos. | 1 | 15000 | 15000 | 5000 | 5000 | 20000
4 |  | INPUT & OUTPUT DEVICES
Supply & installation of input and output devices for the clean agent suppression system (integrated with BMS) with wiring, controls & fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant
| i. | Entinguishing Control Panel for the clean agent fire suppression system | Nos. | 1 | 375000 | 375000 | 5000 | 5000 | 380000
| ii. | Manual Abort / Emergency Cut Off Switch | Nos. | 2 | 9000 | 18000 | 1000 | 2000 | 20000
| iii. | Manual Release Switch - Single Action | Nos. | 2 | 11000 | 22000 | 1000 | 2000 | 24000
| iv. | Horn / Strobe | Nos. | 1 | 37000 | 37000 | 2000 | 2000 | 39000
| v. | Alarm Bell | Nos. | 1 | 14500 | 14500 | 1000 | 1000 | 15500
5 |  | Warning Signs (For eg. "DO NOT ENTER", "MANUAL DISCHARGE STATION", "ROOM PROTECTED") | No. | 1 | 35000 | 35000 | 3000 | 3000 | 38000
6 |  | ACTUATION DEVICES
Supply & installation of actuation devices with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant.
| i. | Solenoid Actuator for the specified cylinder size | Nos. | 1 | 45000 | 45000 | 1000 | 1000 | 46000
| ii. | Manual Control Head for manual actuation of cylinder with safety pull pin | Nos. | 1 | 20000 | 20000 | 1000 | 1000 | 21000
| iii. | Pressure Switch to indicated system discharge with an external manual reset button | Nos. | 1 | 45000 | 45000 | 1000 | 1000 | 46000
| iv. | Low Pressure Switch to monitor the pressure within the cylinder | Nos. | 1 | 45000 | 45000 | 1000 | 1000 | 46000
| v. | Photo Electric Smoke Detector | Nos. | 2 | 35000 | 70000 | 2000 | 4000 | 74000
| vi. | Wire Base 4" Detector Base | Nos. | 2 | 23000 | 46000 | 2000 | 4000 | 50000
7 |  | WIRING
| i. | Supply & installation of wiring of 2C, 1.5 Sq.mm fire resistant shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia MS conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Job. | 1 | 40000 | 40000 | 20000 | 20000 | 60000
8 |  | Making of Shop drawings on Auto CAD 2018 with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects as per instruction of consultant. | Job. | 1 | 10000 | 10000 | 10000 | 10000 | 20000
9 |  | Painting, identification and tagging to the installations and equipments, complete in all respects as per instruction of consultant. | Job. | 1 | 15000 | 15000 | 15000 | 15000 | 30000
10 |  | Flushing of entire fire pipe work according to (NFPA-13), complete in all respects as per instruction of consultant. | Job. | 1 | 0 | 0 | 15000 | 15000 | 15000
11 |  | Testing and commissioning of entire fire fighting and clean agent for fire suppression system complete in all respects as per instruction of consultant. | Job. | 1 | 0 | 0 | 20000 | 20000 | 20000
|  | Total Cost of Novec System (with I.Tax) Rs. |  |  |  | 3984900 |  | 250000 | 4234900