## Summary
S.# | DESCRIPTION | SUPPLY (Rs.) | INSTALLATION (Rs.) | TOTAL (Rs.)
1 | SECTION - A WIRING & WIRING ACCESSORIES
2 | SECTION - B CABLE CONTAINMENT
3 | SECTION - C SWITCHES & SOCKETS
4 | SECTION - D MAIN / SUB-MAIN CABLES
5 | SECTION - E DISTRIBUTION BOARDS
6 | SECTION - F LIGHTING FIXTURES
7 | SECTION - G VOICE & DATA COMMUNICATION SYSTEM
8 | SECTION - H ADDRESSABLE FIRE ALARM SYSTEM
9 | SECTION - I CCTV SYSTEM
10 | SECTION - J ACCESS CONTROL SYSTEM
11 | SECTION - K INTELLIGENT LIGHTING CONTROL SYSTEM
12 | SECTION - L UNINTERRUPTIBLE POWER SUPPLY
13 | SECTION - M IMPORTED EARTHING / GROUNDING SYSTEM (FOR SERVER ROOM)
14 | SECTION - N BOARD ROOM AUTOMATION
15 | SECTION - O DISMANTTLING WORKS
16 | SECTION - P AS-BUILT DRAWINGS
Total Amount (Rs.)
Note: ● Contractor is advised to inform missing items (if any) in BOQ at time of submitting this tender. No escalation will be considered at time of execution of work. ● Owner can supply any material of Contractor scope at any stage and its cost will be completely deleted from Contractor scope without any kind of adjustment. ● Contractor should mark the selected brands and vendors in approved manufacturer list with submission of Tender Documents. ● Owner / Consultant have all the rights to select any brand / vendor from provided approved manufacturer list, Contractor shall not finalize any brand / vendor without written approval from consultant / owner.

## BoQ
S.# | DESCRIPTION | QTY | UNIT | SUPPLY |  | INSTALLATION |  | TOTAL (Rs.)
|  |  |  | RATE (Rs.) | AMOUNT (Rs.) | RATE (Rs.) | AMOUNT (Rs.)
SECTION - A WIRING & WIRING ACCESSORIES
Supply, Installation, Testing & Commissioning of the following items including all material, labour & tools required for completion of work as per item description, specifications & drawings including cutting, chiseling, making good and all necessary accessories such as bends, junction boxes, conduit sockets, earth connecting point connectors, etc. as shown on drawings, specifications and approval by the Engineer. Complete in all respects. Note: - The cost of wiring items shall include Imported Wago Connectors and Imported flexible Polyamide Conduit of appropriate size on each light point. - The circuit wire drop shall be sufficient as per ceiling levels. - The wiring shall be done with LSZH Wires / Cables. - Megger Test of each circuit to be done by the Contractor. - All General Wiring grade should be 450/750 copper with green/yellow Color.
- Surface conduiting wherever required shall be done in aesthetic manner. - Wherever the circuits are running in cable tray, it will enter / leave tray using proper glands / Junction boxes (IP44). The cost of all such accessories to be included in wiring cost. - All electrical circuits and power outlets shall be numbered (i.e. circuit number and distribution board number) and the circuit schedule of the distribution board must accurately reflect the installation. The load across all phases must be balanced. - The ECC to be run with each circuit shall be loop-in and loop-out type, joints are not allowed. It will be green in color (Refer detail BoQ & drawings) - All the cables shall be colour coded according to phases / types of services.
1 | Circuit wiring from DB to Switchboard including any wiring from switch board to switch board with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core PVC wires in 25mm dia PVC conduit as shown in drawings. | 10.5 | No
2 | Wiring for light point from Switchboard to first light point with phase 1.5 Sq.mm, common neutral 2.5 Sq.mm and common ECC 2.5 Sq.mm, 1-core PVC wires in 25mm dia PVC conduit as shown on drawings. | 108.15 | No
a | Point to Point wiring using the same wires size as mentioned in the above item. | 291.9 | No
3 | Circuit Wiring for Board Room light fixtures from DB-BR to first light point with 2x2.5 Sq.mm + ECC 1x2.5 Sq.mm 1-core PVC wires in 25mm dia PVC conduit as shown on drawings. | 25.2 | No
a | Point to Point wiring using the same wires size as mentioned in the above item. | 107.1 | No
4 | Circuit wiring from DB to PIR Sensor including wiring from PIR Sensor to Bypass Switch & Bypass Switch to PIR Sensor with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core Cu/LSZH wires in 25mm dia Anodized Aluminum EMT Conduit as shown in drawings. | 13.65 | No
5 | Emergency Circuit wiring from DB to Switchboard including any wiring from switch board to switch board with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core PVC wires in 25mm dia PVC conduit as shown in drawings. | 6.3 | No
6 | Emergency Wiring for light point from Switchboard to first light point with phase 1.5 Sq.mm, common neutral 2.5 Sq.mm and common ECC 2.5 Sq.mm, 1-core PVC wires in 25mm dia PVC conduit as shown on drawings. | 33.6 | No
a | Point to Point wiring using the same wires size as mentioned in the above item. | 22.05 | No
7 | Circuit Wiring of 13A/15A Switch Socket units (RAW Power) from DB to first outlet including wiring within the same technology box / cable cubby / adjacent power outlets in separate back boxes with following size of 1-core PVC wires in 25mm dia PVC conduit under-floor/wall as shown in the drawings.
a | 2 x 4 Sq.mm + ECC 1 x 4 Sq.mm | 22.05 | No
b | Outlet to Outlet wiring using the same wires & conduit size as mentioned in the above item. | 96.6 | No
8 | Circuit Wiring of 13A/15A Switch Socket units (UPS Power) from DB to first outlet including wiring within the same technology box / cable cubby / adjacent power outlets in separate back boxes with following size of 1-core PVC wires in 25mm dia PVC conduit under-floor/wall as shown in the drawings.
a | 2 x 4 Sq.mm + ECC 1 x 4 Sq.mm | 12.6 | No
b | Outlet to Outlet wiring using the same wires & conduit size as mentioned in the above item. | 115.5 | No
9 | Circuit Wiring for Hand Dryers from DB to 20A DP Switch with 3 x 4 Sqmm Cu/PVC size of 1-core PVC wires in 25mm dia PVC conduit underfloor/wall, as shown in the drawings. | 3.15 | No
10 | Emergency Circuit Wiring for DB-BR from UDB with 3C-4 Sqmm Cu/PVC size cable in 25mm dia PVC conduit via already laid cable tray, as shown in the drawings. | 2.1 | No
11 | Emergency Circuit Wiring for Access Control System from DB to DP Switch for Controller with 3 x 2.5 Sqmm Cu/PVC size of 1-core PVC wires in already laid PVC conduit via already laid cable tray, as shown in the drawings. | 1.05 | No
a | Controller to Controller using the same wires as mentioned in the above item. | 3.15 | No
12 | Emergency Circuit Wiring for Access Control System from DB to Power Supply with 3 x 2.5 Sqmm Cu/PVC size of 1-core PVC wires in already laid PVC conduit via already laid cable tray, as shown in the drawings. | 4.2 | No
a | Power Supply to Power Supply using the same wires as mentioned in the above item. | 5.25 | No
13 | Emergency Circuit Wiring for Fire Alarm Control Panel from DB to FACP with 2C-2.5 Sqmm Cu/PVC size wires in already laid PVC conduit via already laid cable tray, as shown in the drawings. | 1.05 | No
14 | Circuit Wiring for Ceiling/Wall Mounted AC Equipments from DB to 20A DP Switch/Isolator with 3C-4 Sqmm Cu/PVC/PVC size of wires in already laid PVC conduit via already laid cable tray, as shown in the drawings. | 25.2 | No
a | Outlet to Outlet wiring using the same wires size as mentioned in the above item. | 24.15 | No
15 | Circuit Wiring for VRF Outdoor Units from MCC to 40A 4P Isolator with 4C-10 Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC size of wires in already laid PVC conduit via already laid cable tray, as shown in the drawings. | 2.1 | No
16 | Circuit Wiring for VRF Outdoor Units from MCC to 32A 4P Isolator with 4C-6 Sqmm Cu/PVC/PVC + ECC 1C-6 Sqmm Cu/PVC size of wires in already laid PVC conduit via already laid cable tray, as shown in the drawings. | 3.15 | No
17 | Circuit Wiring for Exhaust Air Fan from MCC to 20A 4P Isolator with 4C-4 Sqmm Cu/PVC/PVC + ECC 1C-4 Sqmm Cu/PVC size of wires in already laid PVC conduit via already laid cable tray, as shown in the drawings. | 2.1 | No
Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY)
SECTION - B CABLE CONTAINMENT
1 | Supply & Laying of the following sizes of PVC/UPVC/EMT Conduits including all accessories such as bends, sockets, j-boxes, flexible conduits, metal saddles e.t.c as per design drawings, complete in all respect. Provide Pull boxes where ever required.
a | 25mm dia PVC Conduit | 750 | Rm
b | 32mm dia PVC Conduit | 100 | Rm
c | 38mm dia PVC Conduit | 350 | Rm
d | 25mm dia Imported Flexible Polyamide Conduit with PVC Gland / Adapter | 250 | Rm
2 | Supply & Installation of following G.I 16 SWG Ceiling / Floor / Wall Pull Boxes for data / voice / power / UPS circuits, recessed on wall or column as per design drawings. Complete in all respect.
a | 200mm x 200mm x 50mm | 20 | No.
b | 300mm x 300mm x 50mm | 20 | No.
3 | Supply & Installation of 16 SWG MS Sheet Steel Back Boxes for installation of Switches, Sockets, Voice & Data Outlets, Isolators as per drawings and details including all accessories. | 400 | No.
4 | Supply and Installation of following sizes of GI 16 SWG Perforated Cable Tray with 18 SWG Cover (4 feet covers) duly Painted after degreesing, derusting, phosphating and antirust primer complete in all respect with supporting hangers, brackets, elbows, tee & mounting accessories etc. Note: - Color Printed Tags to be provided at every 3 Meter Length. - Threaded Rods & Base Plate to be used for hanging from ceiling. - Wall Hanger Supports to be provided moving with walls. - U-shaped fischer plates to be used for joints. - Earth bonding to be done with every joint. - Color to be decided with consent of architect. - Imported mounting accessories to be used make mungo or fischer.
a | 300mm x 50mm Horizontal With Ceiling Mounted Hanging Accessories | 175 | Rm.
5 | Supply & Installation of 14-SWG Anodized Linear Aluminum Channel with 14-SWG cover in the following sizes, including all installation accessories such as angle iron mounting brackets (red oxide coated), bends, tees, rawal bolts e.t.c. Complete in all respect.
a | 100mm x 50mm | 69.75 | Rm.
6 | Supply & Installation of Linear Outlet Boxes without face plates made of Aluminum, mounted on wall or punched in furniture as per design drawings. The linear outlet boxes are to be provided with appropriate sizes of knockouts. Refer Detail Drawings.
a | Type-A: (LxHxD in mm=470x125x50) 1 No. 13A International Simplex Switch Socket Outlet with USB Port & C-Type Charging Port on RAW Power 1 No. 13A International Simplex Switch Socket Outlet on UPS Power 1 No. CAT-6 RJ-45 Duplex Outlet for Data 2 No. CAT-6 RJ-45 Duplex Outlet for Voice | 1 | No.
b | Type-A': (LxHxD in mm=310x125x50) 3 No. 13A International Simplex Switch Socket Outlet on UPS Power | 1 | No.
c | Type-A":(LxHxD in mm=470x125x50) 2 No. 13A International Simplex Switch Socket Outlet with USB Port & C-Type Charging Port on RAW Power 3 No. 13A International Simplex Switch Socket Outlet on UPS Power | 1 | No.
d | Type-B: (LxHxD in mm=550x125x50) 2 No. 13A International Simplex Switch Socket Outlet with USB Port & C-Type Charging Port on RAW Power 2 No. 13A International Simplex Switch Socket Outlet on UPS Power 1 No. CAT-6 RJ-45 Duplex Outlet for Data 1 No. CAT-6 RJ-45 Simplex Outlet for Voice | 4 | No.
e | Type-D: (LxHxD in mm=470x125x50) 4 No. 13A International Simplex Switch Socket Outlet on UPS Power 1 No. CAT-6 RJ-45 Duplex Outlet for Data/Voice | 4 | No.
f | Type-D': (LxHxD in mm=470x125x50) 1 No. 13A International Simplex Switch Socket Outlet with USB Port & C-Type Charging Port on RAW Power 3 No. 13A International Simplex Switch Socket Outlet on UPS Power 1 No. CAT-6 RJ-45 Duplex Outlet for Data/Voice | 4 | No.
g | Type-F: (LxHxD in mm=390x125x50) 1 No. 13A International Simplex Switch Socket Outlet with USB Port & C-Type Charging Port on RAW Power 2 No. 13A International Simplex Switch Socket Outlet on UPS Power 1 No. CAT-6 RJ-45 Duplex Outlet for Data/Voice | 4 | No.
h | Type-G: (LxHxD in mm=550x125x50) 1 No. 13A International Simplex Switch Socket Outlet with USB Port & C-Type Charging Port on RAW Power 3 No. 13A International Simplex Switch Socket Outlet on UPS Power 2 No. CAT-6 RJ-45 Duplex Outlet for Data/Voice | 2 | No.
i | Type-H: (LxHxD in mm=470x125x50) 2 No. 13A International Simplex Switch Socket Outlet with USB Port & C-Type Charging Port on RAW Power 1 No. 13A International Simplex Switch Socket Outlet on UPS Power 2 No. CAT-6 RJ-45 Duplex Outlet for Data/Voice | 2 | No.
6 | Supply & Installation of Linear Cable Cubbies with the specified outlets & face plates, to be punched in furniture as shown in design drawings, complete in all respects.
a | Type-C: 2 No. 13A International Simplex Switch Socket Outlet on RAW Power 1 No. CAT-6 RJ-45 Duplex Outlet for Data/Voice 1 No. USB Port 1 No. Type-C Charging Port | 46.2 | No.
b | Type-E: 2 No. 13A International Simplex Switch Socket Outlet on RAW Power 1 No. CAT-6 RJ-45 Duplex Outlet for Data 1 No. CAT-6 RJ-45 Simplex Outlet for Voice 1 No. USB Port 1 No. Type-C Charging Port | 5.5 | No.
7 | Supply & Installation of Imported Floor Outlet Boxes without face plates made of 16 SWG G.I Sheet, recessed in ground as per design drawings. | 1 | No.
Note: Contractor is advised to confirm the sizes, running lengths and termination as per site conditions before commencement of work. All the conduits / cable tray crossings through partition walls shall be properly sealed by fire retardant material after installation.
Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY)
SECTION - C SWITCHES & SOCKETS
Supply & Installation of the following ratings of Light Switches, Power Outlets, DP Switches, Isolators, Industrial Sockets in already installed 16 SWG sheet steel back boxes to be recessed in wall / installed on surface, as shown in drawings, complete in all respect. (Clipsal Pieno for Light Switches & Vivace for Power Sockets or equivalent) (Scame / Legrand or equivalent, for Isolators)
1 | 16A, One Gang Light Switch | 38.85 | No
2 | 16A, Two Gang Light Switch | 2.1 | No
3 | 16A, Three Gang Light Switch | 15.75 | No
4 | 16A, Four Gang Light Switch | 11.55 | No
5 | One Gang ByPass Switch | 13.65 | No
6 | 13A, Flat Pin Simplex Socket Unit | 110.25 | No
7 | 13A, Flat Pin Duplex Socket Unit | 1.05 | No
8 | 13A, International Switch Socket Unit | 111.3 | No
9 | 13A, International Switch Socket Unit with USB Port & Type-C Charging Port | 26.25 | No
10 | 15A 3-Pin Round Switch Socket unit | 2.1 | No
11 | 20A DP Switch (Hand Dryers/Floor Mounted AC/Split AC) | 54.6 | No
12 | 20A 4P Isolator | 2.1 | No
13 | 32A 4P Isolator | 3.15 | No
14 | 40A 4P Isolator | 2.1 | No
15 | 32A 5-Pin (Three Phase) Industrial Socket with Plug, in IP-Rated Enclosure (For UPS) | 1 | No
16 | 40A 3-Pin (Single Phase) Industrial Socket with Plug, in IP-Rated Enclosure (For UPS) | 1 | No
17 | 20A 3-Pin (Single Phase) Industrial Socket with Plug, in IP-Rated Enclosure (For UPS) | 2 | No
18 | HDMI Outlets | 1 | No |  | Rate Only |  | Rate Only | Rate Only
Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY)
SECTION - D MAIN / SUB-MAIN CABLES
Supply, Laying, Termination, Testing & Commissioning of the following ratings of LV Cables along with complete installation and termination accessories to be laid in already installed Cable trench / Cable ladder / Cable tray / Duct Bank including all accessories. Complete in all respects. -Imported Lugs and Connectors shall be used in LV Cables. -Manual crimping of lugs is not allowed. Proper lug presser for smaller lugs and hydraulic lug presser for large size lugs should be used.
1 | From MDB-7TH to LPDB-7TH FLOOR 4C-25 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 15 | Rm.
2 | From MDB to UDB-7TH FLOOR 4C-6 Sqmm Cu/PVC/PVC + ECC 1C-6 Sqmm Cu/PVC | 25 | Rm.
3 | From UDB to 32A 5-Pin Industrial Socket and Industrial Socket to UPS 4C-6 Sqmm Cu/PVC/PVC + ECC 1C-6 Sqmm Cu/PVC | 10 | Rm.
4 | From UPS to 40A 3-Pin Industrial Socket and Industrial Socket to UDB 2C-10 Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 10 | Rm.
5 | From UDB to 20A 3-Pin Industrial Socket and Industrial Socket to UPS 2C-6 Sqmm Cu/PVC/PVC + ECC 1C-6 Sqmm Cu/PVC | 10 | Rm.
6 | From UPS to 20A 3-Pin Industrial Socket and Industrial Socket to UDB 2C-6 Sqmm Cu/PVC/PVC + ECC 1C-6 Sqmm Cu/PVC | 10 | Rm.
7 | Testing and submission of Reports of Existing cables
a | 4C-120 Sq.mm Cu/PVC | 1 | Job
b | 4C-95 Sq. mm Cu/PVC | 1 | Job
Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY)
SECTION - E DISTRIBUTION BOARDS
Supply, Installation, Testing & Commissioning of the following Distribution Boards made with 14/16 SWG Sheet Steel Enclosure including all installation accessories such as Rawal bolt etc. Complete in all respects. Note: - All the DBs should be front accessible and maintainable. - Cost of Lighting Control Relays & Power Supplies should be Included. - The transportation and placement of DBs upto dedicated location is included, complete in all respects including levelling, grouting etc. - Laser engraved tags required as mention in SLDs - Space for circuit tagging required with permanent installation on protective sheet via rivets - 20% space required in DB for future provision - Tin platted Imported Cu bus bar with heat shrink color coded sleeves to be used. - Hindged protective metallic door is required with knob/handle. - Braided Door earth required. - Lockable handle required for main door. - As-built drawing pocket. - Cable hanging arrangement. Minimum One Year Warranty Required from date of successful comissioning on site.
1 | Modifications in existing MDB-7th Floor, including following but not limited to: a) Dismantling of Existing MCB circuit breakers. b) Rectification of any of the fauslty component including multimeter, indication lights etc. c) Addition of proper cable termination tinned copper links in existing 100A circuit brekaer of MCC. d) Swapping of 02 No. Circuit breaker from one bus to another. This job also includes internal wiring modification. e) Dressing, tagging of all circuit breakers and cables Complete in all respect. | 1 | Job
2 | LPDB-7TH FLOOR | 1 | No.
3 | UDB-7TH FLOOR | 1 | No.
4 | MCC-HVAC-7TH FLOOR | 1 | No.
Total Amount (Rs.) Sec - E (CARRIED FORWARD TO SUMMARY)
SECTION - F LIGHTING FIXTURES
Supply, Installation, Testing & Commissioning of the following Light fixtures, complete with ballast, starter p.f.i capacitor and specified lamps and Installation Accessories. Note: - Color temperature will be as per Architect's requirement. - Efficacy of light fixtures shall be equal to or more than 105 Lumens / Watt. - 3 Year Replacement Warranty is required both for fixture and driver. - Power Factory shall be 0.9. - Minimum Operational life should be more than 50,000 Hours @L70 Rated - All External Lights should be IP-65 Rated. - The price of external outdoor box & drivers shall also be included.
1 | Recessed Type Clear Glass Light Fixture with 15W LED, Die-Cast Aluminum Housing, Color 4000K, as approved by the Architect | 114.45 | No.
2 | Recessed Type Clear Glass Downlight, builtin Aluminum Profile with 10W LED, Color 4000K, as approved by Architect | 7.35 | No.
3 | Recessed Type Clear Glass Adjustable Spot Light Fixture with 7W LED, Die-Cast Aluminum Housing, Color 4000K, as approved by the Architect | 68.25 | No.
4 | Recessed Type Clear Glass Adjustable Spot Light Fixture with 5W LED and dimable driver, Color 4000K, as approved by the Architect | 94.5 | No.
5 | Recessed Type DownLight Fixture with 20W LED, Die-Cast Aluminum Housing, Color 4000K, as approved by the Architect | 24.15 | No.
6 | Recessed Type DownLight Fixture with 10W LED, Die-Cast Aluminum Housing, Color 4000K, as approved by the Architect | 25.2 | No.
7 | Wall Mounted 9W LED Up/Down Light Fixture, Color 4000K, as approved by the Architect | 2.1 | No.
8 | LED Rope Light with Highly Transparent Sillicon cover, 7.5W/M, Color 4000K, High Brightness, with Driver & Mounting Accessories | 69.54 | Rm.
9 | Recessed Type Linear Light Fixture 4' with 40W LED | 7.35 | No.
10 | 2ft Batten Light Fixture with 9W, color 4000K, as approved by the Architect | 125.28 | No.
11 | Slim Aluminium Profile Linear Led Light Fixtures with diffused cover and power supply with 9W LED chip, color 4000K, as approved by the Architect | 4.4 | No.
12 | Suspended Type Linear Light Fixture with 18W/M LED, Die-Cast Aluminum Housing, Color 4000K, as approved by the Architect | 39.9 | Rm.
13 | Decorative Pendant Type Suspended Light Fixtures (Type-A,B,C,D) with LEDs, shall be as per specs provided by the architect. | 25 | No.
14 | Decorative Linear Type Suspended Light Fixture with LEDs and dimable driver, shall be as per specs provided by the architect. | 10 | No.
15 | Decorative Chandlier Suspended Light Fixtures with LEDs, shall be as per specs provided by the architect. | 1 | No.
16 | Supply & Installation of 220V Operative Stand Alone Occupancy Sensor | 13.65 | No.
Total Amount (Rs.) Sec - F (CARRIED FORWARD TO SUMMARY)
SECTION - G VOICE & DATA COMMUNICATION SYSTEM
Supply, Laying, Installation, Termination, Testing & Commissioning of following items for voice and data communication system including all material, labor, tools, accessories etc. Complete in all respects. (C-Vivace Series to be quoted) Note: - Different colors of voice and data cables shall be used. - Cable lengths will be verified by Fluke Test and exact length shall reflect the Measurement Sheet/ Bill issued by the contractor. - Cables left for terminating with Patch Panels shall not exceed the required length. Leaving of Unnecessary Excessive lengths shall be avoided. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
1 | Simplex Face plate with 1 No. CAT-6 RJ-45 I/O for Data Communication in white / off white finish, complete with shuttered click-ins, labels and all accessories. Complete in all respects. | 22.8 | No
2 | Simplex Face plate with 1 No. CAT-6 RJ-45 I/O for WIFI Communication in white / off white finish, complete with shuttered click-ins, labels and all accessories. Complete in all respects. | 10.8 | No
3 | Simplex Face plate with 1 No. CAT-6 RJ-45 I/O for Voice Communication in white / off white finish, complete with shuttered click-ins, labels and all accessories. Complete in all respects. | 10.8 | No
4 | Simplex Face plate with 1 No. CAT-6 RJ-45 I/O for CCTV Communication in white / off white finish, complete with shuttered click-ins, labels and all accessories. Complete in all respects. | 27.6 | No
5 | Duplex Face plate with 2 No. CAT-6 RJ-45 I/O for Data Communication in white / off white finish, complete with shuttered click-ins, labels and all accessories. Complete in all respects. | 6 | No
6 | Duplex Face plate with 2 No. CAT-6 RJ-45 I/O for Voice Communication in white / off white finish, complete with shuttered click-ins, labels and all accessories. Complete in all respects. | 2.4 | No
7 | Duplex Face plate with 2 No. CAT-6 RJ-45 I/O for Data/Voice Communication in white / off white finish, complete with shuttered click-ins, labels and all accessories. Complete in all respects. | 24 | No
8 | Simplex Face plate with 1 No. Coaxial Outlet for TV in white / off white finish, complete with labels and all accessories. Complete in all respects. | 14.4 | No
9 | CAT-6 UTP Cables for Data from Communication Rack to each outlet in already laid PVC conduit as per drawings including termination and tagging at both ends. Complete in all respects. (Coil =305 Rm.) Note: Different Color of Wires shall be provided for IT services | 15 | Coil
10 | CAT-6 UTP Cables for Voice from Communication Rack to each outlet in already laid PVC conduit as per drawings including termination and tagging at both ends. Complete in all respects. (Coil =305 Rm.) Note: Different Color of Wires shall be provided for IT services | 12 | Coil
11 | CAT-6 UTP Cables for WIFI Communication from Communication Rack to each outlet in already laid PVC conduit and cable tray as per drawings including termination and tagging at both ends. Complete in all respects. (Coil =305 Rm.) Note: Different Color of Wires shall be provided for IT services | 1 | Coil
12 | RG-6 Cable for CATV System from Communication Rack to each T.V point in 25mm dia PVC conduit via cable tray as per drawings including terminations. Complete in all respect. | 129.6 | Rm.
13 | 15meter long High Speed HDMI cable, must be LLC Certified of any approved European brand in appropriate size of PVC conduit as shown in the drawings, complete with termination at both ends including connectors. Complete in all respects. | 12 | No.
14 | Following Patch Panels equipped with RJ-45 I/Os including all labeling and all mounting accessories. Complete in all respects.
a | 24-Port CAT-6 Patch Panel (Data, Voice & WIFI) | 9 | No
15 | Front Cable Organizer for patch panels / wiring blocks with complete labeling and dressing for incoming cable management. | 9 | No
16 | Following factory certified Patch Cords of specified color having RJ-45 connectors at both ends.
17 | 1 meter long RJ-45 CAT-6 Patch Cord | 201.6 | No
b | 3 meter long RJ-45 CAT-6 Patch Cord | 117.6 | No
18 | Following factory certified Patch Cords of specified color having RJ-11 connectors
b | 3 meter long RJ-11 CAT-6 Patch Cord | 84 | No
19 | 6 Core, Multi Mode OM3 Fiber Optic Cable including termination as per standard specifications, all termination accessories up to entire satisfaction of IT Engineer, in appropriate size PVC conduit / cable tray including testing. | 1 | Rm. |  | Rate Only |  | Rate Only | Rate Only
20 | Termination and Splicing of 6 Core, Multi Mode Fiber Optic Cable, including as per standard specifications, all termination accessories and testing up to entire satisfaction of IT Engineer, Complet in all respect. | 1 | Job
21 | Testing and Commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client
a | Fluke Testing of all CAT-6 cables with calibrated fluke tester | 1 | Job
b | Power Meter and Light Source Testing of all the laid fiber cables shall be included in the scope of works | 1 | Job
Note: Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - G (CARRIED FORWARD TO SUMMARY)
SECTION - H ADDRESSABLE FIRE ALARM SYSTEM
Supply, Installation, Testing & Commissioning of Addressable Fire Alarm System in compliance with comprising of following equipments including all accessories required for the completion of the system in all respects. Note: - Minimum 3 Years Warranty is required - Existing Fire Alarm Control System brand is of GST
1 | Dismantlling and Re-Installation of Existing Addressable Fire Alarm Control Panel of 1 Loops including programming testing & commisioning, Complet in all respect. | 1 | Job | - | -
2 | Addressable Smoke Detectors incorporating a pulsing LED located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 34 | No
3 | Addressable Heat Detectors incorporating a pulsing LED located in labyrinth with in the housing of the detector. Sensing of the detector shall be adjustable via software between 0-90 seconds. The detector shall have built in short circuit isolators on both inputs. | 3 | No
4 | Addressable Indoor Loop Powered electronic Sounder with flasher, having minimum sound output 100 dB at 1 meter with frequencies for variety of sounds as required. Sounder shall be loop wired and loop signaled , built in short circuit isolator, shall have feature to configured via software. | 6 | No
5 | Addressable Resetable Break Glass Type Manual Call Point with Cover having a built in short circuit isolators on both inputs with isolation base and built in microprocessor to ensure a response time of max 1 second. It also incorporates an indication LED, flashed after pressing the button to acknowledge the activation and a key operation facility for testing purposes. | 5 | No
6 | 2C, 1.5 Sq.mm Fire Resistant Shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia PVC Conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respect. (Prysmian FP-200 Gold or Equivalent) | 344.4 | Rm.
7 | 2C, 1.5 Sq.mm Fire Resistant Shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia PVC Conduit from new FACP to existing FACP including all installation accessories complete in all respect. (Prysmian FP-200 Gold or Equivalent) | 24 | Rm.
8 | I/O Module for Integration of FACP with 04 No. 04 Door Access Control System including wiring, testing and commissioning, Complete in all respect | 1 | Job
9 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
10 | Allow for any other item required for completion of system not covered in BOQ or specifications / drawings in accordance with the same standards and brands shown and approved by consultant. All such items shall be covered in this item but complete description, item rates, quantity required and brands shall be mentioned separately and to be attached with the BOQ. | 1 | Job
Note: - Contractor shall provide the complete Technical Literature for the offered system. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - H (CARRIED FORWARD TO SUMMARY)
SECTION - I CCTV SYSTEM
Supply, Installation, Testing, Commissioning of the following items for IP Based (Modbus IP Compatible) CCTV System including but not limited to the description given here under including all power and communication accessories, housings, mounting brackets, suspension rods etc. required for completion of the system.
1 | Following Patch Panels equipped with RJ-45 I/Os including all labeling and all mounting accessories. Complete in all respects.
a | 24-Port CAT-6 Patch Panel | 1 | No
2 | Front Cable Organizer for patch panels / wiring blocks with complete labeling and dressing for incoming cable management. | 1 | No
3 | Following factory certified Patch Cords of specified color having RJ-45 connectors at both ends.
a | 1 meter long CAT-6 Patch Cord | 24 | No
b | 3 meter long CAT-6 Patch Cord | 18 | No
4 | CAT-6 UTP Cables for CCTV Communication from Communication Rack to each outlet in already laid PVC conduit via already laid cable tray as per drawings including termination and tagging at both ends. Complete in all respects. (Coil =305 Rm.) | 3 | Coils
5 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client
a | Fluke Testing of all CAT-6 cables with calibrated fluke tester | 1 | Job
b | Power Meter and Light Source Testing of all the laid fiber cables shall be included in the scope of works | 1 | Job
6 | Allow for any other item required for completion of system not covered in BOQ or specifications / drawings in accordance with the same standards and brands shown and approved by consultant. All such items shall be covered in this item but complete description, item rates, quantity required and brands shall be mentioned separately and to be attached with the BOQ. | 1 | Job
Note: - Contractor shall provide the complete Technical Literature for the offered system. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - I (CARRIED FORWARD TO SUMMARY)
SECTION - J ACCESS CONTROL SYSTEM
Supply, Installation, Testing & Commissioning of following items for Access Control System (with features of Bio Metric & RFID) as described below including all accessories. Complete with mounting brackets, wiring, adapters etc. Note: - Minimum 3 Years Warranty is required
1 | Door Access Controller suitable for 4 door / 4 readers for door access (connecting to readers at upto 100m), monitoring, store at least 10,000 events, provided with power supply unit with battery back-up for at-least 24 hours. Built-in interfacing with TCP / IP switch for LAN/WAN networking and telephone dialer. | 4 | No.
2 | Proximity Card Reader 125KHz, reading range 6", operating at low voltage DC supply, with mounting base suitable for interior and exterior environment with dual color LED and speaker for comprehensive audible feed back to user. | 9 | No.
3 | Power Supply Units for push buttons complete in all respects. | 9 | No.
4 | Proximity RFID Cards standard size and thickness, thin, flexible polyvinyl chloride laminated, passive type, easy printable on both sides. | 9 | No.
5 | Magnetic Lock 600Lbs (Single Door) with holder and fixing accessories. | 6 | No.
6 | Magnetic Lock 600Lbs (Double Door) with holder and fixing accessories. | 3 | No.
7 | Push Button (Exit Switch) suitable for installation on BS standard size back box connected to door controller for access. | 9 | No.
8 | Access Control and Time Management Software along with Security Control system features a password protected user logon system suitable to interface with CCTV, Public Address and Fire Alarm. It provide cardholder management, full alarm and event processing, multi division supports, alarms alerting via SMS and calls on mobile and detailed audit rail records. | 1 | No.
9 | CAT-6 UTP Cables for Access Control System from Comm. Rack to each device in already laid PVC Conduit via already installed cable tray as per drawings including termination and tagging at both ends. Complete in all respects. (Coil =305 Rm.) | 3 | Coils
10 | Supply, laying and termination of 5-Pair Cable for Security System from Server Room to each gates as mentioned below, as per standard specifications, all termination accessories as per instructions of supplier / vendor and client representative, in already laid PVC conduit / cable tray including testing. Complete in all respects. a) 02 No. Main Entrance Doors b) 02 No. Emergency Exit Doors c) 02 No. Numeric Pad in Reception Area | 1 | Job
11 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
12 | Allow for any other item required for completion of system not covered in BOQ or specifications / drawings in accordance with the same standards and brands shown and approved by consultant. All such items shall be covered in this item but complete description, item rates, quantity required and brands shall be mentioned separately and to be attached with the BOQ. | 1 | Job
Note: - Contractor shall provide the complete Technical Literature for the offered system. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - J (CARRIED FORWARD TO SUMMARY)
SECTION - K INTELLIGENT LIGHTING CONTROL SYSTEM
Supply, Installation, Testing & Commissioning of following items for complete Lighting Control System (KNX Based) including all labour, tools etc. Complete in all respect as shown on drawing.
1 | 86mm x 86mm" Granite Display Color Touch Panel > Built-in temperature and humidity sensor, proximity sensor > Adjustable LCD backlight brightness > Buspro voltage detection supported > Time and environment status display and setting | 1 | No.
2 | KNX Control Cable for system wiring from Relay to Lighting control switches and other devices in already installed conduit via cable tray as shown in the drawings. Complete in all respects. (KNX Approved Cable) | 75 | Rm.
3 | Programming, testing and commissioning of complete system upto the entire satisfaction of client and consultant including following: - Intelligent Lighting Control System Schedule (Software + Manual) - Documentation - Web based featuring an extensive schedule Program - Manual Setting in DB with accessories and tagging | 1 | Job
Note: - Contractor shall provide complete technical literature for the quoted equipment for approval of Consultant before procurement. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - K (CARRIED FORWARD TO SUMMARY)
SECTION - L UNINTERRUPTIBLE POWER SUPPLY
Supply, Installation, Testing, Commissioning and top supervision of following UPS at site as per following specifications, Complete in all respect.
1 | Rating : 6 kVA True Online Double Conversion Pure sine wave Microcontroller based. Input voltage: 415V AC Input frequency: 50 Hz Output voltage: 220 Volts Three Phase IN & Single Phase Out Output p.f: 0.9 (Built in PFC) Effiiceincy: 92 to 96% Backup Time: 10 mins at full load. Batteries: Dry Sealed Maintenance Free Overload: 110% for 10min Capacity: 125% for 1-min Operating Temp: 0 to 40 degC Mounting: Floor Mounted Warranty: 1 Years for UPS & Batteries User friendly LCD display for real time UPS status Cold start of load during power failure Transient/Surge Suppressor EMI/RFI Filter Built-in manual and static by-pass switch Remote & local emergency power off function RS-232/RJ-45 connectivity with power management software Provision for external battery bank UPS & Advance Automatic Battery Management system for temperature compensated battery charging and battery testing on user defined time. Power Chute Network Shutdown. SNMP Management Card / Modbus Card | 1 | No |  | Rate Only |  | Rate Only | Rate Only
2 | Rating : 3 kVA True Online Double Conversion Pure sine wave Microcontroller based. Input voltage: 220V AC Input frequency: 50 Hz Output voltage: 220 Volts Single Phase IN & Single Phase Out Output p.f: 0.9 (Built in PFC) Effiiceincy: 92 to 96% Backup Time: 10 mins at full load. Batteries: Dry Sealed Maintenance Free Overload: 110% for 10min Capacity: 125% for 1-min Operating Temp: 0 to 40 degC Mounting: Floor Mounted Warranty: 1 Years for UPS & Batteries User friendly LCD display for real time UPS status Cold start of load during power failure Transient/Surge Suppressor EMI/RFI Filter Built-in manual and static by-pass switch Remote & local emergency power off function RS-232/RJ-45 connectivity with power management software Provision for external battery bank UPS & Advance Automatic Battery Management system for temperature compensated battery charging and battery testing on user defined time. Power Chute Network Shutdown. SNMP Management Card / Modbus Card | 1 | No
Note: - Contractor shall provide complete technical literature for the quoted equipment for approval of Consultant before procurement.
Total Amount (Rs.) Sec - L (CARRIED FORWARD TO SUMMARY)
SECTION - M IMPORTED EARTHING / GROUNDING SYSTEM (FOR SERVER ROOM)
Supply, installation, testing and commissioning of following imported items for Earthing / Grounding System for lightning protection and grounding of other systems including all material, boring, labor, tools, transportation, all accessories etc. Complete in all respects as per drawing and specification with detailed test reports.
1 | Chemical Enhanced Earth using 38 mm dia copper pipe filled with soil conditioning material including 6" dia, 11' deep boring and back filled chemical to enhance conductivity. Complete with termination clamps, 12" dia heavy duty tin plated round cover as per details given in drawings. (Imported Chemical to be Used, 2 Bags in 1 Pit) | 2 | No.
2 | Earth Connecting Point (ECP) or Equipotential bar made with 200 mm wide, 75 mm high and 5 mm thick tin plated Copper, as shown in drawings. Bar shall be provided with holes suitable for installation of 4 No. 35 sqmm bare copper conductor. ECP shall be enclosed in appropriate size of powder coated metal enclosure with front accessible cover. | 1 | No.
3 | Supply, installation, testing & commissioning of following size of single core PVC cables in 32mm dia UPVC Class-B conduit laid in floor including core cutting in floors from Ground floor Earth Station to ECP and exposed conduit run on horizontal ceiling slab and vertical riser from at 3rd Floor to Server Room ECP and ECP to Racks as per details given below, including all material, labor, tools, transportation, accessories etc. Complete in all respects with detailed test reports.
a | 2 No. 1C-16 Sqmm Cu/PVC in 32mm dia PVC Conduit | 150 | Rm.
Note: Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - M (CARRIED FORWARD TO SUMMARY)
SECTION - N BOARD ROOM AUTOMATION
Supply, Installation, Testing & Commissioning of the following items for Automation of Board Room, complete in all respects.
Audio Video Conference System
1 | Dismantling and Re-Installation of Client Provided Complete Audio Video Conference system in Board Room including back-pulling and re-laying of client provided wiring as per standard specifications, all termination accessories and testing up to entire satisfaction of Cleient Engineer, Complet in all respect. | 2 | Jobs
Automation System
2 | 4 Channel IR Emitter > 1) 2-pin 3.5mm detachable terminal block for connection to a Crestron IR port > Black injection molded plastic with integral lightweight cable > The IRP2 connects to any Crestron control system with a 2-pin terminal block type Crestron IR port, providing a 1-way IR control interface to the device | 2 | No.
3 | 86mm x 86mm" Granite Display Color Touch Panel > Built-in temperature and humidity sensor, proximity sensor > Adjustable LCD backlight brightness > Buspro voltage detection supported > Time and environment status display and setting | 2 | No.
4 | DB-BOARDROOM RIGHT WING (with Relay, Dimmer, Curtain Control & Power Supply) (Refer attached SLD) | 1 | No.
5 | DB-BOARDROOM LEFT WING (with Relay, Dimmer, Curtain Control & Power Supply) (Refer attached SLD) | 1 | No.
6 | CAT-6 UTP Cables for IR Emitter from Devices/Equipment to IR Emitter and IR Emitter to Touch screen in 25 mm dia PVC Conduit as per drawings including termination and tagging at both ends. Complete in all respects. | 150 | Rm.
Note: - Contractor shall provide complete technical literature for the quoted equipment for approval of Consultant before procurement. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - N (CARRIED FORWARD TO SUMMARY)
SECTION - O DISMANTTLING WORKS
Dismantling and Disconnection of Existing Electrical & Allied accessories without damaing, including packing and labeling of all the dismantled items, transporation to the designated location and handing over to the client. Complete in all respect
1 | Dismanttling of all Electrical and allied works including wiring, containment and fixtures Distribution boards, Complete in all respect. Except wiring and containment shown in drawing. | 1 | Job
Total Amount (Rs.) Sec - O (CARRIED FORWARD TO SUMMARY)
SECTION - P AS-BUILT DRAWINGS
1 | Preparation & Submission of Shop Draing and As-Built drawings for all electrical and allied works after getting final approval from the Client/Consultant. Note: 2 sets of as-built drawings after work completion of each floor, and 3 sets with a soft copy of complete electrical works after final commissioning of project to be submitted. Approval of bills are subject to the completion of as built drawings upto the entire satisfaction of site engineer. | 1 | Job
Total Amount (Rs.) Sec - P (CARRIED FORWARD TO SUMMARY)