## Summary
S.# | ITEM DESCRIPTION | SUPPLY (Rs.) | INSTALLATION (Rs.) | TOTAL (Rs.)
1 | SECTION - A GENERAL REQUIREMENTS FOR HVAC SYSTEM
2 | SECTION - B OPERATION & MAINTENANCE FOR HVAC SYSTEM
3 | SECTION - C COMMON WORKS RESULTS FOR HVAC SYSTEM
4 | SECTION - D HVAC INSULATION
5 | SECTION - E COMMISSIONING OF HVAC
6 | SECTION - F REFRIGERANT PIPING
7 | SECTION - G HVAC DUCTS & CASING
8 | SECTION - H AIR DUCT ACCESSORIES
9 | SECTION - I HVAC FANS
10 | SECTION - J AIR OUTLETS & INLETS
11 | SECTION - K DECENTRALIZED UNITARY HVAC EQUIPMENT
12 | SECTION - L MAINTENANCE WORKS
Total Amount (Rs.)
Note: ● Contractor is advised to inform missing items (if any) in BOQ at time of submitting this tender. No escalation will be considered at time of execution of work. ● Owner can supply any material of Contractor scope at any stage and its cost will be completely deleted from Contractor scope without any kind of adjustment. ● Contractor should mark the selected brands and vendors in approved manufacturer list with submission of Tender Documents. ● Owner / Consultant have all the rights to select any brand / vendor from provided approved manufacturer list, Contractor shall not finalize any brand / vendor without written approval from consultant / owner.

## BoQ
S.# | ITEM DESCRIPTION | QTY | UNIT | SUPPLY |  | INSTALLATION |  | TOTAL (Rs.)
|  |  |  | RATE (Rs.) | AMOUNT (Rs.) | RATE (Rs.) | AMOUNT (Rs.)
SECTION - A GENERAL REQUIREMENTS FOR HVAC SYSTEM
1 | Making of Shop Drawings with sectional details complete in all respect for complete HVAC Systems as per Specifications | 1 | Job
2 | Making of As Built Drawings with sectional details complete in all respect for complete HVAC Systems as per Specifications | 1 | Job
3 | Shifting of equipment from Ground Floor to respective locations.. | 1 | Job
4 | Excavation and backfilling the earth for pipe works as required to complete the HVAC Works as per Drawings and Specifications. | 1 | Job
5 | Dismentaling and Re-Location of existing of VRF A/C Units as installed on site complete in all respects as per drawings. | 1 | Job
6 | Dismentaling of existing Fresh & Exhaust Air Ducts with air devices as installed on site complete in all respects. Preparation of Inventory list of dismantled items for client submission and handing over dismantled items to location as per client instruction. | 1 | Job
7 | Dismentaling of existing Damaged copper piping as installed on site complete in all respects. Preparation of Inventory list of dismantled items for client submission and handing over dismantled items to location as per client instruction. | 1 | Job
8 | Dismentaling of existing Damaged insulation as installed on site complete in all respects. Preparation of Inventory list of dismantled items for client submission and handing over dismantled items to location as per client instruction. | 1 | Job
Contractor to list and price below with quantities any additional item(s) and/or quantities which are not included but required to complete the lumpsum tender price for this section of works. Should the tenderer fail to insert any item(s) and/or quantities here, it will be deemed that this lumpsum price for the tender includes all items and no subsequent cliams for any additional item will be entertained.
Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY)
SECTION - B OPERATION & MAINTENANCE FOR HVAC SYSTEM
1 | Operation and maintenance of HVAC System
a | One month test run | 1 | Job
b | Operation of mainteance of HVAC System for one year | 1 | Job
c | Special tools and instruments for operation and maineance | 1 | Job
Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY)
SECTION - C COMMON WORKS RESULTS FOR HVAC SYSTEM
Wires, Cables, Conduites and Cable Tray
1 | Supply and installation of cables, conduites for power supply and earthing from isolators to AC equipment. Control cable between indoor and outdoor unit and control cable for Fresh Air Unit with cable tray. Complete in all respect as per drawings and specifications. | 1 | Job
Hangers and Supports for HVAC Ducting
2 | Supply and Installation of hangers and supports for HVAC ducting complete in all respect as per drawings and specifications. | 1 | Job
Hangers and Supports for Refrigerant Piping
3 | Supply and Installation hangers and supports for refrigerant piping complete in all respect as per drawings and specifications. | 1 | Job
Hangers and Supports for HVAC Equipment
4 | Supply and Installation of hangers and supports for HVAC equipment complete in all respect as per drawings and specifications. | 1 | Job
Identification for HVAC Ducting, Piping and Equipment
5 | Supply and Installation of identification for HVAC ducting, piping and equipment complete in all respect as per drawings and specifications. | 1 | Job
Fire Stopping
6 | Supply and Installation of Fire stopping complete in all respect as per drawings and specifications. | 1 | Job
Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY)
SECTION - D HVAC INSULATION
Duct Insulation
1 | Supply and installation of 12 mm thick XLPE Insulation of density 28 kg/m3 with Aluminum jacketing for Internal G.I. sheet metal ducts complete in all respect as per schedule, specifications and drawings. | 1300 | Sq.ft
Refrigerant pipe insulation
2 | Supply and installation of 12 mm thick Pre-moulded Foam Pipe and valve Insulation complete in all respect as per schedule, specifications and drawings.
a | 3/8" Diameter | 80 | Rft
b | 1/4" Diameter | 230 | Rft
c | 1/2" Diameter | 180 | Rft
d | 5/8" Diameter | 90 | Rft
e | 3/4" Diameter | 140 | Rft
f | 7/8" Diameter | 20 | Rft
g | 1-1/8" Diameter | 60 | Rft
h | 1-3/8" Diameter | 15 | Rft
i | 1-7/8" Diameter | 40 | Rft
Condensate Drain Insulation
3 | Supply and installation of 6 mm thick Pre-moulded Armaflex Pipe Insulation complete in all respect as per schedule, specifications and drawings.
a | 20 mm (3/4 inch) Diameter | 30 | Rft
b | 25 mm (1 inch) Diameter | 55 | Rft
c | 32 mm (1-1/4 inch) Diameter | 95 | Rft
d | 38 mm (1-1/2 inch) Diameter | 35 | Rft
e | 50 mm (2 inch) Diameter | 50 | Rft
Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY)
SECTION - E COMMISSIONING OF HVAC
Testing, Adjusting and balancing for HVAC systems
1 | Testing, balancing and commissioning of HVAC system complete in all respect including one month test run, measurement and recording of pressure and electrical data and submission of technical/operation manual, LOG book for each related equipment as per specifications and drawings. | 1 | Job
Total Amount (Rs.) Sec - E (CARRIED FORWARD TO SUMMARY)
SECTION - F REFRIGERANT PIPING
Refrigerant piping
1 | Supply, Installation, testing & Commissioning of refrigerant piping with valves, fittings, Y-joint and specialities complete in all respect as per drawings and specifications.
a | 3/8" Diameter | 80 | Rft
b | 1/4" Diameter | 230 | Rft
c | 1/2" Diameter | 180 | Rft
d | 5/8" Diameter | 90 | Rft
e | 3/4" Diameter | 140 | Rft
f | 7/8" Diameter | 20 | Rft
g | 1-1/8" Diameter | 60 | Rft
h | 1-3/8" Diameter | 15 | Rft
i | 1-7/8" Diameter | 40 | Rft
Condensate Drain piping
2 | Supply, Installation, testing & Commissioning of Condensate Drain Piping UPVC Class-D piping with valves, fittings and specialities complete in all respect as per drawings and specifications.
a | 20 mm (3/4 inch) Diameter | 30 | Rft
b | 25 mm (1 inch) Diameter | 55 | Rft
c | 32 mm (1-1/4 inch) Diameter | 95 | Rft
d | 38 mm (1-1/2 inch) Diameter | 35 | Rft
e | 50 mm (2 inch) Diameter | 50 | Rft
Total Amount (Rs.) Sec - F (CARRIED FORWARD TO SUMMARY)
SECTION - G HVAC DUCTS & CASING
Medium/Low pressure G.I. sheet metal ducting
1 | Supply, Installation, testing & Commissioning of medium/low pressure G.I. sheet metal ducting complete in all respect as per drawings and specifications.
a | 24 gauge | 2100 | Sq.ft
Access door for Fresh Air Unit
2 | Supply, Installation, testing & Commissioning of access door for Fresh air unit and Cassette type units complete in all respect as per drawings and specifications. | 7 | Nos
Total Amount (Rs.) Sec - G (CARRIED FORWARD TO SUMMARY)
SECTION - H AIR DUCT ACCESSORIES
Dampers
1 | Supply, Installation, Testing & Commissioning of dampers complete in all respect as per drawings and specifications.
Volume Control Damper
a | 16"x6" | 4 | Nos
b | 14"x8" | 1 | No
c | 12"x8" | 1 | No
Fire Damper
d | 16"x6" | 4 | Nos
e | 14"x8" | 1 | No
f | 12"x8" | 1 | No
Flexible Connectors
2 | Supply, Installation, testing & Commissioning of flexible connectors between blower section and air duct complete in all respect as per drawings and specifications. | 1 | Job
Flexible Duct
3 | Supply, Installation, testing & Commissioning of flexible duct complete in all respect as per drawings and specifications.
a | 150 mm (6 inch) Diameter | 75 | Rft
b | 600 mm (24 inch) Diameter. For VRF outdoor unit | 40 | Rft
Total Amount (Rs.) Sec - H (CARRIED FORWARD TO SUMMARY)
SECTION - I HVAC FANS
Blowers and fans
1 | Supply, Installation, testing & Commissioning of blowers and fans with SS impailer complete in all respect as per drawings and specifications.
Centrifgual fans (cabinet type)
a | 750 Cfm & 1" ESP | 1 | No
b | 260 Cfm & 0.5" ESP | 1 | No
c | 240 Cfm & 0.5" ESP | 1 | No
d | 200 Cfm & 0.5" ESP | 1 | No
Total Amount (Rs.) Sec - I (CARRIED FORWARD TO SUMMARY)
SECTION - J AIR OUTLETS & INLETS
Diffusers, Registers, and Grilles
1 | Supply, Installation, testing & Commissioning of Diffusers, Registers and Grilles complete in all respect as per drawings and specifications.
Fresh Air Diffuser (FAD)
a | 150x150 (6"x6") | 30 | Nos
b | 225x225 (9"x9) | 2 | Nos
Exhaust Air Register (EAR)
c | 150x150 (6"x6") | 15 | Nos
d | 225x225 (9"x9) | 2 | Nos
Fresh air intake louver
e | 500x250 ( 20"x10") | 1 | No
f | 300x250 ( 12"x10") | 1 | No
Exhaust air louver
g | 600x250 (24"x10") | 1 | No
h | 300x200 (12"x8") | 2 | Nos
Total Amount (Rs.) Sec - J (CARRIED FORWARD TO SUMMARY)
SECTION - K DECENTRALIZED UNITARY HVAC EQUIPMENTEquipment
Mini Split Air-Conditioners
1 | Supply, testing & Commissioning of Mini Split Inverter type Air-Conditioners complete in all respect as per drawings and specifications.
a | 1.5 TR (For UPS Room) | 1 | No
Variable Refrigerant Flow (VRF) System
2 | Supply, installation, testing & Commissioning of Inverter based Variable Refrigerant Flow (VRF) System complete in all respect as per drawings and specifications.
Fresh air processing ducted indoor unit(s).
a | VRF-FAIU (3.5 TR) | 2 | Nos
Wall Mounted indoor unit(s).
b | VRF-WMIU (1.5 TR) | 4 | Nos
Central Controller
c | Central Controller to control VRF air conditioning system, including BACnet BMS gateway, work station with 17 inch monitor and one high speed printer. | 1 | No
Total Amount (Rs.) Sec - K (CARRIED FORWARD TO SUMMARY)
SECTION - L MAINTENANCE WORKS
Outdoor Units
1 | Unit 1 (GMV-PDM-280 WNA/B-M): · Identified Issues: · Oil valve leak · 4-way valve leak · Assessment: · Both compressors are operational. · Electronic control cards are functioning correctly. · Urgent Attention Required: Oil valve and 4-way valve leaks observed, necessitating immediate repair. · Recommendation: Master servicing is advised to address all identified issues comprehensively. | 1 | Job
2 | Unit 2 (GMV-PDM-400 WNA/B-M): · Identified Issues: · Solenoid valve leak · 4-way valve leak · Communication wire damage · Assessment: · Compressors are functioning within normal parameters. · Control cards are intact. · Urgent Attention Required: Solenoid valve leak, 4-way valve leak, and communication wire damage demand immediate attention to ensure system stability. · Recommendation: Master servicing is necessary to rectify all identified issues comprehensively. | 1 | Job
3 | Unit 3 (GMV-PDM-450 WNA/B-M): · Identified Issues: · Condenser side leak · Three solenoid valves in poor condition · Oil valve leak · Assessment: · Compressors are operating within acceptable parameters. · Control cards are functional. · Urgent Attention Required: Condenser side leak and deteriorating solenoid valves pose a risk to system efficiency and performance. · Recommendation: Comprehensive master servicing is imperative to address all identified issues and ensure optimal system functionality. | 1 | Job
4 | Unit 4 (GMV-PDM-280 WNA/B-M): · Identified Issues: · Condenser side leak · Oil valve leak · 4-way valve leak · Assessment: · Compressors are operational. · Control cards are functioning correctly. · Urgent Attention Required: Condenser side leak, oil valve leak, and 4-way valve leak necessitate immediate repair to prevent further damage. · Recommendation: Master servicing is advised to address all identified issues comprehensively. | 1 | Job
5 | Unit 5 (GMV-PDM-280 WNA/B-M): · Identified Issues: · 4-way valve leak · Assessment: · Compressor is operational. · Control cards are intact. · Urgent Attention Required: 4-way valve leak observed, necessitating immediate repair to ensure system efficiency. · Recommendation: Master servicing is necessary to rectify the identified issue comprehensively. | 1 | Job
Indoor Units
6 | GMVR71G/NAG-K (5 Units): · Identified Issues: · IT coils need replacement for all units. · Assessment: · The coils are deteriorated and no longer functioning optimally. · Urgent Attention Required: Replacement of IT coils is necessary to ensure proper heating and cooling functionality. · Recommendation: Immediate replacement of IT coils for all five units is advised. | 1 | Job
7 | GMVR36G/NAG-K (2 Units): · Identified Issues: · Two indoor coils need replacement for both units. · Assessment: · The identified coils are damaged and affecting unit performance. · Urgent Attention Required: Replacement of two coils for each unit is necessary to restore optimal operation. · Recommendation: Immediate replacement of coils for both units is advised. | 1 | Job
8 | GMVR71T/NAG-K (2 Units): · Identified Issues: · Two coils need replacement for both units. · Assessment: · The coils are in need of replacement due to damage or deterioration. · Urgent Attention Required: Replacement of two coils for each unit is necessary to maintain efficient operation. · Recommendation: Immediate replacement of coils for both units is advised. | 1 | Job
9 | GMVR56G/NAG-K (3 Units): · Identified Issues: · Three coils need replacement for all units. · Assessment: · The coils are in poor condition and impacting unit performance. · Urgent Attention Required: Replacement of three coils for each unit is necessary to ensure proper functioning. · Recommendation: Immediate replacement of coils for all three units is advised | 1 | Job
Total Amount (Rs.) Sec - L (CARRIED FORWARD TO SUMMARY)