## BOQ Option-02
Bill of Quantities (Option-02)
Fire Suppression Services
Spar Supermarket | [8 empty] | Rev.00
DHA, Karachi. | [8 empty] | Date: 12-08-2024
S.No. |  | Description | Unit | Qty | Material |  | Labour |  | Total
[5 empty] | Rate | Amount | Rate | Amount | Amount Rs.
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression system including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1 |  | Fire hose cabinet double height 32" x 60" x 14", stainless steel front, powder coated back including 1" dia x 100 Rft. rubber hose reel, nozzle guide, lock shield valve, automatic 180 deg. swing type, with 2-1/2" dia size landing valve, 2-fire extinguishers as shown on drawing.
| i. | Type FHC-LV | Nos. | 4 | 375000 | 1500000 | 7500 | 30000 | 1530000
2 |  | Fire hose cabinet size 42" x 36" x 12" for spare hose pipes including 4 Nos. 2-1/2" x 100 Rft. synthetic hose pipe, jet/spray/fog nozzle with aluminum instantaneous coupling, 2-Nos. fire blanket 6'-0" X 6'-0", fireman's axe, 2-pairs of fire proof gloves, front breakable glass, lock and all other accessories as specified, complete in all respects as per drawings, specified.
| i. | Type FHC-S | No. | 1 | 615000 | 615000 | 7500 | 7500 | 622500
3 |  | MS Sch-40 seamless pipes including all specials fittings UL listed FM approved, threaded, welded joints, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, supports and hangers, sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
| i. | Dia 1" (Threaded fitting) | Rft. | 250 | 650 | 162500 | 200 | 50000 | 212500
| ii. | Dia 1-1/4" (Threaded fitting) | Rft. | 100 | 875 | 87500 | 225 | 22500 | 110000
| iii. | Dia 1-1/2" (Threaded fitting) | Rft. | 40 | 1100 | 44000 | 250 | 10000 | 54000
| iv. | Dia 2" (Threaded fitting) | Rft. | 40 | 1250 | 50000 | 300 | 12000 | 62000
| v. | Dia 2-1/2" (Welded joints fitting) | Rft. | 70 | 1890 | 132300 | 400 | 28000 | 160300
| vi. | Dia 3" (Welded joints fitting) | Rft. | 30 | 2425 | 72750 | 500 | 15000 | 87750
| vii. | Dia 4" (Welded joints fitting) | Rft. | 10 | 4500 | 45000 | 750 | 7500 | 52500
4 |  | Sprinkler Heads
| i. | Sprinkler Upright Type Standard Response K = 5.6 (Opening Temperature 57ºC) | Nos. | 34 | 2150 | 73100 | 500 | 17000 | 90100
| ii. | Dry Sprinkler Side Wall Type Quick Response K = 5.6 (Opening Temperature 57ºC) | No. | 1 | 7500 | 7500 | 1000 | 1000 | 8500
5 |  | Fire extinguishers with fixing accessories.
| i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 8 | 25250 | 202000 | 750 | 6000 | 208000
| ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 8 | 14250 | 114000 | 750 | 6000 | 120000
| iii. | Automatic fire extinguisher (6 Kg. Dry Chemical Powder) | Nos.
| v. | Automatic fire extinguisher (10 Kg. Dry Chemical Powder) | Nos. | 3 | 29900 | 89700 | 1000 | 3000 | 92700
6 |  | Zone Control Valve assembly 3" dia UL Listed/FM Approved complete with following.
| i. | OS & Y Gate valve 3" size with tamper switch
| ii. | Check valve 3" size
| iii. | Pressure Gauge | No. | 1 | 619000 | 619000 | 8000 | 8000 | 627000
| iv. | Water flow switch 3" dia
| v. | 1-1/2" dia test valve with sight glass & sectional drain valve.
7 |  | Alarm Check valve assembly with alarm gong and pipe work. with retarding chamber.
| i. | Size. 6" | No. | 1 | 492000 | 492000 | 10000 | 10000 | 502000
8 |  | Pressure relief valve size 3" dia | No. | 1 | 467400 | 467400 | 10000 | 10000 | 477400
9 |  | Automatic air relief valve, 1" connection | No. | 1 | 39500 | 39500 | 1000 | 1000 | 40500
10 |  | Float Switch for low water level cut off. | No. | 1 | 45000 | 45000 | 5000 | 5000 | 50000
11 |  | Anti vortex suction plates for 6" dia. suction pipe | No. | 1 | 115000 | 115000 | 10000 | 10000 | 125000
12 |  | Flow meter 6" dia. | No. | 1 | 946000 | 946000 | 10000 | 10000 | 956000
13 |  | OS & Y Gate valve matching flanges with tamper switch.
| i. | Size. 6" | Nos. | 4 | 211000 | 844000 | 5000 | 20000 | 864000
14 |  | Throttling type butterfly valve with matching flanges.
| i. | Size. 6" | Nos. | 2 | 41500 | 83000 | 5000 | 10000 | 93000
15 |  | C.I body check valve with matching flanges.
| i. | Size. 6" | Nos. | 2 | 93000 | 186000 | 5000 | 10000 | 196000
16 |  | Fire Pumps Set 500 gpm @ 7 bar comprising of 1 No. multistage in line Jockey Pump + 1 No. main horizontal pump with electrical motor + 1 No. Standby horizontal pump with diesel engine, diesel storage tank including pump controllers mounted on common MS skid, inter connecting pipes, wiring, OS&Y valve, check valves and all accessories as per requirement of NFPA 20, drawings and engineer instruction. | Set. | 1 | 15246000 | 15246000 | 150000 | 150000 | 15396000
17 |  | Supervisory Fire Control Panel for sensing and monitoring of flow and monitoring OS&Y valves switching with true alarm including batteries and charger. | Job. | 1 | 465000 | 465000 | 35000 | 35000 | 500000
18 |  | MS insulated 6" dia Diesel Engine Flue pipe with 2" Rockwool insulation up to outside the building as per Consultant's approval. | Job. | 1 | 180000 | 180000 | 20000 | 20000 | 200000
19 |  | Allied electrical work including power cables to pumps motors, control cables and wires from sensing, monitoring and indicating devices such as valves and flow switches and switches to Electrical Control Panel and Fire Control Panel and supervisory switch including GI/PVC conduits and tray, termination, luxes and all accessories complete in all respects. Note: Contractor shall perform allied electrical works within the pump room. Power to the pump room shall be provided by the client. | Job. | 1 | 175000 | 175000 | 35000 | 35000 | 210000
20 |  | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1 | 60000 | 60000 | 20000 | 20000 | 80000
21 |  | Making of As-Built & Shop Drawings on AutoCAD 2018 or latest version with sectional details complete in all respects as per instructions of consultant. | Job. | 1 | 15000 | 15000 | 15000 | 15000 | 30000
22 |  | Painting, identification and tagging to the installations and equipments. | Job. | 1 | 40000 | 40000 | 35000 | 35000 | 75000
23 |  | Flushing of entire fire pipe work according to (NFPA-13). | Job. | 1 | 20000 | 20000 | 30000 | 30000 | 50000
24 |  | Testing, and commissioning of entire fire fighting installation as per Consultant's approval. | Job. | 1 |  | 0 | 100000 | 100000 | 100000
|  | Total Cost of Fire Suppression Services Rs. |  |  |  | 23233250 |  | 749500 | 23982750
Note:
> | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).