## TITLE
BILL OF QUANTITIES
Architecture/Interior, MEP & Furniture Works
11TH FLOOR, RANDHAWA TOWERS
ISLAMABAD, PAKISTAN
| Principal Design Consultant | Project Management and Cost Consultants

## Grand Summary
EY Islamabad - 11th Floor - Grand Summary
S.No | DOMAIN | MATERIAL AMOUNT (Rs.) | INSTALLATION AMOUNT (Rs.) | TOTAL AMOUNT (Rs.) | Sub-Cons
A | Civil ID | 0 | 0 | 0
B | Electrical | 0 | 0 | 0
C | ACMV | 3584780 | 826650 | 3900630
D | Firefighting | 4885400 | 630000 | 5515400
E | Plumbing | 1208100 | 154000 | 1362100
| Total= | 9678280 | 1610650 | 10778130
General Contractor's Markup on MEP Cost=
Grand Total Inclusive of Markup= |  | 9678280 | 1610650 | 10778130
GST on Supply=
SST on Installation=
Grand Total Inclusive of Taxes= |  | 9678280 | 1610650 | 10778130

## CIVIL ID
EY OFFICES, INTERIOR FINISHES WORK. |  |  |  |  | Bill of Quantities
ISLAMABAD. |  |  |  |  | 11th Floor
ITEM | DESCRIPTION | Unit | Estimated Qty | Verified Qty | Supply |  | Services |  | Total | Brand | Lead Time | Remarks
[5 empty] | Rate | Total | Rate | Total | Amount
0 | DEMOLITION WORK:
1- | Dismantling Works
Dismantling & Removing of following items, as per instruction of Architect and give to all salvageable item to Client and thrown out dust upto any lead and lift out side the construction Site as per CDA SOP's and as per architect / Project Manager instruction (Contractor to visit site before quote rate)
a. | Removing of existing Flooring / Skirting / Walls Tiles (any type) with mortar to entire exiting area including Toilets / Pantry.
b. | Remove existing Cladding (Any type) on Walls / Columns etc with proper care as per proposed layout Plan.
c. | Removing and dismantling existing Partition Walls (Any type) including Doors Lintel / Vanity Counters etc as per proposed layout Plan.
d. | Removing existing Plumbing fixtures (Any type) as per proposed layout Plan.
e. | Removing existing HVAC (Any type) / Piping & Ducting, exposed conduits, cable tray etc as per proposed layout Plan.
f. | Removing existing Electrical / Networking fixtures (Any type) / Wiring & cabling, exposed conduits, cable tray etc as per proposed layout Plan. | Job | 1
A- | Wall Finishes:
1 | Cement Board Wooden Partitions / Portal / Bulkheads.
| Providing, making and fixing of Cement Board Wooden Partitions / Portal / Bulkheads (Elephant / Eltoro or equivalent) 4" thick as per proposed layout Plan consist of 1/2" thick Cement board (both side) with GI.framing structure (16 swg), fixed on existing finished surface / Ceiling / Wall using screws / bolts as shown in Elevational drawings & details including infill of Rockwool insulation approved material, cutting, hardware's, wastage, lifting, all fixing accessories and arrangements, scaffolding, making openings, cutting of electric switch board, solignum treatment, etc., Complete job in all respect as per drawing/detail and as directed by the Architects. (This job will be coordinated with electrical/ air-conditioning works & Payment Exposed Elevation area will be measured with-out any depth and thickness) | Sft | 2710
2 | Cement Board Cladding on Block / RCC Walls & Columns.
| Providing, making and fixing of Cement Board Cladding on Block / RCC Walls & Columns (Elephant / Eltoro or equivalent) consist of 1/2" thick Cement board with rough wood backing fixed on existing finished surface / Ceiling / Wall using screws / bolts as shown in Elevational drawings & details in smooth surface finish including, cutting, hardware's, wastage, lifting, all fixing accessories and arrangements, scaffolding, making openings, cutting of electric switch board, solignum treatment, etc., Complete job in all respect as per drawing/detail and as directed by the Architects. (This job will be coordinated with electrical/ air-conditioning works & Payment Exposed Elevation area will be measured with-out any depth and thickness) | Sft | 1385
3 | Texture Paint.
Providing and applying Texture Paint (Innovative Coatings / Equivalent) minimum coats of approved shade as per manufacture recommendation over a coat of primer surfaces, prepared smooth with carborandum stone, filling the depression with putty, including scaffolding, mixing of fine sand so as to achieve desired texture, etc. complete in all respect as per drawing, specifications and as instructed by the architect. (Base Rate: 300/Sft)
i. | Reception /Small Hub / Team / FCR Rooms / Hall areas/ Passages / Multi-functional Room. | Sft | 5350
4 | Matt Enamel Paint.
Provide and apply of three coats of approved quality and shade Matt Enamel paint of (ICI/Berger/Nippon ) on Masonry Walls & Column / Wooden Paneling & Partition Walls etc. minimum 3 coats of matt enamel paint with primer and base preparation up to any height and level including preparing the surfaces smooth by putty filling, scraping with sand paper, cleaning the surface etc., complete as per drawings and as directed by the Architects.
i. | Paint over Fluted Pattern / Wooden Paneling. (Small Hub / | Sft | 171
ii. | Paint on Plaster Finish surface Walls. (Storage area) | Sft | 325.5
5 | HDF Board Wooden Cladding with CNC Cutting Pattern on Walls / Columns.
Providing, making and fixing of HDF Board Wooden cladding on Walls / Columns consist of 1/2" thick HDF board cladding on cement board Partitions walls / Columns having CNC Cutting in panels Pattern as per detail elevational drawing fix with screw bolts in smooth surface including Grooves, cutting, hardware's, wastage, glues, lifting, all fixing accessories and arrangements, scaffolding, making openings, cutting of electric switch board, solignum treatment, etc., Complete job in all respect as per drawing/detail and as directed by the Architects. (This job will be coordinated with electrical/ air-conditioning works & Payment Exposed Elevation area will be measured with-out any depth and thickness)
i. | Small Hub. | Sft | 171
6 | HDF Board Cladding on Partition Walls in Polish Finish.
Providing, making and fixing of HDF Board Cladding on Partition Walls in Polish Finish 6'-0" high consist of 1/2" thick HDF board fixed on Masonry / Cement Board Partition walls using screws / bolts as shown in Elevational drawings & details up to recommended height including 1/4" x 1/4" Grooves, cutting, hardware's, wastage, glues, lifting, all fixing accessories and arrangements, scaffolding, making openings, cutting of electric switch board, solignum treatment, etc., Complete job in all respect as per drawing/detail and as directed by the Architects. (This job will be coordinated with electrical/ air-conditioning works & Payment Exposed Elevation area will be measured with-out any depth and thickness)
i. | Hall-A, B, C & D. | Sft | 1530
7 | HDF Board Vertical Fluted Pattern over Cement Board Partition Walls.
Providing, making and fixing of HDF Board Vertical Fluted Pattern over Cement Board Partition Walls 3'-3" high in Polish finish consist of 1/2" HDF Board fix over Cement Board Partition walls having 1/8"x1/8" vertical Flutes (Grooves)as per elevational detail drawing fix / paste with adhesive in level including cutting, hardware's, wastage, glues, lifting, all fixing accessories and arrangements, scaffolding, making openings, cutting of electric switch board, solignum treatment, etc., as shown in drawing & details, complete job in all respect as per drawing/detail and as directed by the Architects. (This job will be coordinated with electrical/ air-conditioning works & Payment Exposed Elevation area will be measured with-out any depth and thickness)
i. | Hall-A, B, C & D. | Sft | 870
8 | HDF Board Half Round Vertical Fluted Panel Cladding over Columns in Polish finish.
Item description same as above item # 7 but having 1" x 3/4" thick half round shape Vertical Fluted Pattern fix / paste with adhesive / screw bolts in level on cement board finish Columns including cutting, hardware's, wastage, glues, lifting, all fixing accessories and arrangements, scaffolding, making openings, cutting of electric switch board, solignum treatment, etc., as shown in drawing & details, complete job in all respect as per drawing/detail and as directed by the Architects. (This job will be coordinated with electrical/ air-conditioning works & Payment Exposed Elevation area will be measured with-out any depth and thickness)
i. | Hall-A, B, C & D. | Sft | 1930
9 | Pre-Fabricated Acoustic Paneling on Wall
Providing, making and fixing of Pre-Fabricated Acoustic Paneling on Walls in approved decorative design fixed over existing Wall upto required height as per elevational detail drawing using best quality adhesive/screw including cutting, fixing, hardware's, wastage, glues, lifting, all fixing accessories and arrangements, scaffolding, making openings, cutting of electric switch board, solignum treatment, etc., as shown in drawing & details, complete job in all respect as per drawing/detail and as directed by the Architects. (This job will be coordinated with electrical/plumbing and air-conditioning works.)
i. | Team / JIT / FCR Rooms. | Sft | 710
10 | Porcelain Tile on Wall.
Providing and Fixing Porcelain Tile on walls / Columns / Dry Wall Partitions (approved Sample and shade by Architect) fixing with 1:4 cement sand mortar and base with approved bond of required thickness, setting the tiles with neat cement mortar, butt joints if required with approved grout & color of equivalent, including curing, cleaning, hacking / chipping of existing surface for bonding where necessary, etc., complete in all respect. (Base Rate: 8000/Sqm)
i. | Toilets Cubical & Lobby areas upto False-Ceiling Height. | Sft | 1550
ii. | Dado in Kitchen Counter Wall. | Sft | 50
iii. | 4" Skirting in Kitchen / Cleaning area. | Rft | 60
11 | 3" High Solid Oak Wood Skirting in Polish Finish for Carpet Floor area.
| Providing, making and fixing 3" High Solid Oak Wood Skirting in Polish Finish for Carpet area (using seasoned & termite treated wood) of approved thickness with required design & pattern as per drawing & detail, fixed on wall including all hardware's, cutting, polishing with approved polish, wastage, nails, adhesive, etc., Complete in all respect as per drawing & Architect instruction. (For Payment net Running length will be measured). | Rft | 865
12 | PVC Skirting.
Providing and fixing PVC Skirting 3" high Pasting over existing finish walls / Dry wall partitions / Columns using best quality pasting adhesive including cutting, preparation of existing surface for pasting, cleaning, smooth surface, etc. Complete job with all respects and as directed by the Architect. (Base Rate: 570/Sft)
i. | VL-01 (Small Hub / FCR / Storage) | Rft | 265
ii. | VL-03 (Reception area) | Rft | 23
B- | FLOORING FINISHES:
13 | Vinyl Flooring.
Providing and Laying Vinyl Flooring (approved Vendor) over existing CC finish floor with best quality adhesive, including cutting, lifting, wastage, etc., complete in all respect, as per drawing and instruction of the Architect. (For Payment Net installed Carpet tile area will be measured.) Base Rate: 1200/Sft.
i. | VL-01 (Small Hub / FCR / Storage / Hall area Passages) | Sft | 1890
ii. | VL-03 (Reception area) | Sft | 60
14 | Carpet Flooring.
Providing and Laying Carpet (approved Sample / vendor by Architect) over existing CC finish floor with approved adhesive, including cutting, lifting, wastage, etc., complete in all respect, as per drawing and instruction of the Architect. (For Payment Net installed Carpet tile area will be measured.) Base Rate: 1200/Sft.
i. | CT-01, 20"x 20": Hall areas | Sft | 1342
ii. | CT-02, 20"x 20" Teams & JIT Rooms. | Sft | 775
iii. | CT-05, 20"x 20" Multi Function Room. | Sft | 1160
15 | 2 'x 4' Porcelain Tile Flooring in Toilets area.
| Providing and Laying of Porcelain tile flooring (approved sample by Architect) with 1:4 cement sand mortar base & bond of required thickness so as to achieve a minimum overall finished floor thickness of 3', setting the tiles with neat cement mortar, butt joints if required with approved waterproof grout, curing, cleaning, hacking / chipping of existing surface for bonding where necessary, etc. Complete in all respect, as per drawing and instruction of the Architect. (For Payment Net tile area will be measured.) | Sft | 385
16 | C.C Floor under Carpet / Vinyl Flooring.
| Providing and Laying 2" ~ 3" thick (avg.) with 1:3:6 cement concrete floor finished of required thickness including curing, hacking of existing surface for bonding where necessary, etc., Complete in all respect as per drawings and as instructed by the Architect. | Sft | 5227
17 | C.C Raised Platform for Kitchen Base Cabinets.
| Providing, making / laying 1:3:6 C.C Raised Platform for for Kitchen Base Cabinets made up of debris / solid blocks or Broken pieces laid with cement sand mortar levelling, curing, Plaster finish, etc. complete as per drawing and as directed by the Architect. | Sft | 20
18 | Trim Inlay on Floor.
| Providing & Laying Brass Trim Inlay on Floor (approved sample / Color by Architect) laying with proper smooth floors finish as per drawing and detail, complete job with all necessary Laying, arrangements including cutting, bending, Polish, Proper inlay in existing floor with best quality adhesive materials, etc., as per drawings and as directed by the Architect. (Base Rate: 300/Rft, Running length will be measured). | Rft | 410
19 | Waterproofing for Wet Areas.
Providing & apply of Waterproofing for Wet Area on floor and walls upto 1' feet height by brush application of Aquafin or approved equivalent on floor and walls including treatment at the junctions of horizontal & vertical surface, etc., complete in all respect as per drawings and instructions of the Architect. (For Payment only Floor area will be measured).
i. | Male & Fe-Male Toilet Areas/ Pantry areas. | Sft | 435
C- | CEILING FINISH.
20 | Gypsum Suspended False-Ceiling with Bulkhead.
Providing and installing in position gypsum board false ceiling 12mm thick (Elephant brand or approved equivalent) best quality gypsum sheet including the cost of galvanized iron adjustable clutch wire hanging system, horizontal and vertical framework of approved material, making Cove/Bulkheads/light pelmet, fiber tape on joints, provision of openings for all lights fixtures, linear grills and diffusers and providing aluminum flush band for protection of edges/corners where ever required etc., all hardware, wastage, cutting, lifting etc., Complete in all respect as per drawing and as instructed by the architect. (For payment net surface L x B will be measured)
i. | Small Hub / Reception / Team rooms / JIT / Hall areas. | Sft | 3961
21 | Moisture Resistant Gypsum Suspended False-Ceiling for Toilets / Kitchen / Cleaning area.
| Item description same as item above item # 20, but moisture resistant gypsum board ceiling. Complete in all respect as per drawing and as instructed by the architect. (For payment net surface L x B will be measured) | Sft | 385
22 | MDF Wooden Ribs Suspended Ceiling in Small Hub room.
| Providing, making and installing in position MDF Wooden Ribs Suspended Ceiling (Lassani or approved equivalent) using of 1/2" MDF Board for making Ribs (6"x6" Panels) having 1/2" groove, 3-1/2" x 4" main exterior Ribs frame & 2-1/4" x 4" intermediate Ribs framing joint with main frame with best quality adhesive / bolts and hanging with galvanized iron adjustable clutch wire system to RCC Slab. All Joints should be properly joint with each other in proper screw bolts / adhesive and using best quality hardware. Complete job with all necessary fixing arrangement, scaffolding, wastage, cutting, lifting, provision of openings for all lights fixtures, etc as per drawing and as directed by the Architect. (For payment net surface L x B will be measured) | Sft | 35
23 | Gypsum Access Panel.
| Provide and install 2'x2' Gypsum access panel (Knauf) comprising of 1/2" thick gypsum sheet with GI frame and suspension system including all required fixing arrangements, openable mechanism, 3 coats of white matt enamel paint complete with all respect as per drawings and as instructed by Architect. | Nos | 10
24 | Pre Fabricated Acoustic Panel False Ceiling
| Providing and installing in position Pre Fabricated Acoustic Panel False Ceiling, consisting of Acoustic Panels of approved brand (FELTECH), fixed at required ceiling level hanged and supported with galvanized iron adjustable clutch wire hanging system, horizontal and vertical framework of approved material, making Cove/Bulkheads/light pelmet, fiber tape on joints, provision of openings for all lights fixtures, linear grills and diffusers and providing aluminum flush band for protection of edges/corners where ever required etc., all hardware, wastage, cutting, lifting etc., Complete in all respect as per drawing and as instructed by the architect. (For payment net horizontal surface L x B will be measured) | Sft | 450
25 | Plastic Emulsion Paint.
| Providing and applying 3 coats of Plastic Emulsion paint roller finish approved shade (Burger/Kansai/ICI) on False-ceiling with bulkheads / Concrete Slab /beams over one coat of primer and base preparation up to required height and level, including preparing the surfaces smooth with carborandum stone, filling the depression with putty, scraping with sand paper, cleaning the surfaces etc., complete as per drawings or as directed by the Architect. | Sft | 5612
D | Miscellaneous Work:
26 | Internal Fixed Glazing with 12 mm thick Laminated Cleared Glass with Powder Coated Aluminum Framing
Providing, fabrication and installation in position fixed glazing consisting of Laminated Glass (6mm+0.76mm (PVB) + 6mm) tempered cleared glass with one side curve side Design of approved brand with powder coated Aluminum framing of approved section fixed on Floor/wall/overhead beam etc., as per shown in drawing including all hardware's, neoprene gasket, rubber gasket seal / silicone sealant, fixing arrangements, etc., complete in all respect. Door area will be deducted. (For payment frame to frame exposed Elevation area will be measured.)
i. | Small Hub / Teams / JIT Rooms. | Sft | 350
27 | 8mm thick Tempered Glass Paneling on wall
Providing, fabrication and installation in position of Glass Panel consisting of 8mm thick tempered glass with sand blasted from back side only, fixed on wall with approved hardware's as shown in drawing/details including all hardware's, rubber seal of approved sample on edges of glass to protect edges, fixing arrangements, sand blasting, etc., complete as per drawing, hardware schedule and instruction of the Architect. (For payment exposed Elevation area will be measured.)
i. | Teams & FCR Rooms. | Sft | 105
28 | Acoustic Foldable Paritition Fabric Finish Both Side
| Supply and install imported Folding Partition with Acoustic Paneling on Both Side, including heavy duty Sliding frame section in Powder coated, Aluminum profiles and top MS tube support complete in all respect. Shop drawing will be submitted by GC for approval. (For payment one side elevation area will be measured). | Sft | 200
(Multi Functional Rooms)
29 | Mirror in Toilets.
| Providing and Installation in position 6mm thick imported Belgium mirror (2'-0" x 3'-6")with ply backing fixed on MS Frame (deco paint Finish) to be fixed in existing finish wall as shown in drawings and details, including hardware's, wastage, lifting, painting with deco paint (ICI, Jotun) etc., complete in all respects. (For Payment Frame to Frame Exposed area will be measured with-out any depth and thickness) | Sft | 42
30 | Frosted Film.
| Provide & apply Frosted film 150 Micron (3M or approved equivalent) on glazing / Doors as per approved sample & Pattern by Architect, Complete job with all necessary pasting material including cutting, wastage etc in all respect. (Base Rate: 270/Sft) | Sft | 600
31 | Glass Doors of Laminated Glass (6mm+0.76mm (PVB) + 6mm) both tempered cleared glass with Powder Coated Aluminum Framing.
Providing, fabrication & installation in position Glass door, consisting of Laminated Glass (6mm+0.76mm (PVB) + 6mm) both tempered cleared glass of approved brand, with powder coated Aluminum framing of approved section, all fitting with hinges of approved quality, locking arrangements, as per approved customized M.S handles as per design on both sides of shutter including all hardware's, wastage, silicon sealant, lifting, cutting, fixing, etc., complete as per drawing, hardware schedule and instruction of the Architect. (Base Rate of Hardware's 60,000/-, JB Saeed or approved equivalent brand / supplier).
i. | 5'-0" x 8'-0" (Double leaf) Main Entrance at Reception &Lift Lobby area. | Nos | 2
ii. | 3'-0" x 9'-6" (Single leaf), Office area Rooms. | Nos | 10
(Note: All Building Terrace Area Glass Doors are existing and Part of Building Owner Finish.)
32 | Laminated Wooden Door
Providing, making & fixing of Laminated Door, consisting of 50mm thick solid core flush shutter (for flush door shutters Partal wood infill framing) using approved Lamination on both sides of shutter over rough wood structure frame with 6mm thick wood lipping polish finish, including 6" wide & 2" thick wooden door frame of Oak wood in polish finish including 1"x 2-1/2" wide Architrave polish finish both side of door frame. Complete job with all respect with all necessary making and fixing arrangement with approved hardware's, seasoning, termite proofing in wooden surface area, etc as per drawings, specifications and instructions of the architect. (Door's Hardware will be from approved vendors i/c Hinges & Customized doors Handle, Base Rate of Hardware's Rs 30,000/-).
i. | Single Shutter Openable: 3'-6" x 8'-0". (Store) | No | 1
ii. | Single Shutter Openable: 2'-6" x 8'-0" (Toilets / Cleaner) | Nos | 8
iii. | Single Shutter Sliding: 3'-0" x 8'-0" (Kitchen/ Store) | Nos | 2
33 | Fire Rated Doors for Staircase (120 Minutes Fire Rating)
Providing & fixing 1-1/2" thick plain flush panel wood Fire Rated doors (Fire Rating upto One Twenty Minutes, MEK or equivalent vendor as approved by Architect) with 16 gauge M.S frame coated with intumescent Paint, shutters to be made up of a composite mineral core with mineral sheets on each side. The stiles and rails are mineral with wood edge. the skins are made of plywood, including providing 1.5 mm thick lead lining fire-resisting hardware's, Locks, Hinges, door closers, Panic exit device etc. Complete as per Drawings / Details, Specifications and as directed by the Architect.
i. | Size: 3'-6" x 8'-0". | Each | 2
34 | Roller Blind for Façade Glazing. (Manual Operated)
Providing and install Roller Blind for Facade Glazing with complete mechanism, shade approved by the Architect with brand (Manual Operated), Complete job with all necessary arrangement as per drawings/detail and as directed by the Architects. (Base Rate: 550/Sft)
i. | Light / Net Fabric exterior face. (Base Rate: 475/Sft) | Sft | 2200
ii. | Black Out Fabric inside. (Base Rate: 575/Sft.) | Sft | 2200
35 | Roller Blind for Façade Glazing. (Motorized)
| Providing and install Roller Blind for Facade Glazing with complete mechanism, shade approved by the Architect with brand (Motorized), Complete job with all necessary arrangement as per drawings/detail and as directed by the Architects. (Base Rate: 1650/Sft) | Sft | Rate Only.
36 | Graphics & Signage.
| Providing and installing in position Vinyl Graphics & Signage of approved size, shape by the Architect. Complete job with all necessary fixing arrangements, all hardware's, lifting, fixing, installation, scaffolding, tools, wastage, etc. Complete job with all necessary arrangement as per drawings/detail and as directed by the Architects. | L/S Job | 1
37 | Planter and Plantation work. (Natural / Artifical)
| Providing and Placing Planter and Plantation work including Pots as per Architect interior Layout with approved Plants with Pots up to recomended approved size with fill of Gravels & infill sand material (Natural / Artifical) with all respect as per Architect instruction. (Base Rate for Each Planter: Rs.30,000/-) | Nos | 25
E | Wooden Carpentry Work: (Fixed Furniture)
1 | (RT-01) Reception Counter.
| Providing, making and fixing in position Reception Counter completely consisting of 3/4" thick MDF board casing with approved Ply pasted over (ZRK/Merbok/Al-Noor/Lasani) including Counter Tops / Partitions / inside finish surface / Shelves etc with PVC match lipping all around exposed edging, Desk exterior finish having CNC cutting design Pattern using 1/2" MDF Sheet with making provision of cove for rope light. 1-1/2" high S.S finish Pedestal Base fix below reception counter desk. Complete job with all necessary making arrangement as per detail drawing using best quality approved hardware's, adhesive, wastage, cutting, lifting, solignum treatment to all wooden surfaces and as directed by the Architect. Length: 5'-2" x 3'-6" high & 24" deep. | No | 1
2 | Drawer Unit for Reception Counter.
| Complete Item description same as above item # 1, except exterior finish. Complete job with all necessary making arrangement as per detail drawing using best quality approved hardware's, Sliding Channel for drawer, best quality wheels, Lock, MS Paint Finish handle as per detail, wastage, cutting, lifting, solignum treatment to all wooden surfaces and as directed by the Architect. Length: 30" x 30" deep x 27" high . | No | 1
3 | Ridge Design Cabinets for Small Hub Room:
a. | Floor Cabinets with Ridge Design Pattern Shutters.
| Providing, making and fixing Floor Cabinets 3'-0" high and 24" deep made up of 3/4" thick Laminated MDF board (SRK, Lassani or equivalent) complete structure case including Intermediate Partitions / shelves and drawers with match PVC lipping exposed surface edges, 3/4" thick Solid Wooden Shutter with Ridge Design Pattern in polish finish fix in Laminated Cabinet case, Finally laying 1" thick approved approved Marble Polish finish counter top, 3/4" thick Shutter having 3/4" thick HDF vertical fluted pattern as per detail drawing, using best quality approved S.S Finish hardware's like hinges, handles, locks, 3" high Solid wood Polish finish Pedestal Base, etc. Complete job with all necessary fixing arrangement with all respect as per drawing and as directed by the Architect. (Base Rate: Marble Top: 2500/-sft) | Sft | 30
b. | Wall Cabinets with Ridge Design Pattern Shutters.
| Providing, making and fixing Wall Cabinets upto 5'-6" high & 18" deep madeup of 3/4" thick Lassani Laminated MDF board Complete structure case including Shutters / Intermediate Partitions / shelves and drawers with match PVC lipping all around shutters / drawers & exposed surface edges, 3/4" thick Solid Wooden Shutter with Ridge Design Pattern in polish finish fix in Laminated Cabinet case, Using best quality approved S.S Finish hardware's like hinges, handles, locks etc. Complete job with all necessary fixing arrangement with all respect as per drawing and as directed by the Architect. | Sft | 50
4 | Deco Paint Finish Filling Cabinets & Lockers in Hall areas / Passages.
a. | Floor Cabinets.
| Providing, making and fixing Floor Cabinets 2'-6" high and 22" deep made up of 3/4" thick white Laminated MDF board (SRK, Lassani or equivalent) complete structure case including Intermediate Partitions / shelves and drawers with match PVC lipping all around exposed surface edges 3/4" thick MDF Cabinet shutters having Deco Paint finish (approved color by Architect), laying 1" thick approved Marble counter top having round edges, Using best quality approved S.S Finish hardware's like hinges, handles, locks etc. Complete job with all necessary fixing arrangement with all respect as per drawing and as directed by the Architect. (Base Rate: Marble Top: 2500/-sft) | Sft | 115
b. | Wall Cabinets
| Providing, making and fixing Wall Cabinets upto 3'-6" high & 22" deep madeup of 3/4" thick Lassani Laminated MDF board Complete structure case including Intermediate Partitions / shelves and drawers with match PVC lipping all around exposed surface edges, 3/4" thick MDF Cabinet shutters having Deco Paint finish (approved color by Architect), Using best quality approved S.S Finish hardware's like hinges, handles, locks etc. Complete job with all necessary fixing arrangement with all respect as per drawing and as directed by the Architect. | Sft | 161
5 | Full Height locker Shelve & Storage area Cabinets.
Providing, making and fixing Full Height locker Shelve & Storage area Cabinet upto 6'-0" High & 18" deep, completely madeup of 3/4" thick Lassani Laminated MDF board Complete structure case including Intermediate Partitions / shelves and drawers with match PVC lipping all around exposed surface edges, 3/4" thick MDF Cabinet shutters having Deco Paint finish (approved color by Architect), Using best quality approved S.S Finish hardware's like hinges, handles, locks etc. Complete job with all necessary fixing arrangement with all respect as per drawing and as directed by the Architect.
i. | Locker Shelves Floor Cabinet upto 6'-0" high in Passage areas. | Sft | 110
ii. | Floor Cabinet upto Ceiling Height in Storage room. | Sft | 115
6 | Kitchen Cabinets:
a. | Base Cabinets:
Providing, making and fixing Kitchen Floor Cabinets 3'-0" high and 24" deep made up of 3/4" thick Laminated MDF board (SRK, Lassani or equivalent) complete structure case including Shutters / Intermediate Partitions / shelves and drawers with match PVC lipping all around exposed surface edges, laying 1" thick approved Marble counter top having round edges & Provision of sink counter, Using best quality approved S.S Finish hardware's like hinges, handles, locks etc. Complete job with all necessary fixing arrangement with all respect as per drawing and as directed by the Architect. (Base Rate of Marble: 2500/-sft)
i. | Main Kitchen: Floor Cabinet (with Sinks Provision). | Sft | 35.25
b. | Wall Cabinets
| Providing, making and fixing Wall Cabinets upto 2'-6" high & 16" deep madeup of 3/4" thick Lassani Laminated MDF board Complete structure case including Shutters / Intermediate Partitions / shelves and drawers with match PVC lipping all around exposed surface edges, Using best quality approved S.S Finish hardware's like hinges, handles, locks etc. Complete job with all necessary fixing arrangement with all respect as per drawing and as directed by the Architect. | Sft | 30
7 | Full Height Floor Cabinet for Cleaners area.
| Providing, making and fixing Full Height Floor Cabinet upto 7-0" high & 24" deep on both side walls, completely madeup of 3/4" thick Lassani Laminated MDF board Complete structure case including Shutters / Intermediate Partitions / shelves and drawers with match PVC lipping all around shutters / drawers & exposed surface edges, Using best quality approved S.S Finish hardware's like hinges, handles, locks etc. Complete job with all necessary fixing arrangement with all respect as per drawing and as directed by the Architect. | Sft | 75
8 | L-Shape Floor Mounted Wooden Sofa Seater in Small Hub area. (08 Seater)
Providing, making and fixing HL-Shape Floor Mounted Wooden Sofa Seater consist of following material are: Size: 7'-8"+4'-6" Length x 39" deep & 3'-0" high.
i. | Using 3/4" thick Laminated MDF complete Structure with rough wooden framing including Bench structure , made as per detail drawing with all respect.
ii. | Laying approved 3" thick Cushion Bed (Master or equivalent Foam) over complete surface of Sofa Seater (Seats with Front / Back) with round edging using best quality adhesive for pasting as per detail drawing.
iii. | Wrapping Brass Finish leatherite Fabric over Cushion (seat / back) surface using quality finish stitching including edges around cushion / bench exposed fabric surface, complete as per detail drawing.
| Complete job with all respect with necessary fixing arrangement, Cleaning, Polish, bending, cutting, etc including Termite treated rough wood, best quality hardware's as per drawing details and as per instruction of Architect. | No | 1
38 | Additional M.S Framing in Partition wall Behind DB
| Providing, fabrication and fixing in position of Additional M.S Framing in Partition wall Behind DB, consisting of M.S framing structure of 2"x4" hollow pipe of 16 gauge, all members will be proper welded with each other, fixing of framing on floor and with existing RCC ceiling from top with the support of approved hardware's and fittings, including applying two coats of anti rust coating of approved brand to all M.S work & painting to all MS work with approved paint, Colour & shade, complete job with all necessary fixing arrangements, all hardware's, all hardware's, wastage, cutting, fabrication, welding, lifting, clipping, scaffolding, painting, etc., complete in all respect as per drawings, specifications and as instructed by the Architect. (For Payment Installed Running Length will be measured without any depth and thickness) | Rft | 30
39 | As-Built and Shop Drawings
| Making of CCP, As-Built & Shop Drawings (Civil, MEP, IT, AV, CCTV etc) on AutoCAD 2018 or latest version with sectional details in coordination with all the relevant contractors/teams complete in all respects as per instructions of consultants prior to execution of work. | Job | 1
Total Cost of 11th Floor Finishes Work =

## ELEC SUMM
S.# | DESCRIPTION | SUPPLY (Rs.) | INSTALLATION (Rs.) | AMOUNT (Rs.)
1 | SECTION - A WIRING & WIRING ACCESSORIES
2 | SECTION - B CABLE CONTAINMENT
3 | SECTION - C SWITCHES & SOCKETS
4 | SECTION - D LIGHTING FIXTURES
5 | SECTION - E MAIN SUBMAIN CABLES
6 | SECTION - F DISTRIBUTION BOARDS
7 | SECTION - G INTELLIGENT LIGHTING CONTROL SYSTEM
8 | SECTION - H WIRING FOR LOW CURRENT SYSTEMS
9 | SECTION - I UNINTERRUPTIBLE POWER SUPPLY
10 | SECTION -J PERSONAL PROTECTIVE EQUIPMENTS
11 | SECTION - K WCR & LOAD FITNESS
12 | SECTION - L SHOP DRAWINGS / AS-BUILT DRAWINGS
Total Amount (Rs.)

## ELEC BOQ
S.# | DESCRIPTION | QTY | UNIT | Verified QTY | SUPPLY |  | INSTALLATION |  | AMOUNT (Rs.) | Brand/Model | Lead Time | Remarks
[5 empty] | RATE (Rs.) | AMOUNT (Rs.) | RATE (Rs.) | AMOUNT (Rs.)
SECTION - A WIRING & WIRING ACCESSORIES
Supply, Installation, Testing & Commissioning of the following items including all material, labour & tools required for completion of work as per item description, specifications & drawings including cutting, chiseling, making good and all necessary accessories such as bends, junction boxes, conduit sockets, earth connecting point connectors, etc. as shown on drawings, specifications and approval by the Engineer. Complete in all respects. Note: - The cost of wiring items shall include Imported Wago Connectors and Imported flexible Polyamide Conduit of appropriate size on each light point. - The circuit wire drop shall be sufficient as per ceiling levels. - The wiring shall be done with LSZH Wires / Cables. - Megger Test of each circuit to be done by the Contractor. - All General Wiring grade should be 450/750 copper with green/yellow Color.
- Surface conduiting wherever required shall be done in aesthetic manner. - Wherever the circuits are running in cable tray, it will enter / leave tray using proper glands / Junction boxes (IP44). The cost of all such accessories to be included in wiring cost. - All electrical circuits and power outlets shall be numbered (i.e. circuit number and distribution board number) and the circuit schedule of the distribution board must accurately reflect the installation. The load across all phases must be balanced. - The ECC to be run with each circuit shall be loop-in and loop-out type, joints are not allowed. It will be green in color (Refer detail BoQ & drawings) - All the cables shall be colour coded according to phases / types of services.
1 | Circuit wiring from DB to Switchboard including any wiring from switch board to switch board with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core Cu/LSZH wires in 25mm dia PVC conduit as shown in drawings. | 10 | No.
2 | Wiring for light point from Switchboard to first light point with phase 1.5 Sq.mm, common neutral 2.5 Sq.mm and common ECC 2.5 Sq.mm, 1-core Cu/LSZH wires in 25mm dia PVC conduit as shown on drawings. | 54 | No.
a | Point to Point wiring using the same wires & conduit size as mentioned in the above item. | 234 | No.
3 | Emergency Circuit Wiring for Group Control light fixtures from DB to first light point with 2x2.5 Sq.mm + ECC 2.5 Sq.mm 1-core Cu/LSZH wires in 25mm dia PVC conduit as shown on drawings. | 3 | No.
a | Point to Point wiring using the same wires & conduit size as mentioned in the above item. | 41 | No.
4 | Circuit Wiring of 13A/15A Switch Socket units (RAW Power) from DB to first outlet including wiring with in the same technology box / cable cubby / adjacent power outlets in separate back boxes with following size of 1-core Cu/LSZH wires in 25mm dia PVC conduit as shown in the drawings.
a | 2 x 4 Sq.mm + ECC 1 x 4 Sqmm, Cu/LSZH wires | 45 | No.
b | Same as above item but wiring from outlet to outlet | 73 | No.
5 | Circuit Wiring for Hand Dryers from DB to 20A DP Switch with 2 x 4 Sq.mm + ECC 1 x 4 Sqmm, Cu/LSZH wires1 core Cu/LSZH/ wires in 25mm dia PVC conduit as shown in the drawings. Including wiring to equipment. | 5 | No.
a | Same as above item but wiring from outlet to outlet | 2 | No.
7 | Circuit Wiring for office VRF indoor Fan Coil Unit from DB to 10A DP Isolator with 2 x 2.5 Sq.mm + ECC 1 x 2.5 Sqmm, Cu/LSZH wires in 25mm dia PVC Conduit , as shown in drawings. | 15 | No.
b | Same as above item but wiring from outlet to outlet | 11 | No.
8 | Circuit Wiring for FCR VRF indoor Unit from DB to 25A DP Isolator with 3C-4 Sqmm Cu/LSZH/LSZH wires in 25mm dia PVC conduit as shown in the drawings. Including wiring to equipment. | 1 | No.
9 | Circuit Wiring for office VRF outdoor Unit from DB to 16A 4P Isolator with 4C-4 Sqmm Cu/LSZH/LSZH + ECC 1C 4 Sqmm Cu/LSZH wires in 25mm dia PVC conduit as shown in the drawings. Including wiring to equipment. | 2 | No.
10 | Circuit Wiring for DB to 20A DP Switch (For water heater & exhaust fans) with 2 x 4 Sq.mm + ECC 1 x 4 Sqmm, Cu/LSZH wires1 core Cu/LSZH/ wires in 25mm dia PVC conduit as shown in the drawings. Including wiring to equipment. | 3 | No.
11 | Circuit Wiring for FCR VRF outdoor Unit from DB to 16A 4P Isolator at roof top with 4C-4 Sqmm Cu/LSZH/LSZH + ECC 1C 4 Sqmm Cu/LSZH wires in 25mm dia PVC conduit as shown in the drawings. Including wiring to equipment. | 1 | No.
Note: -Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. -Wires color of UPS circuits should be different from RAW Power -Wiring for outgoing circuits of MCCs required for Fire Fighting, HVAC & Plumbing Services shall be in the scope of Mechanical Works.
Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY)
SECTION - B CABLE CONTAINMENT
1 | Supply & Laying of following sizes of PVC/UPVC Conduits including all accessories such as bends, sockets, j-boxes, flexible conduits, metal saddles e.t.c for Main / Sub Main Power, Telephone & Data Cables, concealed / surface on wall as per design drawings. Provide Pull boxes where ever required. Note: -The below mentioned conduits will be used for items where description of the item clearly states that the conduit is not inclusive or already installed. -This section will also cover empty conduit runs, sleeves, conduit risers etc.
a | 25mm dia PVC Conduit | 50 | Rm.
b | 38mm dia PVC Conduit | 50 | Rm.
c | 25mm dia Imported Flexible Polyamide Conduit with PVC Gland | 35 | Rm.
d | 25mm dia AL EMT conduit | 15 | Rm.
2 | Supply & Installation of following sizes of 16-SWG G.I made Ceiling / Floor / Wall Pull Boxes for data / voice / power / UPS circuits, recessed on wall or column as per design drawings. Complete in all respect.
a | 200mm x 200mm x 50mm (For Communication System) | 25 | No.
b | 300mm x 300mm x 50mm | 5 | No.
c | 300mm x 300mm x 50mm | 5 | No.
3 | Supply & Installation of 16 SWG Powder Coated MS Sheet Steel Back Boxes for installation of Switches, Sockets, Voice & Data Outlets, Isolators etc as per drawings and details including all accessories. | 140 | No.
4 | Supply and Installation of following sizes of Imported 36 micron GI 16 SWG Perforated Cable Tray / Cable Ladder with 18 SWG Solid Cover of 4 feet each, the finish form shall be supplied at site after complete process of degreesing, derusting, phosphating and antirust primer. The Fabrication of tray shall be done at factory with complete coorindation from site routing as per design / shop drawings, complete in all respects. The Complete accessories for all supporting hangers, brackets, elbows, tee & bends to be provided by Contractor. Note: - Color Printed Tags to be provided at every 3 Meter Length. - Threaded Rods & C-Channel base is required for hanging from Ceiling. - All the accessories such as thread M10 rods shall be cadmium plated/stainless steel made such as nuts, screws, bolts, wire etc - Wall Hanger Supports to be provided wherever required. - U-shaped fischer plates to be used for joints. - 6 Sqmm braided copper terminals with lugs for bonding to be done with every joint
a | 300mm x 100mm Horizontal (IT Room) With Ceiling Mounted Hanging Accessories | 10 | Rm.
b | 450mm x 100mm Horizontal 2-Partition With Ceiling Mounted Hanging Accessories | 95 | Rm.
6 | Supply & Installation of the following types of Imported Floor Outlet Boxes without face plates made of 16 SWG G.I Sheet, recessed in ground as per design drawings.
a | Type-A (250mm x 250mm x 70mm): 2 No. 13A International Switch Sockets + 1 No. RJ-45 Duplex Outlet | 10 | No.
b | Type-B (250mm x 250mm x 70mm): 2 No. 13A International Switch Sockets + 1 No. RJ-45 Simplex Outlet | 6 | No.
c | Type-C' (250mm x 250mm x 70mm): 2 No. 13A International Switch Sockets | 25 | No.
d | Type-C' (350mm x 350mm x 70mm): 4 No13A International Switch Sockets + + 1 No. RJ-45 Simplex Outlet | 4 | No.
e | Type-D (250mm x 250mm x 70mm): 2 No. 13A International Switch Sockets + 2 No. RJ-45 Duplex Outlet | 4 | No.
Note: Contractor is advised to confirm the sizes, running lengths and termination as per site conditions before commencement of work. All the conduits / cable tray crossings through partition walls shall be properly sealed by fire retardant material after installation.
Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY)
SECTION - C SWITCHES & SOCKETS
Supply & Installation of following Switches and socket outlets recessed / surface on wall in already installed Backbox or as per design drawings. Following makes and models are suggested in white color but the final recommendation and approval to be given by the Architect on physical samples. Switches: Vivace Sockets: Vivace Isolators: Schneider, Gewiss, Walther Industrial Sockets: PCE, Gewiss, Walther
1 | One Gang Switch Unit | 6 | No.
2 | Two Gang Switch Unit | 4 | No.
3 | Three Gang Switch Unit | 14 | No.
4 | One Gang PIR By-Pass Switch | 3 | No.
5 | 13A Flat Pin Duplex Switch Socket unit | 2 | No.
6 | 13A International Switch Socket unit | 195 | No.
7 | 15A 3-Pin Round Switch Socket unit | 2 | No.
8 | 20A DP Switch (Hand Dryer + Water Heater) | 8 | No.
9 | 20A DP Isolator (Water Heater) | 3 | No.
10 | 10A FUSED DP Isolator | 26 | No.
11 | 25A DP Isolator | 2 | No.
12 | 16A TP Isolator | 3 | No.
13 | 32A TP Isolator | 2 | No.
14 | Blank plate with knockout | 6 | No.
15 | 32A 3-Pin (Single Phase) Industrial Socket with Plug For Communication Racks & UPS | 4 | No.
16 | Ceiling suspended cameras and wifi mounting poles (Aluminum finish) adjustable 2ft to 4ft. | 12 | No.
Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY)
SECTION - D LIGHTING FIXTURES
Supply, Installation, Testing & Commissioning of the following Light fixtures complete with all hanging accessories including clips, suspension rods / wires, ceiling frame etc. - Color temperature will be as per Architect's requirement. - Efficacy of light fixtures shall be equal to or more than 105 Lumens / Watt. - 3 Year Replacement Warranty is required both for fixture and driver. - Warranty period will start from the date of successful Testing & Commissioning - Power Factor shall be 0.9. - Minimum Operational life should be more than 50,000 Hours @L80 Rated - Light Brand = NVC
1 | 8W Recessed LED Down Lights, Cri 83 Above, Beam Angle 60 Degree, Brand Coarts, Britlite, Philips And Nvc (Typer-A) | 160 | No.
2 | 15W Surface Mounted LED Light Cylindrical, Cri 83 Above, Beam Angle 24 Degree Brand Coarts, Britlite, Philips And Nvc. (Black Housing) (Type-B) | 36 | No.
3 | 15W Surface Mounted LED Light Cylindrical, Cri 83 Above, Beam Angle 24 Degree Brand Coarts, Britlite, Philips And Nvc. (Maroon Housing) (Typer-D) | 22 | No.
4 | 15W Fancy Pendant Round Light Pendant Light Bombay Light House, Massive Lights Gallery Or Equivalent (Type-E) | 5 | No.
5 | 15W Fancy Pendant Round Light Pendant Light Bombay Light House, Massive Lights Gallery Or Equivalent (Type-F) | 4 | No.
6 | 15W Fancy Pendant Round Light Pendant Light Bombay Light House, Massive Lights Gallery Or Equivalent (Typer-G) | 3 | No.
7 | 15W Fancy Pendant Light, Spherical with Accoustic Panels, Brand: Bombay Light House, Massive Lights Gallery or Equivalent (Type-L) | 8 | No.
8 | 36W/4 Feet Pendant Light: Linear, Cri 83 Above, Beam Angle 110 Degree Brand Coarts, Britlite, Philips And Nvc. (Community Table) (Type-M) | 3 | No.
9 | 8W/M Neon Flex Rope Light with Drivers, Brand: Coarts, Britlite, Philips & NVC (Type-N) | 270 | Rm.
10 | 15W Recessed Led Down Lights, Cri 83 Above, Beam Angle 60 Degree, Brand Coarts, Britlite, Philips And Nvc. (Type-P) | 20 | No.
11 | 18W TASK LIGHT (JIT ROOM) (Type-V) | 4 | No.
12 | 8W Non-Maintained Downlight with 3 Hours Battery Backup | 33 | No.
13 | Ceiling Mounted Non-Maintained Exit Light with 3 Hours Battery Backup | 10 | No.
14 | Supply & Installation of Ceiling Mounted I.R Stand Alone Motion Sensor (Occupancy Sensor) for Lights having following specifications: Coverage Range : 360 ° Operating Voltage : 230 V AC Timing Range : 5 sec to 20 minutes Connection : Parallel Switching Mode : Auto IP Value : IP 21 (min) | 4 | No.
Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY)
SECTION - E MAIN SUBMAIN CABLES
Supply, Laying, Termination, Testing & Commissioning of the following ratings of LV Cables along with complete installation and termination accessories to be laid in already installed Cable trench / Cable ladder / Cable tray / Duct Bank including all accessories. Complete in all respects. -Imported Lugs and Connectors shall be used in LV Cables. -Bi-Mettalic Lugs to be used with Aluminum Cables. -Manual crimping of lugs is not allowed. Proper lug presser for smaller lugs and hydraulic lug presser for large size lugs should be used.
1 | From 32A TP Isolator to DB-LP-11F-A 4C-10 Sqmm Cu/LSZH/LSZH + ECC 1C-10 Sqmm Cu/LSZH | 20 | Rm.
2 | From 32A TP Isolator to DB-LP-11F-B 4C-10 Sqmm Cu/LSZH/LSZH + ECC 1C-10 Sqmm Cu/LSZH | 25 | Rm.
3 | From DB-LP-11F-A to DB-FCR-11F 4C-6 Sqmm Cu/LSZH/LSZH + ECC 1C-6 Sqmm Cu/LSZH | 25 | Rm.
4 | From DB-LP-11F-B to DB-FCR-11F 4C-6 Sqmm Cu/LSZH/LSZH + ECC 1C-6 Sqmm Cu/LSZH | 40 | Rm.
5 | From DB-FCR-11F to Rack PDU 3C- 4Sqmm Cu/LSZH/LSZH | 10 | Rm.
6 | From DB-FCR-11F to 3kVA UPS to PDU 3C- 4Sqmm Cu/LSZH/LSZH | 10 | Rm.
7 | From DB-FCR-11F to UDB-11F 2C-4Sq.mm Cu./LZH/LZH + ECC 1C-4Sq.mm Cu./LZH CABLE | 10 | Rm.
8 | From DB-FCR-11F to UPS to UDB-11F 2C-4Sq.mm Cu./LZH/LZH + ECC 1C-4Sq.mm Cu./LZH CABLE | 10 | Rm.
9 | From FCR RACKS TO EARTH CONNECTION POINT ECC 1C-6 Sqmm Cu/PVC | 20 | Rm.
Note: - Contractor is instructed to confirm the cable running lengths and termination as per site conditions before commencement of work. - Imported Lugs and Connectors shall be used in LV Cables. - Megger Test of all LV Cables to be done by contractor.
Total Amount (Rs.) Sec - E (CARRIED FORWARD TO SUMMARY)
SECTION - F DISTRIBUTION BOARDS
Supply, Placement, Installation, Testing & Commissioning of following Distribution Boards as shown on drawing made with 14/16 SWG sheet steel housing, flush in wall / surface type, with approved color and having specified circuit breakers and components as shown in drawings / specified in list of approved manufacturers. Shop drawings shall be submitted by the contractor before fabrication. Notes: 1) All the DB should be front accessible and maintainable. 2) Cost of Lighting Control Relays & Power Supplies should be included in Distribution Boards . 3) The transportation and placement of DBs upto dedicated location is also included in the work scope, complete in all respects including leveling, grouting etc. 4) Laser engraved tags required as mention in SLDs 5) Space for circuit tagging required with permanent installation on protective sheet via rivets 6) Tin platted Imported Cu bus bar with heat shrink color coded sleeves to be used. 7) Hindged protective metallic door required with knob/handle. 8) Braided Door earth required. 9) Lockable handle required for main door. 10) As-built drawing pocket. 11) Cable hanging arrangement. Minimum One Year Warranty Required from date of successful commissioning on site.
1 | DB-LP-11F-A | 1 | No.
2 | DB-LP-11F-B | 1 | No.
3 | DB-FCR-11 | 1 | No.
4 | UDB-11-F | 1 | No.
Total Amount (Rs.) Sec - F (CARRIED FORWARD TO SUMMARY)
SECTION - G LIGHTING CONTROL SYSTEM
Supply, Installation, Testing & Commissioning of following items for complete Lighting Control System (KNX Based) including all labour, tools etc. Complete in all respect as shown on drawing.
1 | KNX Intelligent Lighting Control Switch for Lighting Control System including all accessories and equipments etc.
a | KNX 4 Gang Intelligent Input Units with bus coupler & LCD Touch Display | 2 | No.
2 | KNX Control Cable for system wiring from Relay to Lighting control switches and other devices in 25mm dia PVC Conduit as shown in the drawings. Complete in all respects. (KNX Approved Cable) | 100 | Rm.
3 | Programming, testing and commissioning of complete system upto the entire satisfaction of client and consultant including following: - Intelligent Lighting Control System Schedule (Software + Manual) - Documentation - Web based featuring an extensive schedule Program - Manual Setting in DB with accessories and tagging | 1 | Job
Note: - Contractor shall provide the complete Technical Literature for the offered system. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - G (CARRIED FORWARD TO SUMMARY)
SECTION - H WIRING FOR LOW CURRENT SYSTEMS
Supply, Laying, Termination, Testing & Commissioning of the following communication cables required for ELV Systems in Conduit, Cable Tray, Cable Trench, including termination at both ends.
FIRE ALARM SYSTEM
1 | 2C-1.5 Sq.mm Fire Resistant Shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia AL EMT Conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respect. (Cavicel SR-114H or Equivalent) | 225 | Rm.
PUBLIC ADDRESS SYSTEM
2 | Supply and Installation of of Wiring for Public Address / Back Ground Music System using 2C, 1.5 Sq.mm flexible Speaker Cable as per zoning layout shown in drawings in 25 mm dia PVC conduit. Complete in all respects. | 200 | Rm.
ACCESS CONTROL SYSTEM
3 | Supply and Wiring of CAT-6, UTP Cables from Door Controller to all devices as shown in the schematic diagram in 25mm dia PVC Conduit, including termination and tagging at both ends. Complete in all respects. | 300 | Rm.
Note: - Contractor shall provide the complete Technical Literature for the offered system. Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - H (CARRIED FORWARD TO SUMMARY)
SECTION - I UNINTERRUPTIBLE POWER SUPPLY
Supply, Installation, Testing, Commissioning and top supervision of following UPS at site as per following specifications, Complete in all respect.
1 | Rating : 1 kVA True Online Double Conversion Pure sine wave Microcontroller based. Input voltage: 220V AC Input frequency: 50 Hz Output voltage: 220 Volts Single Phase IN & Single Phase Out Output p.f: 0.9 (Built in PFC) Effiiceincy: 92 to 96% Backup Time: 10 mins at full load. Batteries: Dry Sealed Maintenance Free In built Overload: 110% for 10min Capacity: 125% for 1-min Operating Temp: 0 to 40 degC Mounting: Wall Mounted/floor stand Warranty: 1 Years for UPS & Batteries User friendly LCD display for real time UPS status Cold start of load during power failure Transient/Surge Suppressor EMI/RFI Filter Built-in manual and static by-pass switch Remote & local emergency power off function RS-232/RJ-45 connectivity with power management software Power Chute Network Shutdown. SNMP Management Card / Modbus Card | 1 | No
Note: - Contractor shall provide complete technical literature for the quoted equipment for approval of Consultant before procurement.
Total Amount (Rs.) Sec - I (CARRIED FORWARD TO SUMMARY)
SECTION - J PERSONAL PROTECTIVE EQUIPMENTS
| Include below as billable item: Provision of PPEs for clients and consultants with following while doing construction: Cotton Dangree / Coverall color: Light Grey Steel toe Shoes Jaguar / Catapiller / Color: Black Safety Helmet Economical with "chin strap" / Color: Blue / White / Red | 1 | Job
Total Amount (Rs.) Sec - J (CARRIED FORWARD TO SUMMARY)
SECTION - K WCR & LOAD FITNESS
| Obtaining NOC / Approval Certificate for entire electrical installation works from approved Electric Inspector, Regional office (official inspection charges/fee will be paid directly and separately by the employer) | 1 | Job
Total Amount (Rs.) Sec -K (CARRIED FORWARD TO SUMMARY)
SECTION - L SHOP DRAWINGS / AS-BUILT DRAWINGS
1 | Preparation of Shop drawings and as-built drawings of all electrical and allied works after final approval from the consultant/client. 1) Submission of as-built drawings 2 sets after work completion of each floor and 3 sets & soft copy of complete electrical works after final commissioning of project. Approval of final bills are subject to completion of as built drawings. 2) Documents including the Operation and Maintenance Manuals. 3) Testing Reports and Measurement Sheets. 4) Warranty certificates for products. | 1 | Job
Total Amount (Rs.) Sec - L (CARRIED FORWARD TO SUMMARY)

## ACMV
Bill of Quantities
ACMV Works
EY ISLAMABAD
[6 empty] | MATERIAL |  | LABOUR |  | TOTAL | BRAND | LEAD TIME | REMARKS
S. No. |  | DESCRIPTION | UNIT | BOQ QTY | VERIFIED QTY | RATE | AMOUNT | RATE | AMOUNT | AMOUNT
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of Consultant
1 |  | Servicing, re-location, re-installation, testing and commissioning of existing VRF indoor units (Brand: MIDEA) in coordination with Landlord, of different capacities with central controller complete in all respects, ready to operate including supply & installation of supports, brackets, flexible duct connector / connection, rubber isolators, flashing, power wiring from isolation box to unit (10' to 15' radius), control wiring termination etc, complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 1.1 | Cassette Type Units (0.75 TR) | Nos. | 3 | 3 | 25000 | 75000 | 12000 | 36000 | 111000
| 1.2 | Cassette Type Units (1.0 TR) | Nos. | 5 | 5 | 25000 | 125000 | 12000 | 60000 | 185000
| 1.3 | Cassette Type Units (1.25 TR) | Nos. | 4 | 4 | 25000 | 100000 | 12000 | 48000 | 148000
| 1.4 | Cassette Type Units (2.0 TR) | Nos. | 8 | 8 | 25000 | 200000 | 12000 | 96000 | 296000
| 1.5 | FAHU | Nos. | 2 | 2 | 35000 | 70000 | 20000 | 40000 | 110000
2 |  | Supply & installation of refrigerant pipes for existing units (liquid + gas) with 1/2" thick expended close cell rubber foam insulation, PVC tape wrapping complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. Note: >All existing refirgerant piping to be re-used by Contractor shall first be approved by Project Manager/Consultant as per approved drawing. > VRF / VRV Units copper pipes sizes & quantities shall be vary according to the equipment brand / selection) > Floors piping only for existing units, riser piping will remain same. |  |  |  |  | 0 |  | 0
|  | All hard pipes except 1/4" |  |  |  |  | 0 |  | 0
| 2.1 | 1/4" dia | Rft | 50 | 50 | 650 | 32500 | 300 | 15000 | 47500 | Pipe: Mueller Insulation: Aeroflex | 4 Weeks
| 2.2 | 3/8" dia | Rft | 70 | 70 | 1050 | 73500 | 300 | 21000 | 94500
| 2.3 | 1/2" dia | Rft | 65 | 65 | 1470 | 95550 | 300 | 19500 | 115050
| 2.4 | 5/8" dia | Rft | 50 | 50 | 1950 | 97500 | 300 | 15000 | 112500
| 2.5 | 3/4" dia | Rft | 20 | 20 | 2430 | 48600 | 300 | 6000 | 54600
| 2.6 | 7/8" dia | Rft | 10 | 10 | 2900 | 29000 | 400 | 4000 | 33000
| 2.7 | 1 1/8" dia (also for 1") | Rft | 33 | 33 | 3910 | 129030 | 400 | 13200 | 142230
| 2.8 | 1 3/8" dia (also for 1-1/4") | Rft | Rate only | 40 | 5500 | 220000 |  | 0
| 2.9 | 1 5/8" dia (also for 1-1/2") | Rft | Rate only | 40 | 6470 | 258800 |  | 0
|  | Supply and Installation of Exhaust Air Fans (50 CFM) | Nos. | 5 | 5 | 15000 | 75000 | 1000 | 5000 | 80000 | SISTEVAN | 4 Weeks
3 |  | Supply & charging of refrigerant gas for existing units (to be done wherever required due to relocation OR changes of refrigerant pipe size) complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Lot | 1 | 1 | 180000 | 180000 | 50000 | 50000 | 230000 | Honeywell | 1 Week
4 |  | Supply & installation of control wiring (existing units) in G.I. conduit for external / PVC conduit for internal area from outdoor unit to indoor unit including microprocessor & central controller wiring & fixing / installation of central controller supplied with units complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Lot | 1 | 1 | 415000 | 415000 | 75000 | 75000 | 490000 | Pioneer / Pakistan | 2 Weeks
5 |  | Supply & installation of 18 SWG powder quoted G.I. sheet metal tray with cover for refrigerant pipes and control wiring (existing units), complete in all respects including hangers, supports brackets complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Rft | 15 | 15 | 1200 | 18000 | 200 | 3000 | 21000 | Al-Fazal Engineering | 4 Weeks
6 |  | Supply & installation of uPVC make class D SCH-40 pipe (existing units) for internal area with 3/8" thick expanded closed cell rubber foam insulation, PVC tape wrapping for condensate drain including support hangers, excavation, cutting, chiseling and making good complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. |  |  |  |  | 0 |  | 0
| 6.1 | 1" dia | Rft | 310 | 310 | 650 | 201500 | 100 | 31000 | 232500 | Pipe: AGM Insulation: Aeroflex | 2 Weeks
| 6.2 | 1.25" dia | Rft | 110 | 110 | 780 | 85800 | 100 | 11000 | 96800
| 6.3 | 1.5" dia | Rft | 10 | 10 | 1200 | 12000 | 125 | 1250 | 13250
| 6.4 | 2" dia | Rft | 2 | 2 | 2000 | 4000 | 150 | 300 | 4300
7 |  | Supply, fabrication and installation of machine made G.I sheet metal duct different sections supply, return, fresh & exhaust air including plenums, splitter dampers, guide vanes, flexible duct connector/connection, access door, transformation, plenums chambers, wooden frame, anchors supports & hangers complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Sqft | 580 | 580 | 600 | 348000 | 100 | 58000 | 406000 | ISL | 2 Weeks
8 |  | Supply & installation of 3/4" thick 25kg/m3 density rubber foam (XLPE) adhesive insulation with aluminum foil over internal area ducts, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqft | 580 | 580 | 500 | 290000 | 80 | 46400 | 336400 | Thermobreak | 3 Weeks
9 |  | Supply & installation of aluminum fabricated powder coated exhaust & fresh Air louvers including wooden frame, rain protection sheet bird mesh etc complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. |  |  |  |  | 0 |  | 0
| 9.1 | 4" dia | Nos. | 3 | 3 | 3000 | 9000 | 1000 | 3000 | 12000 | Steel Craft / Engatech | 6 Weeks
| 9.2 | 14" x 8" | Nos. | 1 | 1 | 4500 | 4500 | 1000 | 1000 | 5500
| 9.3 | 14" x 10" | Nos. | 1 | 3 | 4500 | 13500 | 1000 | 3000 | 16500
10 |  | Supply, installation of Aluminum fabricated, powder coated Grills, Diffusers and Registers for supply air, return air, exhaust air & fresh air of different sizes (Grade A ), wooden frame, supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. |  |  |  |  | 0 |  | 0
| 10.1 | Registers / Diffuser with Damper |  |  |  |  | 0 |  | 0
| i. | 6" x 6" | Nos. | 3 | 3 | 4000 | 12000 | 1000 | 3000 | 15000 | Steel Craft / Engatech | 6 Weeks
| 10.2 | Grills |  |  |  |  | 0 |  | 0
| i. | 6" x 4" | Nos. | 12 | 6 | 3000 | 18000 | 1000 | 6000 | 24000
| ii. | 6" x 6" | Nos. | 2 | 5 | 3000 | 15000 | 1000 | 5000 | 20000
| iii. | 8" x 4" | Nos. | Rate only |  | 4000 | 0 | 1000 | 0 | 0
| iv. | 10" x 4" | Nos. | Rate only |  | 4000 | 0 | 1000 | 0 | 0
| v. | 24" x 6" | Nos. | Rate only | 2 | 4500 | 9000 | 1000 | 2000 | 11000
| vi. | 38" x 26" | Nos. | Rate only |  | 35000 | 0 | 1000 | 0 | 0
11 |  | Supply & installation of Volume Control Damper in 16 SWG G.I sheet metal with gas kits, nut bolts, complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. |  |  |  |  | 0 |  | 0
| 11.1 | 6" x 4" | Nos. | 9 | 6 | 4000 | 24000 | 1000 | 6000 | 30000 | Steel Craft / Engatech | 6 Weeks
| 11.2 | 6" x 6" | Nos. | 3 | 5 | 4000 | 20000 | 1000 | 5000 | 25000
| 11.3 | 8" x 4" | Nos. | Rate only | 2 | 4000 | 8000 | 1000 | 2000
| 11.4 | 8" x 6" | Nos. | Rate only | 2 | 4500 | 9000 | 1000 | 2000
| 11.5 | 10" x 4" | Nos. | Rate only | 2 | 4500 | 9000 | 1000 | 2000
12 |  | Supply & installation of rubberfoam acoustical duct sound liner adhesive with1/2" thick in supply air duct complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Sqft | 120 | 120 | 500 | 60000 | 100 | 12000 | 72000 | AEROFOAM | 3 Weeks
13 |  | Stencilling & Identification work on supports, hangers, platform of condensing units etc complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Lot | 1 | 1 | 90000 | 90000 | 10000 | 10000 | 100000
14 |  | Testing, balancing and commissioning of air side of the system (from independent agency) complete in all respects including air measurement & balancing, temp, pressure & electrical data of related equipment etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job. | 1 | 1 | 0 | 0 | 100000 | 100000 | 100000
15 |  | Making of Shop drawings on Auto CAD (latest version) with section details, equipment foundation details etc, As Built drawings Auto CAD (latest version), Documentation Technical / Operational Manual & LOG Book for each equipment etc, complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job. | 1 | 1 | 100000 | 100000 | 10000 | 10000 | 110000
|  | Total Cost of Works with I.Tax Rs. |  |  |  |  | 3584780 |  | 826650 | 3900630
Note:
1) | Electric power wiring / supply to be provided at outdoor, indoor units & other ACMV equipment with isolation box by client / electrical contractor.
2) | The refrigerant pipes sized + quantity provided for reference only. The contractor / supplier shall calculate the refrigerant pipes, sized & length as per the drawing provided and shall submitted refrigerant piping layout to consultant for approval.
3) | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
4) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
5) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## FSS BOQ
Bill of Quantities
Fire Suppression Services
EY Islamabad (11th. Floor)
S.No. |  | Description | Unit | BOQ QTY | VERIFIED QTY | Material |  | Labour |  | Total | BRAND | LEAD TIME | REMARKS
[6 empty] | Rate | Amount | Rate | Amount | Amount Rs.
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression system including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1 |  | MS Sch-40 seamless pipes including all specials fittings UL listed FM approved, threaded, welded joints, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, supports and hangers, sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
| i. | Dia 1" (Threaded fitting) | Rft. | 120 | 480 | 850 | 408000 | 250 | 120000 | 528000 | PROTECK | 4 Weeks
| ii. | Dia 1-1/4" (Threaded fitting) | Rft. | 20 | 80 | 1200 | 96000 | 275 | 22000 | 118000
| iii. | Dia 1-1/2" (Threaded fitting) | Rft. | 15 | 60 | 1450 | 87000 | 300 | 18000 | 105000
| iv. | Dia 2" (Threaded fitting) | Rft. | 5 | 40 | 1880 | 75200 | 350 | 14000 | 89200
| v. | Dia 2-1/2" (Welded joints fitting) | Rft. | 5 | 20 | 2860 | 57200 | 400 | 8000 | 65200
2 |  | Sprinkler Heads | [6 empty] | 0
| i. | Sprinkler Upright type quick response (Existing as per site handover) | Nos. | 15 | 15 |  | Existing | Existing |  |  | Shield | 8 Weeks
| ii. | Sprinkler Concealed Pendent type with cover plate, Quick Response K = 5.6 (Opening Temperature 57ºc) | Nos. | 60 | 60 | 8600 | 516000 | 1000 | 60000 | 576000
| iii. | SS Flexible connector for sprinklers 3 feet length. | Nos. | 60 | 60 | 10800 | 648000 | 750 | 45000 | 693000 | LIFFCO | 8 Weeks
3 |  | Fire extinguishers with fixing accessories. |  |  |  |  | 0 |  | 0
| i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 2 | 2 | 28000 | 56000 | 1000 | 2000 | 58000 | FIREX | 12 Weeks
| ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 2 | 2 | 17000 | 34000 | 1000 | 2000 | 36000
| iii. | Type Class K FX-5 (6 Litre Wet chemical fire extinguisher). | Nos. | 2 | 2 | 52000 | 104000 | 1000 | 2000 | 106000
| iv. | Automatic fire extinguisher (10 Kg. Dry Chemical Powder) | Nos. | 1 | 1 | 26000 | 26000 | 2000 | 2000 | 28000
4 |  | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1 | 1 | 110000 | 110000 | 15000 | 15000 | 125000 | NAFFCO | 2 Weeks
5 |  | Making of As-Built & Shop Drawings on AutoCAD 2018 or latest version with sectional details complete in all respects as per instructions of consultant. | Job. | 1 | 1 | 10000 | 10000 | 10000 | 10000 | 20000
6 |  | Painting, identification and tagging to the installations and equipments. | Job. | 1 | 1 | 25000 | 25000 | 45000 | 45000 | 70000 | Berger | 2 Weeks
7 |  | Flushing of entire fire pipe work according to (NFPA-13). | Job. | 1 | 1 | 15000 | 15000 | 40000 | 40000 | 55000
8 |  | Testing, and commissioning of entire fire fighting installation as per Consultant's approval. | Job. | 1 | 1 | 0 | 0 | 100000 | 100000 | 100000
9 |  | NOVEC-1230 SYSYEM |  |  |  |  | 0 |  | 0
9.1 |  | CLEAN AGENT (FK-5-1-12 Stored In Cylinder - Ul Listed / Fm Approved) |  |  |  |  | 0 |  | 0
|  | Supply of clean agent in engineered cylinders of FSS with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant. |  |  |  |  | 0 |  | 0
| iii. | Clean Agent (FK-5-1-12, Fluoroketone) (14 Kg.) | Lot. | 1 | 1 | 1650000 | 1650000 | 25000 | 25000 | 1675000 | FIREX | 16 to 18 Weeks
| iv. | Engineered cylinder with head valve, top plug adapter, siphon tube, pressure gauge, brackets and all other items, complete in all respect. | Lot. | 1 | 1 | 125000 | 125000 | 15000 | 15000 | 140000 | FIREX | 16 to 18 Weeks
9.2 |  | Supply of MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant. |  |  |  |  | 0 |  | 0
| i. | Dia. 20 mm (3/4") (Threaded fitting) | Rft. | 20 | 20 | 1200 | 24000 | 300 | 6000 | 30000 | PROTECK | 2 Weeks
9.3 |  | SPRINKLER HEADS |  |  |  |  | 0 |  | 0
|  | Supply of nozzles with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant. |  |  |  |  | 0 |  | 0
|  | Brass Discharge Nozzle - 360 Degrees discharge pattern. |  |  |  |  | 0 |  | 0
| i. | Dia. 20 mm (3/4") | Nos. | 1 | 1 | 35000 | 35000 | 1000 | 1000 | 36000 | ZETA | 12 to 14 Weeks
9.4 |  | INPUT & OUTPUT DEVICES |  |  |  |  | 0 |  | 0
|  | Supply of input and output devices for the clean agent suppression system with wiring, controls & fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant |  |  |  |  | 0 |  | 0
| i. | Entinguishing Control Panel for the clean agent fire suppression system | Nos. | 1 | 1 | 225000 | 225000 | 10000 | 10000 | 235000 | ZETA | 12 to 14 Weeks
| ii. | Manual Abort / Emergency Cut Off Switch | Nos. | 2 | 2 | 15000 | 30000 | 1000 | 2000 | 32000 | ZETA | 12 to 14 Weeks
| iii. | Manual Release Switch - Single Action | Nos. | 2 | 2 | 15000 | 30000 | 1000 | 2000 | 32000 | ZETA | 12 to 14 Weeks
| iv. | Horn / Strobe | Nos. | 1 | 1 | 25000 | 25000 | 2000 | 2000 | 27000 | ZETA | 12 to 14 Weeks
| v. | Alarm Bell | Nos. | 1 | 1 | 17000 | 17000 | 2000 | 2000 | 19000 | ZETA | 12 to 14 Weeks
9.5 |  | ACTUATION DEVICES |  |  |  |  | 0 |  | 0
|  | Supply of actuation devices with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant. |  |  |  |  | 0 |  | 0
| i. | Solenoid Actuator for the specified cylinder size | Nos. | 1 | 1 | 90000 | 90000 | 5000 | 5000 | 95000 | ZETA | 12 to 14 Weeks
| ii. | Manual Control Head for manual actuation of cylinder with safety pull pin | Nos. | 1 | 1 | 45000 | 45000 | 5000 | 5000 | 50000 | ZETA | 12 to 14 Weeks
| iii. | Pressure Switch to indicated system discharge with an external manual reset button | Nos. | 1 | 1 | 65000 | 65000 | 5000 | 5000 | 70000 | ZETA | 12 to 14 Weeks
| iv. | Low Pressure Switch to monitor the pressure within the cylinder | Nos. | 1 | 1 | 42000 | 42000 | 5000 | 5000 | 47000 | ZETA | 12 to 14 Weeks
9.6 |  | WIRING |  |  |  |  | 0 |  | 0
| i. | Supply of wiring of 2C, 1.5 Sq.mm fire resistant shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia MS conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Job. | 1 | 1 | 215000 | 215000 | 40000 | 40000 | 255000 | Pioneer / Pakistan | 2 Weeks
|  | Total Cost of Works with Income Tax Rs. |  |  |  |  | 4885400 |  | 630000 | 5515400
Note:
> | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## PLUMBING
Bill of Quantities
Plumbing & Sanitary Services
EY Islamabad (11th Floor)
S.No. |  | Description | Unit | BOQ QTY | VERIFIED QTY | Material |  | Labour |  | Total | BRAND | LEAD TIME | REMARKS
[6 empty] | Rate | Amount | Rate | Amount | Amount Rs.
SECTION - 01, PLUMBING FIXTURES
Supply and Installation of plumbing fixtures & faucets complete in all respects including all accessories, support, hangers, etc. ready to use as per specifications, drawings and instructions of Consultant.
1.1 |  | Wash basin (WB) including bottle trap, waste, stop cocks, etc.
| i. | Type - WB (Without Pedestal) | Nos. | Rate only |  | 42000 | 0 | 5000 | 0 | 0 | PORTA | 6 weeks
| ii. | Type - WB (Vanity) | Nos. | Rate only |  | 29000 | 0 | 5000 | 0 | 0
1.2 |  | Wash basin hot and cold water mixer, etc. |  |  |  |  | 0 |  | 0
| i. | Type - WB | Nos. | Rate only |  | 40500 | 0 | 2000 | 0 | 0
| ii. | Type - WB (for Vanity) | Nos. | Rate only |  | 40500 | 0 | 2000 | 0 | 0
1.3 |  | S.S Grease Trap 7.5 Kg inlet/outlet connections 2" dia complete in all respects. | Nos. | 2 | 2 | 215000 | 430000 | 5000 | 10000 | 440000 | Alpine | 8 weeks
1.4 |  | Bib cock brass body for Ablution. (Long Neck) |  |  |  |  | 0 |  | 0 |  | ZILVER | 6 weeks
| i. | AB | Nos. | Rate only |  | 15000 | 0 | 2000 | 0
1.5 |  | Toilet accessories complete set. |  |  | 4 |  | 0 |  | 0
| i. | Soap Dispenser | Nos. | 4 |  | 10500 | 0 | 1000 | 0 | 0 | ZILVER | 6 weeks
| ii. | Towel Rail | Nos. | Rate only |  | 8450 | 0 | 1000 | 0 |  | ZILVER | 6 weeks
| iii. | Automatic Hand Dryer | Nos. | 4 | 4 | 27500 | 110000 | 3000 | 12000 | 122000 | SIEMENS | 6 weeks
| iv. | Kitchen Sink with Mixer | Nos. | 2 | 2 | 72000 | 144000 | 7000 | 14000 | 158000 |  | 6 weeks
| v. | Toilet Roll Holder | Nos. | 6 | 6 | 6000 | 36000 | 1000 | 6000 | 42000 | ZILVER | 6 weeks
| vi. | Tissue Paper Dispenser | Nos. | 4 | 4 | 18850 | 75400 | 1000 | 4000 | 79400 | ZILVER | 6 weeks
|  | Sub Total Rs. |  |  |  |  | 0 |  | 0
|  | SECTION-02 WATER SUPPLY SYSTEM |  |  |  |  | 0 |  | 0
|  | Supply, installation, testing and commissioning of complete pipe work for cold and hot water system including all accessories required to complete systems ready to operate as per specification, drawings & instruction of Consultant. |  |  |  |  | 0 |  | 0
2.1 |  | Polypropylene Random PP-R pipes PN 20 and fittings with fusion jointing along with all types of unions, tees, bends, sockets, clamps, hangers, supports, sleeves, masking plates, chiseling, making holes making good, excavation, bedding backfilling as required complete in all respect. |  |  |  |  | 0 |  | 0
| i. | Dia. OD 25 mm | Rft. | Rate only |  | 600 | 0 | 150 | 0 | 0 | RAK THERM | 4 Weeks
2.2 |  | Same as item # 2.1 but for hot water supply with Polypropylene Random PP-R (PN -25) with Aluminium foil. |  |  |  |  | 0 |  | 0
| i. | Dia OD 25 mm | Rft. | Rate only |  | 990 | 0 | 150 | 0 | 0 | RAK THERM | 4 Weeks
| ii. | Dia. OD 32 mm | Rft. | Rate only |  | 1450 | 0 | 200 | 0 | 0
2.3 |  | Open cell rubber foam insulation 3/8" thick & pvc tape wrapping for hot water pipes. |  |  |  |  | 0 |  | 0
| i. | Dia OD 25 mm | Rft. | Rate only |  | 250 | 0 | 60 | 0 | 0 | Aeroflex | 2 Weeks
| ii. | Dia. OD 32 mm | Rft. | Rate only |  | 300 | 0 | 60 | 0 | 0
2.4 |  | Brass body gate valves / ball valves with unions. |  |  |  |  | 0 |  | 0
| i. | Size 1" | Nos. | Rate only |  | 12500 | 0 | 2000 | 0 | 0 | GALA | 4 Weeks
2.5 |  | Brass body check valve. |  |  |  |  | 0 |  | 0
| i. | Size 1" | Nos. | Rate only |  | 11800 | 0 | 2000 | 0 | 0
2.6 |  | 3 way Thermostatic mixing valve complete in all respects. |  |  |  |  | 0 |  | 0
| i. | Size 1" | Nos. | Rate only |  | 85000 | 0 | 2000 | 0 | 0
|  | Sub Total Rs. |  |  |  |  | 0 |  | 0
|  | SECTION-03 SOIL, WASTE VENT AND RAIN WATER DRAINAGE SYSTEM |  |  |  |  | 0 |  | 0
|  | Supply, fixing, testing and commissioning of equipment, pipe work required to complete the soil, waste, vent and rain water systems in all respects with accessories ready to operate as per specifications, drawings and instructions of Consultant. |  |  |  |  | 0 |  | 0
3.1 |  | uPVC pipes of approved make along with specials, fittings, bends, wye, tees, sockets, flexible connectors, sleeves, masking plates, chiseling, making hole, excavation, backfilling making good where as required jointing with rubber ring seal. |  |  |  |  | 0 |  | 0
| i. | Dia. 1-1/2" | Rft. | Rate only |  | 600 | 0 | 150 | 0 | 0 | DADEX | 2 Weeks
| ii. | Dia. 2" | Rft. | 15 | 40 | 880 | 35200 | 200 | 8000 | 43200
| iii. | Dia. 4" | Rft. | Rate only | 150 | 2350 | 352500 | 300 | 45000 | 397500
3.2 |  | Floor trap including S.S grating floor trap, inlet outlet connection complete in all respects. |  |  |  |  | 0 |  | 0
| i. | FT- with 4" P - trap | Nos. | Rate only |  | 9800 | 0 | 1000 | 0 | 0 | DADEX | 2 Weeks
|  | Sub Total Rs. |  |  |  |  | 0 |  | 0
|  | SECTION-04 SUNDRIES |  |  |  |  | 0 |  | 0
|  | Contractor will priced the sundries items for all Plumbing & Sanitary (P&S) services as per specifications, drawings and instruction of consultant. |  |  |  |  | 0 |  | 0
4.1 |  | Submittals, samples, shop drawings, inspections, As-Built drawings, operation and maintenance manuals and the like as required by specification. | Job. | 1 | 1 | 25000 | 25000 | 10000 | 10000 | 35000
4.2 |  | Testing, and commissioning entire P&S installation as per Engineer's approval. | Job. | 1 | 1 | 0 | 0 | 45000 | 45000 | 45000
Sub Total Rs.
|  | TOTAL OF ALL SECTIONS RS. |  |  |  |  | 1208100 |  | 154000 | 1362100
Note:
> | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).