## ACMV
Bill of Quantities
ACMV Works
EY ISLAMABAD
[6 empty] | MATERIAL |  | LABOUR |  | TOTAL | BRAND | LEAD TIME | REMARKS
S. No. |  | DESCRIPTION | UNIT | QTY | VERIFIED QTY | RATE | AMOUNT | RATE | AMOUNT | AMOUNT
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of Consultant
1 |  | Servicing, re-location, re-installation, testing and commissioning of existing VRF indoor units (Brand: MIDEA) in coordination with Landlord, of different capacities with central controller complete in all respects, ready to operate including supply & installation of supports, brackets, flexible duct connector / connection, rubber isolators, flashing, power wiring from isolation box to unit (10' to 15' radius), control wiring termination etc, complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 1.1 | Cassette Type Units (0.75 TR) | Nos. | 3 | 3 | 5000 | 15000 | 5000 | 15000 | 30000
| 1.2 | Cassette Type Units (1.0 TR) | Nos. | 5 | 5 | 5000 | 25000 | 5000 | 25000 | 50000
| 1.3 | Cassette Type Units (1.25 TR) | Nos. | 4 | 4 | 5000 | 20000 | 5000 | 20000 | 40000
| 1.4 | Cassette Type Units (2.0 TR) | Nos. | 8 | 8 | 5000 | 40000 | 5000 | 40000 | 80000
| 1.5 | FAHU | Nos. | 2 | 2 | 5000 | 10000 | 5000 | 10000 | 20000
2 |  | Supply & installation of refrigerant pipes for existing units (liquid + gas) with 1/2" thick expended close cell rubber foam insulation, PVC tape wrapping complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. Note: >All existing refirgerant piping to be re-used by Contractor shall first be approved by Project Manager/Consultant as per approved drawing. > VRF / VRV Units copper pipes sizes & quantities shall be vary according to the equipment brand / selection) > Floors piping only for existing units, riser piping will remain same. | [6 empty] | 0
|  | All hard pipes except 1/4" | [6 empty] | 0
| 2.1 | 1/4" dia | Rft | 50 | 50 | 650 | 32500 | 300 | 15000 | 47500 | Pipe: Mueller Insulation: Aeroflex | 4 Weeks
| 2.2 | 3/8" dia | Rft | 70 | 70 | 1050 | 73500 | 300 | 21000 | 94500
| 2.3 | 1/2" dia | Rft | 65 | 65 | 1470 | 95550 | 300 | 19500 | 115050
| 2.4 | 5/8" dia | Rft | 50 | 50 | 1950 | 97500 | 300 | 15000 | 112500
| 2.5 | 3/4" dia | Rft | 20 | 20 | 2430 | 48600 | 300 | 6000 | 54600
| 2.6 | 7/8" dia | Rft | 10 | 10 | 2900 | 29000 | 400 | 4000 | 33000
| 2.7 | 1 1/8" dia (also for 1") | Rft | 33 | 33 | 3910 | 129030 | 400 | 13200 | 142230
| 2.8 | 1 3/8" dia (also for 1-1/4") | Rft | Rate only | 50 | 5500 | 275000 |  | 0
| 2.9 | 1 5/8" dia (also for 1-1/2") | Rft | Rate only | 50 | 6470 | 323500 |  | 0
|  | Supply and Installation of Exhaust Air Fans (50 CFM) | Nos. | 5 | 5 | 15000 | 75000 | 1000 | 5000 | 80000 | SISTEVAN | 4 Weeks
3 |  | Supply & charging of refrigerant gas for existing units (to be done wherever required due to relocation OR changes of refrigerant pipe size) complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Lot | 1 | 1 | 180000 | 180000 | 50000 | 50000 | 230000 | Honeywell | 1 Week
4 |  | Supply & installation of control wiring (existing units) in G.I. conduit for external / PVC conduit for internal area from outdoor unit to indoor unit including microprocessor & central controller wiring & fixing / installation of central controller supplied with units complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Lot | 1 | 1 | 80000 | 80000 | 75000 | 75000 | 155000 | Pioneer / Pakistan | 2 Weeks
5 |  | Supply & installation of 18 SWG powder quoted G.I. sheet metal tray with cover for refrigerant pipes and control wiring (existing units), complete in all respects including hangers, supports brackets complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Rft | 15 | 15 | 1200 | 18000 | 200 | 3000 | 21000 | Al-Fazal Engineering | 4 Weeks
6 |  | Supply & installation of uPVC make class D SCH-40 pipe (existing units) for internal area with 3/8" thick expanded closed cell rubber foam insulation, PVC tape wrapping for condensate drain including support hangers, excavation, cutting, chiseling and making good complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | [6 empty] | 0
| 6.1 | 1" dia | Rft | 310 | 310 | 550 | 170500 | 100 | 31000 | 201500 | Pipe: AGM Insulation: Aeroflex | 2 Weeks
| 6.2 | 1.25" dia | Rft | 110 | 110 | 680 | 74800 | 100 | 11000 | 85800
| 6.3 | 1.5" dia | Rft | 10 | 10 | 1100 | 11000 | 125 | 1250 | 12250
| 6.4 | 2" dia | Rft | 2 | 2 | 1900 | 3800 | 150 | 300 | 4100
7 |  | Supply, fabrication and installation of machine made G.I sheet metal duct different sections supply, return, fresh & exhaust air including plenums, splitter dampers, guide vanes, flexible duct connector/connection, access door, transformation, plenums chambers, wooden frame, anchors supports & hangers complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Sqft | 760 | 760 | 600 | 456000 | 100 | 76000 | 532000 | ISL | 2 Weeks
8 |  | Supply & installation of 3/4" thick 25kg/m3 density rubber foam (XLPE) adhesive insulation with aluminum foil over internal area ducts, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqft | 760 | 760 | 500 | 380000 | 80 | 60800 | 440800 | Thermobreak | 3 Weeks
9 |  | Supply & installation of aluminum fabricated powder coated exhaust & fresh Air louvers including wooden frame, rain protection sheet bird mesh etc complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | [6 empty] | 0
| 9.1 | 4" dia | Nos. | 5 | 5 | 2800 | 14000 | 1000 | 5000 | 19000 | Steel Craft / Engatech | 6 Weeks
| 9.2 | 14" x 8" | Nos. | 1 | 1 | 4300 | 4300 | 1000 | 1000 | 5300
| 9.3 | 14" x 10" | Nos. | 1 | 2 | 4300 | 8600 | 1000 | 2000 | 10600
10 |  | Supply, installation of Aluminum fabricated, powder coated Grills, Diffusers and Registers for supply air, return air, exhaust air & fresh air of different sizes (Grade A ), wooden frame, supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | [6 empty] | 0
| 10.1 | Registers / Diffuser with Damper | [6 empty] | 0
| i. | 6" x 6" | Nos. | 5 | 5 | 4300 | 21500 | 1000 | 5000 | 26500 | Steel Craft / Engatech | 6 Weeks
| 10.2 | Grills |  |  |  |  | 0 |  | 0
| i. | 6" x 4" | Nos. | 14 | 12 | 2800 | 33600 | 1000 | 12000 | 45600
| ii. | 6" x 6" | Nos. | 4 | 3 | 2800 | 8400 | 1000 | 3000 | 11400
| iii. | 8" x 4" | Nos. | Rate only |  | 3800 | 0 | 1000 | 0 | 0
| iv. | 10" x 4" | Nos. | Rate only |  | 3800 | 0 | 1000 | 0 | 0
| v. | 24" x 6" | Nos. | Rate only | 2 | 4300 | 8600 | 1000 | 2000 | 10600
| vi. | 38" x 26" | Nos. | Rate only |  | 35000 | 0 | 1000 | 0 | 0
11 |  | Supply & installation of Volume Control Damper in 16 SWG G.I sheet metal with gas kits, nut bolts, complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | [6 empty] | 0
| 11.1 | 6" x 4" | Nos. | 10 | 12 | 4000 | 48000 | 1000 | 12000 | 60000 | Steel Craft / Engatech | 6 Weeks
| 11.2 | 6" x 6" | Nos. | 3 | 3 | 4000 | 12000 | 1000 | 3000 | 15000
| 11.3 | 8" x 4" | Nos. | Rate only | 2 | 4000 | 8000 | 1000 | 2000
| 11.4 | 8" x 6" | Nos. | Rate only | 2 | 4500 | 9000 | 1000 | 2000
| 11.5 | 10" x 4" | Nos. | Rate only | 2 | 4500 | 9000 | 1000 | 2000
12 |  | Supply & installation of rubberfoam acoustical duct sound liner adhesive with1/2" thick in supply air duct complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Sqft | 120 | 120 | 500 | 60000 | 100 | 12000 | 72000 | AEROFOAM | 3 Weeks
13 |  | Stencilling & Identification work on supports, hangers, platform of condensing units etc complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Lot | 1 | 1 | 90000 | 90000 | 10000 | 10000 | 100000
14 |  | Testing, balancing and commissioning of air side of the system (from independent agency) complete in all respects including air measurement & balancing, temp, pressure & electrical data of related equipment etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job. | 1 | 1 | 0 | 0 | 100000 | 100000 | 100000
15 |  | Making of Shop drawings on Auto CAD (latest version) with section details, equipment foundation details etc, As Built drawings Auto CAD (latest version), Documentation Technical / Operational Manual & LOG Book for each equipment etc, complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job. | 1 | 1 | 100000 | 100000 | 10000 | 10000 | 110000
|  | Total Cost of Works with I.Tax Rs. |  |  |  |  | 3098280 |  | 700050 | 3167830
Note:
1) | Electric power wiring / supply to be provided at outdoor, indoor units & other ACMV equipment with isolation box by client / electrical contractor.
2) | The refrigerant pipes sized + quantity provided for reference only. The contractor / supplier shall calculate the refrigerant pipes, sized & length as per the drawing provided and shall submitted refrigerant piping layout to consultant for approval.
3) | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
4) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
5) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## FSS
Bill of Quantities
Fire Suppression Services
EY Islamabad (10th. Floor)
S.No. |  | Description | Unit | BOQ QTY | VERIFIED QTY | Material |  | Labour |  | Total | BRAND | LEAD TIMES | REMARKS
[6 empty] | Rate | Amount | Rate | Amount | Amount Rs.
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression system including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1 |  | MS Sch-40 seamless pipes including all specials fittings UL listed FM approved, threaded, welded joints, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, supports and hangers, sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects. Note: > Existing piping to be re-used by Contractor shall first be approved by Project Manager/Consultant as per approved drawing. > Following quantities are for reference of procuring & installation of new fire piping, wherever required.
| i. | Dia 1" (Threaded fitting) | Rft. | 120 | 120 | 850 | 102000 | 250 | 30000 | 132000 | PROTECK | 4 Weeks
| ii. | Dia 1-1/4" (Threaded fitting) | Rft. | 20 | 20 | 1200 | 24000 | 275 | 5500 | 29500
| iii. | Dia 1-1/2" (Threaded fitting) | Rft. | 15 | 15 | 1450 | 21750 | 300 | 4500 | 26250
| iv. | Dia 2" (Threaded fitting) | Rft. | 10 | 10 | 1880 | 18800 | 350 | 3500 | 22300
| v. | Dia 2-1/2" (Welded joints fitting) | Rft. | 10 | 10 | 2860 | 28600 | 400 | 4000 | 32600
2 |  | Sprinkler Heads | [6 empty] | 0
| i. | Sprinkler Upright type quick response (Existing as per site handover) | Nos. | 15 | 15 | Existing | Existing | 1000 | 15000 |  | Shield | 8 Weeks
| ii. | Sprinkler Concealed Pendent type with cover plate, Quick Response K = 5.6 (Opening Temperature 57ºc) | Nos. | 60 | 60 | 8600 | 516000 | 1000 | 60000 | 576000
| iii. | SS Flexible connector for sprinklers 3 feet length. | Nos. | 60 | 60 | 10800 | 648000 | 750 | 45000 | 693000 | LIFFCO | 8 Weeks
3 |  | Fire extinguishers with fixing accessories. |  |  |  |  | 0 |  | 0
| i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 2 | 2 | 28000 | 56000 | 1000 | 2000 | 58000 | NAFFCO | 12 Weeks
| ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 2 | 2 | 17000 | 34000 | 1000 | 2000 | 36000
| iii. | Type Class K FX-5 (6 Litre Wet chemical fire extinguisher). | Nos. | 2 | 2 | 52000 | 104000 | 1000 | 2000 | 106000
| iv. | Automatic fire extinguisher (10 Kg. Dry Chemical Powder) | Nos. | 1 | 1 | 26000 | 26000 | 2000 | 2000 | 28000
4 |  | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1 | 1 | 110000 | 110000 | 15000 | 15000 | 125000 | Fisher | 2 Weeks
5 |  | Making of As-Built & Shop Drawings on AutoCAD 2018 or latest version with sectional details complete in all respects as per instructions of consultant. | Job. | 1 | 1 | 10000 | 10000 | 10000 | 10000 | 20000
6 |  | Painting, identification and tagging to the installations and equipments. | Job. | 1 | 1 | 25000 | 25000 | 45000 | 45000 | 70000 | Berger | 2 Weeks
7 |  | Flushing of entire fire pipe work according to (NFPA-13). | Job. | 1 | 1 | 15000 | 15000 | 40000 | 40000 | 55000
8 |  | Testing, and commissioning of entire fire fighting installation as per Consultant's approval. | Job. | 1 | 1 | 0 | 0 | 100000 | 100000 | 100000
9 |  | NOVEC-1230 SYSYEM |  |  |  |  | 0 |  | 0
9.1 |  | CLEAN AGENT (FK-5-1-12 Stored In Cylinder - Ul Listed / Fm Approved) |  |  |  |  | 0 |  | 0
|  | Supply of clean agent in engineered cylinders of FSS with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant. |  |  |  |  | 0 |  | 0
| iii. | Clean Agent (FK-5-1-12, Fluoroketone) (14 Kg.) | Lot. | 1 | 1 | 1800000 | 1800000 | 25000 | 25000 | 1825000 | FIREX | 16 to 18 Weeks
| iv. | Engineered cylinder with head valve, top plug adapter, siphon tube, pressure gauge, brackets and all other items, complete in all respect. | Lot. | 1 | 1 |  | 0 | 15000 | 15000 | 15000 | FIREX | 16 to 18 Weeks
9.2 |  | Supply of MS Sch-40 seamless pipes including all specials M.I & D.I threaded & welded joint fittings UL listed FM approved, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, lindapter supports hangers and sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant. |  |  |  |  | 0 |  | 0
| i. | Dia. 20 mm (3/4") (Threaded fitting) | Rft. | 20 | 20 | 1200 | 24000 | 300 | 6000 | 30000 | PROTECK | 2 Weeks
9.3 |  | SPRINKLER HEADS |  |  |  |  | 0 |  | 0
|  | Supply of nozzles with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant. |  |  |  |  | 0 |  | 0
|  | Brass Discharge Nozzle - 360 Degrees discharge pattern. |  |  |  |  | 0 |  | 0
| i. | Dia. 20 mm (3/4") | Nos. | 1 | 1 |  | 0 | 1000 | 1000 | 1000 | ZETA | 12 to 14 Weeks
9.4 |  | INPUT & OUTPUT DEVICES |  |  |  |  | 0 |  | 0
|  | Supply of input and output devices for the clean agent suppression system with wiring, controls & fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant |  |  |  |  | 0 |  | 0
| i. | Entinguishing Control Panel for the clean agent fire suppression system | Nos. | 1 | 1 |  | 0 | 10000 | 10000 | 10000 | ZETA | 12 to 14 Weeks
| ii. | Manual Abort / Emergency Cut Off Switch | Nos. | 2 | 2 |  | 0 | 1000 | 2000 | 2000 | ZETA | 12 to 14 Weeks
| iii. | Manual Release Switch - Single Action | Nos. | 2 | 2 |  | 0 | 1000 | 2000 | 2000 | ZETA | 12 to 14 Weeks
| iv. | Horn / Strobe | Nos. | 1 | 1 |  | 0 | 2000 | 2000 | 2000 | ZETA | 12 to 14 Weeks
| v. | Alarm Bell | Nos. | 1 | 1 |  | 0 | 2000 | 2000 | 2000 | ZETA | 12 to 14 Weeks
9.5 |  | ACTUATION DEVICES |  |  |  |  | 0 |  | 0
|  | Supply of actuation devices with fixing accessories, complete in all respects ready to operate as per drawings, specification, instruction of consultant. |  |  |  |  | 0 |  | 0
| i. | Solenoid Actuator for the specified cylinder size | Nos. | 1 | 1 |  | 0 | 5000 | 5000 | 5000 | ZETA | 12 to 14 Weeks
| ii. | Manual Control Head for manual actuation of cylinder with safety pull pin | Nos. | 1 | 1 |  | 0 | 5000 | 5000 | 5000 | ZETA | 12 to 14 Weeks
| iii. | Pressure Switch to indicated system discharge with an external manual reset button | Nos. | 1 | 1 |  | 0 | 5000 | 5000 | 5000 | ZETA | 12 to 14 Weeks
| iv. | Low Pressure Switch to monitor the pressure within the cylinder | Nos. | 1 | 1 |  | 0 | 5000 | 5000 | 5000 | ZETA | 12 to 14 Weeks
9.6 |  | WIRING |  |  |  |  | 0 |  | 0
| i. | Supply of wiring of 2C, 1.5 Sq.mm fire resistant shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia MS conduit from fire alarm control panel to all sensors & devices including all installation accessories complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Job. | 1 | 1 | 35000 | 35000 | 10000 | 10000 | 45000 | Pioneer / Pakistan | 2 Weeks
|  | Total Cost of Works with Income Tax Rs. |  |  |  |  | 3598150 |  | 480500 | 4063650
Note:
> | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## PLUMBING
Bill of Quantities
Plumbing & Sanitary Services
EY Islamabad (10th Floor)
S.No. |  | Description | Unit | BOQ QTY | VERIFIED QTY | Material |  | Labour |  | Total | BRAND | LEAD TIME | REMARKS
[6 empty] | Rate | Amount | Rate | Amount | Amount Rs.
SECTION - 01, PLUMBING FIXTURES
Supply and Installation of plumbing fixtures & faucets complete in all respects including all accessories, support, hangers, etc. ready to use as per specifications, drawings and instructions of Consultant.
1.1 |  | Wash basin (WB) including bottle trap, waste, stop cocks, etc.
| i. | Type - WB (Without Pedestal) | Nos. | Rate only |  | 42000 | 0 | 5000 | 0 | 0 | PORTA | 6 weeks
| ii. | Type - WB (Vanity) | Nos. | Rate only |  | 29000 | 0 | 5000 | 0 | 0
1.2 |  | Wash basin hot and cold water mixer, etc. |  |  |  |  | 0 |  | 0
| i. | Type - WB | Nos. | Rate only |  | 40500 | 0 | 2000 | 0 | 0
| ii. | Type - WB (for Vanity) | Nos. | Rate only |  | 40500 | 0 | 2000 | 0 | 0
1.3 |  | S.S Grease Trap 7.5 Kg inlet/outlet connections 2" dia complete in all respects. | Nos. | 2 | 2 | 215000 | 430000 | 5000 | 10000 | 440000 | Alpine | 8 weeks
1.4 |  | Bib cock brass body for Ablution. (Long Neck) |  |  |  |  | 0 |  | 0 |  | ZILVER | 6 weeks
| i. | AB | Nos. | Rate only |  | 15000 | 0 | 2000 | 0
1.5 |  | Toilet accessories complete set. |  |  |  |  | 0 |  | 0
| i. | Soap Dispenser | Nos. | 4 |  | 10500 | 0 | 1000 | 0 | 0 | ZILVER | 6 weeks
| ii. | Towel Rail | Nos. | Rate only |  | 8450 | 0 | 1000 | 0 |  | ZILVER | 6 weeks
| iii. | Automatic Hand Dryer | Nos. | 4 |  | 27500 | 0 | 3000 | 0 | 0 | SIEMENS | 6 weeks
| iv. | Kitchen Sink with Mixer | Nos. | 2 |  | 72000 | 0 | 7000 | 0 | 0 |  | 6 weeks
| v. | Toilet Roll Holder | Nos. | 6 |  | 6000 | 0 | 1000 | 0 | 0 | ZILVER | 6 weeks
| vi. | Tissue Paper Dispenser | Nos. | 4 |  | 18850 | 0 | 1000 | 0 | 0 | ZILVER | 6 weeks
|  | Sub Total Rs. |  |  |  |  | 0 |  | 0
|  | SECTION-02 WATER SUPPLY SYSTEM |  |  |  |  | 0 |  | 0
|  | Supply, installation, testing and commissioning of complete pipe work for cold and hot water system including all accessories required to complete systems ready to operate as per specification, drawings & instruction of Consultant. |  |  |  |  | 0 |  | 0
2.1 |  | Polypropylene Random PP-R pipes PN 20 and fittings with fusion jointing along with all types of unions, tees, bends, sockets, clamps, hangers, supports, sleeves, masking plates, chiseling, making holes making good, excavation, bedding backfilling as required complete in all respect. |  |  |  |  | 0 |  | 0
| i. | Dia. OD 25 mm | Rft. | Rate only |  | 600 | 0 | 150 | 0 | 0 | RAK THERM | 4 Weeks
2.2 |  | Same as item # 2.1 but for hot water supply with Polypropylene Random PP-R (PN -25) with Aluminium foil. |  |  |  |  | 0 |  | 0
| i. | Dia OD 25 mm | Rft. | Rate only |  | 990 | 0 | 150 | 0 | 0 | RAK THERM | 4 Weeks
| ii. | Dia. OD 32 mm | Rft. | Rate only |  | 1450 | 0 | 200 | 0 | 0
2.3 |  | Open cell rubber foam insulation 3/8" thick & pvc tape wrapping for hot water pipes. |  |  |  |  | 0 |  | 0
| i. | Dia OD 25 mm | Rft. | Rate only |  | 250 | 0 | 60 | 0 | 0 | Aeroflex | 2 Weeks
| ii. | Dia. OD 32 mm | Rft. | Rate only |  | 300 | 0 | 60 | 0 | 0
2.4 |  | Brass body gate valves / ball valves with unions. |  |  |  |  | 0 |  | 0
| i. | Size 1" | Nos. | Rate only |  | 12500 | 0 | 2000 | 0 | 0 | GALA | 4 Weeks
2.5 |  | Brass body check valve. |  |  |  |  | 0 |  | 0
| i. | Size 1" | Nos. | Rate only |  | 11800 | 0 | 2000 | 0 | 0
2.6 |  | 3 way Thermostatic mixing valve complete in all respects. |  |  |  |  | 0 |  | 0
| i. | Size 1" | Nos. | Rate only |  | 85000 | 0 | 2000 | 0 | 0
|  | Sub Total Rs. |  |  |  |  | 0 |  | 0
|  | SECTION-03 SOIL, WASTE VENT AND RAIN WATER DRAINAGE SYSTEM |  |  |  |  | 0 |  | 0
|  | Supply, fixing, testing and commissioning of equipment, pipe work required to complete the soil, waste, vent and rain water systems in all respects with accessories ready to operate as per specifications, drawings and instructions of Consultant. |  |  |  |  | 0 |  | 0
3.1 |  | uPVC pipes of approved make along with specials, fittings, bends, wye, tees, sockets, flexible connectors, sleeves, masking plates, chiseling, making hole, excavation, backfilling making good where as required jointing with rubber ring seal. |  |  |  |  | 0 |  | 0
| i. | Dia. 1-1/2" | Rft. | Rate only |  | 600 | 0 | 150 | 0 | 0 | DADEX | 2 Weeks
| ii. | Dia. 2" | Rft. | 15 |  | 880 | 0 | 200 | 0 | 0
| iii. | Dia. 4" | Rft. | Rate only |  | 2350 | 0 | 300 | 0 | 0
3.2 |  | Floor trap including S.S grating floor trap, inlet outlet connection complete in all respects. |  |  |  |  | 0 |  | 0
| i. | FT- with 4" P - trap | Nos. | Rate only |  | 9800 | 0 | 1000 | 0 | 0 | DADEX | 2 Weeks
|  | Sub Total Rs. |  |  |  |  | 0 |  | 0
|  | SECTION-04 SUNDRIES |  |  |  |  | 0 |  | 0
|  | Contractor will priced the sundries items for all Plumbing & Sanitary (P&S) services as per specifications, drawings and instruction of consultant. |  |  |  |  | 0 |  | 0
4.1 |  | Submittals, samples, shop drawings, inspections, As-Built drawings, operation and maintenance manuals and the like as required by specification. | Job. | 1 |  | 25000 | 0 | 10000 | 0 | 0
4.2 |  | Testing, and commissioning entire P&S installation as per Engineer's approval. | Job. | 1 |  | 0 | 0 | 45000 | 0 | 0
Sub Total Rs.
|  | TOTAL OF ALL SECTIONS RS. |  |  |  |  | 430000 |  | 10000 | 440000
Note:
> | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).