## Summary
S.# | DESCRIPTION | SUPPLY | INSTALLATION | TOTAL (Rs.)
1 | SECTION - A WIRING & WIRING ACCESSORIES
2 | SECTION - B CABLE CONTAINMENT
3 | SECTION - C SWITCHES & SOCKETS
4 | SECTION - D LIGHTING FIXTURES
5 | SECTION - E MAIN / SUB-MAIN CABLES
6 | SECTION - F DISTRIBUTION BOARDS
7 | SECTION - G VOICE & DATA COMMUNICATION SYSTEM
8 | SECTION - H ADDRESSABLE FIRE ALARM SYSTEM (WIRING ONLY)
9 | SECTION - I CCTV SYSTEM
10 | SECTION - J PUBLIC ADDRESS SYSTEM
11 | SECTION - K UNINTERRUPTIBLE POWER SUPPLY
12 | SECTION - L LIGHTING CONTROL SYSTEM
14 | SECTION - M AS-BUILT DRAWINGS
| Sub-Total (Rs.) |  |  |  | 0
Note: ● Owner can supply any material of Contractor scope at any stage and its cost will be completely deleted from Contractor scope without any kind of adjustment. ● Contracotor should mark the selected brands and vendors in approved manufacturer list with submission of Tender Documents. ● Owner / Consultant have all the rights to select any brand / vendor from provided approved manufacturer list, Contractor shall not finalize any brand / vendor without written approval from consultant / owner. ● Installation of generator along with generator pad, its testing and commisioning to be done by others. ● The quantities may vary ± 15%.

## BOQ
S.# | DESCRIPTION | QTY | UNIT | SUPPLY |  | INSTALLATION |  | TOTAL (Rs.)
|  |  |  | RATE (Rs.) | AMOUNT (Rs.) | RATE (Rs.) | AMOUNT (Rs.)
SECTION - A WIRING & WIRING ACCESSORIES
Supply, Installation, Testing & Commissioning of the following items including all material, labour & tools required for completion of work as per item description, specifications & drawings including cutting, chiseling, making good and all necessary accessories such as bends, junction boxes, conduit sockets, earth connecting point connectors, etc. as shown on drawings, specifications and approval by the Engineer. Complete in all respects. Note: - The cost of wiring items shall include Imported WAGO made tool less Connectors and 25mm dia Fire Retardant Spiral Polyamide Flexible Conduit along with Gland on each light point. - The circuit wire drop shall be sufficient as per ceiling levels. - The wiring shall be done with LSZH Wires / Cables. - Megger Test of each circuit is to be done by the Contractor. - All General Wiring grade should be 450/750 copper with green/yellow Color.
- Surface conduiting wherever required shall be done in aesthetic manner as per the consent of Architect/Consultant/Client. - Wherever the circuits are running in cable tray, it will enter / leave tray using proper glands / Junction boxes (IP44). The cost of all such accessories to be included in wiring cost. - All electrical circuits and power outlets shall be numbered (i.e. circuit number and distribution board number) and the circuit schedule of the distribution board must accurately reflect the installation. The load across all phases must be balanced. - The ECC to be run with each circuit shall be loop-in and loop-out type, joints are not allowed. It will be green in color (Refer detail BoQ & drawings) - All the cables shall be colour coded according to phases / types of services. - 18-SWG, 25mm dia Aluminum EMT Conduit with anodizing on both Internal & External Sides (Internal Diameter must be 25mm)
1 | Circuit wiring from DB to Switchboard including any wiring from switchboard to switchboard with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core LSZH wires in 25mm dia Anodized Aluminum EMT Conduit as shown in drawings. | 1 | No
2 | Wiring for light point from Switchboard to first light point with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core LSZH wires, in 25mm dia Anodized Aluminum EMT Conduit as shown in drawings. | 2 | No
a | Point to Point wiring using the same wires and conduit size as mentioned in the above item. | 19 | No
3 | Emergency Circuit wiring from DB to Switchboard including any wiring from switchboard to switchboard with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core LSZH wires in 25mm dia Anodized Aluminum EMT Conduit as shown in drawings. | 1 | No
4 | Emergency Wiring for light point from Switchboard to first light point with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core LSZH wires, in 25mm dia Anodized Aluminum EMT Conduit as shown in drawings. | 2 | No
a | Point to Point wiring using the same wires and conduit size as mentioned in the above item. | 5 | No
5 | Circuit Wiring for Group Control light fixtures from DB to First Light Point with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core LSZH wires in 25mm dia Anodized Aluminum EMT Conduit as shown in drawings. | 20 | No
a | Point to Point wiring using the same wires and conduit size as mentioned in the above item. | 55 | No
6 | Emergency Circuit Wiring for Group Control light fixtures from DB to First Light Point with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core LSZH wires in 25mm dia Anodized Aluminum EMT Conduit as shown in drawings. | 1 | No
a | Point to Point wiring using the same wires and conduit size as mentioned in the above item. | 7 | No
7 | Circuit Wiring for Signage from DB to First Light Point with 2x2.5 Sq.mm + ECC 1x2.5 Sqmm, 1-core LSZH wires in 25mm dia Anodized Aluminum EMT Conduit as shown in drawings. | 1 | No
8 | Circuit Wiring of 13A/15A Switch Socket units (RAW Power) from DB to first outlet including wiring within the same technology box / adjacent power outlets in separate back boxes with following size of LSZH wires in 25mm dia PVC conduit under-floor/wall as shown in the drawings.
a | 2 x 4 Sq.mm Cu/LSZH + ECC 1 x 4 Sq.mm Cu/LSZH | 8 | No
b | Outlet to Outlet wiring in 25mm dia PVC Conduit with 3 x 1C-2.5 Sqmm Cu/LSZH | 16 | No
9 | Circuit Wiring of 13A/15A Switch Socket units (UPS Power) from DB to first outlet including wiring within the same technology box / adjacent power outlets in separate back boxes in 25mm dia PVC conduit under-floor/wall as shown in the drawings.
a | 2 x 4 Sq.mm Cu/LSZH + ECC 1 x 4 Sq.mm Cu/LSZH | 2 | No
b | Outlet to Outlet wiring in 25mm dia PVC Conduit with 3 x 1C-2.5 Sqmm Cu/LSZH | 4 | No
10 | Wiring of 20A DP Isolator for AC Equipment from DB to Isolator outlet with 2 x 4 Sq.mm Cu/LSZH + ECC 1 x 4 Sq.mm Cu/LSZH in 25mm dia Anodized Aluminum EMT Conduit as shown in drawings. | 2 | No
11 | Circuit Wiring of 16A 3-Pin Industrial Socket for Communication Rack (For IT Rack) with 3C-4 Sqmm Cu/LSZH wires in 25mm dia PVC Conduit in wall as shown in the drawings. | 2 | No
Note: 1) Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. 2) The ECC to be run with each circuit shall be loop-in and loop-out type, joints are not allowed. It will be green in color (Refer detail drawings) 3) All the cables shall be colour coded according to phases / types of services. 4) Wires color of UPS circuits should be different from RAW Power.
Total Amount (Rs.) Sec - A (CARRIED FORWARD TO SUMMARY)
SECTION - B CABLE CONTAINMENT
1 | Supply & Laying of the following sizes of PVC/UPVC/EMT Conduits including all accessories such as bends, sockets, j-boxes, flexible conduits, metal saddles e.t.c as per design drawings, complete in all respect. - Provide Pull boxes where ever required.
a | 18-SWG, 25mm dia Aluminum EMT Conduit with anodizing on both Internal & External Sides (Internal Diameter must be 25mm) (For Fire Alarm devices) | 30 | Rm
b | 25mm dia Fire Retardant Spiral Polyamide Flexible Conduit along with Gland | 50 | Rm
c | 25mm dia PVC Conduit | 50 | Rm
2 | Supply & Installation of the following sizes of GI Powder Coated 16 SWG Ceiling / Floor / Wall BackBox Pull Boxes, with cover recessed on wall or column as per design drawings. Complete in all respect.
a | 150mm x 150mm x 25mm | 4 | No.
3 | Supply & installation of Imported Floor Boxes without face plates made of 16 SWG G.I Sheet, recessed in ground as per design drawings. | 2 | No.
4 | Supply and Installation of the following sizes of 16 SWG GI Powder Coated Perforated Cable Tray with 18 SWG 4 feet Cover (Z140) & upto 100micron powder coating having duly Painted after degreesing, derusting, phosphating and antirust primer, along with supporting hangers, brackets, elbows, tee & mounting accessories etc. complete in all respect. Note: - Color Printed Tags to be provided at every 3 Meter Length. - Threaded Rods & C-Channel base is required for hanging from Ceiling. - All the accessories such as thread M12 rods shall be cadmium plated/stainless steel made such as nuts, screws, bolts, wire etc - Wall Hanger Supports to be provided wherever required. - U-shaped fischer plates to be used for joints. - 6 Sqmm braided copper terminals with lugs for bonding to be done with every joint
a | 150mm x 100mm Horizontal (FOR POWER CABLE) With Ceiling Mounted Hanging Accessories & Loop Hangers | 15 | Rm.
b | 150mm x 100mm Horizontal (FOR COMMUNICATION CABLE) With Ceiling Mounted Hanging Accessories & Loop Hangers | 15 | Rm.
5 | Supply & Installation of the following sizes of Linear Outlet Boxes without face plates made of Aluminum, mounted on wall or punched in furniture as per design drawings. The linear outlet boxes are to be provided with appropriate sizes of knockouts.
a | 450mm x 100mm (5 No. Face Plates) | 3 | No.
6 | Supply & Installation of 16 SWG MS Sheet Steel Back Boxes for installation of Switches, Sockets, Voice & Data Outlets, Isolators as per drawings and details including all accessories. | 25 | No.
Note: Contractor is advised to confirm the sizes, running lengths and termination as per site conditions before commencement of work. All the conduits / cable tray crossings through partition walls shall be properly sealed by fire retardant material after installation.
Total Amount (Rs.) Sec - B (CARRIED FORWARD TO SUMMARY)
SECTION - C SWITCHES & SOCKETS
Supply, Installation, Testing & Commissioning of the following ratings of Light Switches, Power Outlets, DP Switches, Isolators, Industrial Sockets in already installed 16 SWG sheet steel back boxes to be recessed in wall / installed on surface, as shown in drawings, complete in all respect. (Clipsal Vivace for Light Switches & Power Sockets or equivalent) (Clipsal Kavacha Series for Isolators or equivalent) (Clipsal PCE Series for Industrial Sockets or equivalent)
1 | Two Gang Light Switch | 2 | No
2 | Three Gang Light Switch | 3 | No
2 | 13A Flat Pin Simplex Socket Unit (For UPS Power) | 22 | No
3 | 13A International Switch Socket Unit (For RAW Power) | 6 | No
4 | 20A DP Isolator | 2 | No
5 | 16A 3-Pin (Single Phase) Industrial Socket with Plug, in IP-Rated Enclosure (For Communication Rack) | 2 | No
6 | 32A 3-Pin (Single Phase) Industrial Socket with Plug, in IP-Rated Enclosure (For 2kVA UPS) | 2 | No
Total Amount (Rs.) Sec - C (CARRIED FORWARD TO SUMMARY)
SECTION - D LIGHTING FIXTURES
Supply, Installation, Testing & Commissioning of the following Light fixtures, complete with ballast, starter p.f.i capacitor and specified lamps and Installation Accessories. Note: - Color temperature will be as per Architect's requirement. - Efficacy of light fixtures shall be equal to or more than 105 Lumens / Watt. - 3 Year Replacement Warranty is required both for fixture and driver. - Power Factory shall not be less than 0.9 & CRI>85. - Minimum Operational life should be more than 25,000 Hours.
1 | Track Mounted Adjustable Light Fixture with 35W LED, Color 4000K, or as appproved by the Architect. | 115 | No.
2 | 1 meter track for LED track lights with all connectors, & jointing strips | 39 | No.
3 | LED Rope Light15W/M Color 4000K, with Driver | 60 | Rm.
4 | LED Rope Light with Infused Glass cover in Bendable Aluminum Profile 15W/M Color 4000K, with Driver & Mounting Accessories | 105 | Rm.
5 | Surface Mounted 12W LED Down Light Color 4000K, or as appproved by the Architecht. | 15 | No.
6 | Recessed Mounted 12W LED Down Light Color 4000K, or as appproved by the Architecht. | 9 | No.
7 | Recessed Mounted 10W LED Down Light Color 4000K, or as appproved by the Architecht. | 10 | No.
8 | Pendant Type 15W LED Down Light Color 4000K, or as appproved by the Architecht. | 8 | No.
9 | Recessed Mounted 20W Double Head LED Down Light Color 4000K, or as appproved by the Architecht. | 54 | No.
10 | Planter LED Lights 7W Light Color 4000K, or as appproved by the Architecht. | 5 | No.
11 | Recessed Mounted Exit Light Fixture with 4W LED, IP-44, Single Sided Directional Arrow, Maintained Type with Battery Backup | 1 | No.
Total Amount (Rs.) Sec - D (CARRIED FORWARD TO SUMMARY)
SECTION - E MAIN / SUB-MAIN CABLES
Supply, Laying, Termination, Testing & Commissioning of the following ratings of LSZH, 120 minutes Fire Resistant LV Cables along with complete installation and termination accessories to be laid in already installed Cable trench / Cable ladder / Cable tray / Duct Bank including all accessories. Complete in all respects. -Imported Lugs and Connectors shall be used. -Appropriate Size of Glands and Lugs to be used for termination. -Manual crimping of lugs is not allowed. Proper lug presser for smaller lugs and hydraulic lug presser for large size lugs should be used. -Megger Test of all LV Cables to be done by contractor. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
1 | From 80A TP BOX to LPDB-OUTLET 4C-16 Sqmm Cu/LSZH/SWA/PVC + ECC 1C-16 Sqmm Cu/LSZH/SWA/PVC | 15 | Rm.
2 | From LPDB-OUTLET to UPS 3C-6 Sqmm Cu/LSZH/LSZH | 6 | Rm.
3 | From UPS to LPDB-OUTLET 3C-6 Sqmm Cu/LSZH/LSZH | 6 | Rm.
Note: - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. - Rain water drip protection is required for laying of cables from building service shaft to respective distribution boards. - All the cable crossings through shaft shall be properly sealed by fire retardant material after installation.
Total Amount (Rs.) Sec - E (CARRIED FORWARD TO SUMMARY)
SECTION - F DISTRIBUTION BOARDS
Supply, Installation, Testing & Commissioning of the following Distribution Boards made with 16/14 SWG Sheet Steel Enclosure including all installation accessories such as Rawal bolt etc. Complete in all respects. Note: - All the DBs should be front accessible and maintainable. - Cost of Lighting Control Relays & Power Supplies should be Included. - The transportation and placement of DBs upto dedicated location is included, complete in all respects including levelling, grouting etc. - Laser engraved tags required as mention in SLDs - Space for circuit tagging required with permanent installation on protective sheet via rivets - 20% space required in DB for future provision - Tin platted Imported Cu bus bar with heat shrink color coded sleeves to be used. - Hindged protective metallic door is required with knob/handle. - Braided Door earth required. - Lockable handle required for main door. - As-built drawing pocket. - Cable hanging arrangement. Minimum One Year Warranty Required from date of successful comissioning on site.
1 | MS Powder Coated TP Box with 35A TP MCCB Breaker 25kA | 1 | No.
2 | LPDB-OUTLET | 1 | No.
Total Amount (Rs.) Sec - F (CARRIED FORWARD TO SUMMARY)
SECTION - G VOICE & DATA COMMUNICATION SYSTEM
Supply, Laying, Installation, Termination, Testing & Commissioning of following items for voice and data communication system including all material, labor, tools, accessories etc. Complete in all respects. Note: - Different colors of voice and data cables shall be used. - Cable lengths will be verified by Fluke Test and exact length shall reflect the Measurement Sheet/ Bill issued by the contractor. - Cables left for terminating with Patch Panels shall not exceed the required length. Leaving of Unnecessary Excessive lengths shall be avoided. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work. -Price of Installation Accessories to be included in Price of Installation Works.
1 | Simplex Face plate with 1 No. CAT-6 RJ-45 I/O for Data Communication in white / off white finish, complete with, shuttered click-ins, labels and all accessories. Complete in all respects. | 1 | No
2 | Duplex Face plate with 2 No. CAT-6 RJ-45 I/O for Data Communication in white / off white finish, complete with, shuttered click-ins, labels and all accessories. Complete in all respects. | 6 | No
3 | Simplex Face plate with 2 No. CAT-6 RJ-45 I/O for WIFI Communication in white / off white finish, complete with, shuttered click-ins, labels and all accessories. Complete in all respects. | 2 | No
4 | Simplex Face plate with 1 No. CAT-6 RJ-45 I/O for CCTV Communication in white / off white finish, complete with, shuttered click-ins, labels and all accessories. Complete in all respects. | 14 | No
5 | CAT-6 UTP Cables for Data Voice & WIFI Communication from Communication Rack to each outlet in 25mm dia PVC Conduit including termination and tagging at both ends. Complete in all respects. (Coil =305 Rm.) (Selected Cable Must be UL Listed CM-P of LSZH) | 1 | Coil
6 | Imported 19U Communication Rack (Wall Mounted) suitable for installation of standard patch panels etc. Complete with floor base, vertical cable managers. Rack shall be equipped with 2 No. power distribution units (PDUs) with at least 8 imported power sockets & proper ventilation system including fan etc. Complete in all respects. | 1 | No.
7 | Following Patch Panels equipped with RJ-45 I/Os including all labeling and all mounting accessories. Complete in all respects.
a | 24-Port CAT-6 Patch Panel | 1 | No
8 | Front Cable Organizer for patch panels / wiring blocks with complete labeling and dressing for incoming cable management. | 1 | No
9 | Following factory certified Patch Cords of specified color having RJ-45 connectors at both ends.
a | 1 meter long CAT-6 Patch Cord | 24 | No
b | 3 meter long CAT-6 Patch Cord | 9 | No
10 | 4 Core, 9/125um Single Mode OS2 Fiber Optic Cable as per standard specifications with all termination accessories including termination and tagging at both ends, up to entire satisfaction of IT Engineer, to be laid in already installed cable tray / ladder. Complete in all respects. | 30 | Rm.
11 | Single Mode 8 port ODF (with utilization of 8 Ports) 8 port SM ODF complete with all accessories with pigtails, LC / SC connectors, splicing etc complete in all respect | 1 | No.
12 | Testing and Commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
13 | Fluke Testing of all CAT-6 cables with calibrated fluke tester | 1 | Job
14 | Power Meter and Light Source Testing of all the laid fiber cables shall be included in the scope of works | 1 | Job
Note: Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - G (CARRIED FORWARD TO SUMMARY)
SECTION - H ADDRESSABLE FIRE ALARM SYSTEM (WIRING ONLY)
Supply, Installation, Testing & Commissioning of Addressable Fire Alarm System in compliance with comprising of following equipments including all accessories required for the completion of the system in all respects. Note: - Minimum 3 Years Warranty is required - Price of Installation Accessories to be included in Price of Installation Works.
1 | 2C, 1.5 Sq.mm Fire Resistant Shielded Cable (Fire rating for 2 hours at 950 C) in 25mm dia Anodized EMT Conduit from Mall including all installation accessories complete in all respect. (Prysmian FP-200 Gold or Equivalent) | 50 | Rm.
Note: - Contractor shall provide the complete Technical Literature for the offered system. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - H (CARRIED FORWARD TO SUMMARY)
SECTION - I CCTV SYSTEM
Supply, Installation, Testing, Commissioning of the following items for IP Based CCTV System including but not limited to the description given here under including all power and communication accessories, housings, mounting brackets, suspension rods etc. required for completion of the system. Note: - Minimum 3 Years Warranty is required - Price of Installation Accessories to be included in Price of Installation Works.
1 | Ceiling Mounted Fixed-Type PoE Powered HD Resolution I.P Dome Camera with day and night feature with 2-MP Resolution and with live view at 25fps and recording quality of minimum 15 fps, Varifocal Lens, WDR, face recognition till minimum 10metres, Tamper Detection, remote focus lens, motion detection activated recording, edge recording, H.265+ compression, audio recording feature, horizontal view mode along with all mounting accessories complete in all respects. | 12 | No.
2 | Wall Mounted Fixed-Type PoE Powered HD Resolution I.P Box Camera with day and night feature with 2-MP Resolution and with live view at 25fps and recording quality of minimum 15 fps, Varifocal Lens, WDR, face recognition till minimum 10metres, Tamper Detection, remote focus lens, motion detection activated recording, edge recording, H.265+ compression, audio recording feature, horizontal view mode along with all mounting accessories complete in all respects. | 2 | No.
3 | Network Video Recorder (NVR) with 16 channel Video input Analytics Features. The NVR shall be equipped with LAN / WAN facility. NVR should have minimum 15 days storage capacity on 25 frame per second with Surveillance Grade HDD to cater 100% cameras with Raid 6 storage mechanism, RW CD Drive. Complete with all connecting cords and accessories including SFP modules. | 1 | No.
4 | CAT-6 UTP Cables for CCTV System from POE Switch to each camera in 25mm dia Anodized Colored Aluminum EMT Conduit as per drawings including termination and tagging at both ends. Complete in all respects. (Coil=305 Rm.) (Selected Cable Must be UL Listed CM-P of LSZH) | 1 | Coils
5 | 32" LED Color Screen to be installed in control Room in racks with all connecting cords and mounting stands. | 1 | No.
5 | 16 Port POE Switch | 1 | No.
5 | Following CAT-6, Patch Panel equipped with RJ-45 I/Os for including all labeling and all mounting accessories. Complete in all respects.
a | 24-Port Data CAT-6 Patch Panels | 1 | No.
6 | Front Cable Organizer for patch panels / wiring blocks with complete labeling and dressing for incoming cable management. | 1 | No.
7 | Following factory certified Patch Cords of specified color having RJ-45 connectors at both ends.
a | 3 meter long CAT-6 factory certified patch cords (outlet to camera) | 14 | No.
b | 1 meter long CAT-6 factory certified patch cords (patch panel to switch) | 24 | No.
8 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
9 | Fluke Testing of all CAT-6 cables with calibrated fluke tester | 1 | Job
Note: - Contractor shall provide the complete Technical Literature for the offered system. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - I (CARRIED FORWARD TO SUMMARY)
SECTION - J PUBLIC ADDRESS SYSTEM
Supply, Installation, Testing & commissioning of the following items for Public Address & Voice Evacuation System as described below including all tools, accessories etc with mounting brackets/placement in IDF rack, wiring, adapters etc Complete in all respect. Note: - Minimum 3 Years Warranty is required - Price of Installation Accessories to be included in Price of Installation Works.
1 | 30W Power Amplifier operating at 220V, AC suitable for rack mounting incorporates two audio line level inputs: a Music input and a priority call input. A built-in relay switches the amplifier from the music input of priority call input (AT COUNTER). | 1 | No.
2 | 6W Recessed Ceiling Speakers with back boxes intended for high quality speech and music reproduction with sealed enclosure protective against moisture and dust. The speaker shall have output power adjustments for full, half and quarter power outputs, including back boxes if required. | 4 | No.
3 | Micro Phone Outlet including all accessories. | 1 | No.
4 | Volume Controller for 12W as per requirement. Complete in all respect. | 1 | No.
5 | Supply & Wiring for Public Address System using 2C-2.5 Sq.mm flexible Speaker Cable as perlayout shown in drawings in 25mm dia Anodized Colored Aluminum EMT Conduit conduit. Complete in all respects. | 65 | Rm.
6 | CAT-6 STP Cables for Microphone from Amplifier to Microphone Outlet to be laid in 25mm dia PVC Conduit in floor/wall as shown in drawings including termination and tagging at both ends, Complete in all respects. (Selected Cable Must be UL Listed CM-P of LSZH) | 15 | Rm.
7 | Programming, testing and commissioning of complete system including on site demonstration and training of client's representative upto the entire satisfaction of consultant/client | 1 | Job
Note: - Contractor shall provide the complete Technical Literature for the offered system. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - J (CARRIED FORWARD TO SUMMARY)
SECTION - K UNINTERRUPTIBLE POWER SUPPLY
Supply, Installation, Testing & Commissioning of following ratings of UPS as per following specifications, Complete in all respect.
1 | Rating : 2 kVA UPS True Online Double Conversion Pure sine wave Microcontroller based. Input voltage: 220V AC Input frequency: 50 Hz Output voltage: 220 Volts Single Phase IN & Single Phase Out Output p.f: 0.95 (Built in PFC) Effiiceincy: 92 to 96% Backup Time: 60 mins at 100% Load Batteries: Dry Sealed Maintenance Free (European) Provision for external battery bank Voltage Regulated: 5 years Overload: 110% for 10min Capacity: 125% for 1-min Operating Temp: 0 to 40 degC Mounting: Floor Mounted Warranty: 1 Years for UPS & Batteries User friendly LCD display for real time UPS status Cold start of load during power failure Transient/Surge Suppressor EMI/RFI Filter Built-in manual and static by-pass switch Remote & local emergency power off function RS-232 connectivity with power management software UPS & Advance Automatic Battery Management system for temperature compensated battery charging and battery testing on user defined time. Power Chute Network Shutdown. SNMP Management Card / Modbus Card | 1 | No
Note: - Contractor shall provide complete technical literature for the quoted equipment for approval of Consultant before procurement.
Total Amount (Rs.) Sec - K (CARRIED FORWARD TO SUMMARY)
SECTION - L LIGHTING CONTROL SYSTEM
Supply, Installation, Testing & Commissioning of following items for complete Lighting Control System (KNX Based) including all labour, tools etc. Complete in all respect as shown on drawing.
1 | 8 Scene Intelligent Input Units with bus coupler and remote controlled | 1 | No
1 | 12 Scene Intelligent Input Units with bus coupler and remote controlled | 1 | No
2 | KNX Control Cable for system wiring from Screen to Relay in Distribution Boards and other devices in 25mm dia Anodized Colored Aluminum EMT conduit as shown in the drawings. Complete in all respects. (KNX Approved Cable & Must be LSZH type) | 35 | Rm.
3 | Programming, testing and commissioning of complete system upto the entire satisfaction of client and consultant including following: - Intelligent Lighting Control System Schedule (Software + Manual) - Documentation - Web based featuring an extensive schedule Program - Manual Setting in DB with accessories and tagging | 1 | Job
Note: - Contractor shall provide complete technical literature for the quoted equipment for approval of Consultant before procurement. - Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
Total Amount (Rs.) Sec - L (CARRIED FORWARD TO SUMMARY)
SECTION - M AS-BUILT DRAWINGS
1 | VIDEO WALL Supply and Installation of Video wall of size 13' x 6'-7" & 3' x 6' with controller and other accessories. Complete in all respects. | 1 | Job
2 | VIDEO WALL Supply and Installation of Video wall of size 3' x 6' with controller and other accessories. Complete in all respects. | 1 | Job
3 | Preparation & Submission of As-Built drawings for all electrical and allied works after getting final approval from the Client/Consultant. Note: 3 sets of as-built drawings after work completion with a soft copy of complete electrical works after final commissioning of project to be submitted. Approval of bills are subject to the completion of as built drawings upto the entire satisfaction ot site engineer. | 1 | Job
Total Amount (Rs.) Sec - M (CARRIED FORWARD TO SUMMARY)