## Salvage - Title
STATE LIFE INSURANCE CORPORATION BUILDING No. 9
BOQ SALVAGEABLE MATERIAL

## Salvage BOQ
GENERAL - SALVAGABLE MATERIAL (TO BE CREDITED TO THE CLIENT)
S. No. | DESCRIPTION | QTY | UNIT | RATE (RS) | AMOUNT (RS)
A. | REMOVAL OF EXISTING COOLING TOWERS OF 150 TR. EACH FROM ROOF (S) ALONG WITH PIPE LINE NETWORK, PUMPS ETC AS PER SCHEDULE APPROVED BY CONSULTANT & STACKING THOSE ON DESIGNATED PLACE PRIOR TO REMOVAL FROM BUILDING. > 3 UNITS, 150 TR. EACH | 3 | No. |  | 0
B. | REMOVAL OF EXISTING AIR HANDLING UNITS (PACKAGE TYPE UNIT) FROM EACH FLOOR ALONG WITH CHILLED WATER LINES, POWER CABLES, DBS ETC. AS PER SCHEDULE APPROVED BY CONSULTANT AND STACKING THOSE ON DESIGNATED PLACE PRIOR TO REMOVAL FROM BUILDING. > 20 UNITS, 15 TR. EACH > 03 UNITS, 20 TR. EACH | 23 | No. |  | 0
C. | REMOVAL OF EXISTING AIR HANDLING UNITS (PACKAGE TYPE UNITS) FROM THE MEDICAL SECTION GROUND FLOOR, ALONG, POWER CABLES, DBS ETC. AS PER SCHEDULE APPROVED BY CONSULTANT AND STACKING THOSE ON DESIGNATED PLACE PRIOR TO REMOVAL FROM BUILDING. > 02 UNITS > 10 TR. EACH | 2 | No. |  | 0
D. | REMOVAL OF EXISTING AIR HANDLING UNITS (PACKAGE TYPE UNITS) FROM THE BANK SIDE GROUND FLOOR, FLOOR ALONG, POWER CABLES, DBS ETC. AS PER SCHEDULE APPROVED BY THE CONSULTANT AND STACKING THOSE ON DESIGNATED PLACE PRIOR TO REMOVAL FROM BUILDING. > 05 UNITS, 7 TR. EACH > 02 UNITS, 4 TR. EACH | 7 | No. |  | 0
| TOTAL AMOUNT TO BE CREDITED TO THE CLIENT |  |  |  | 0

## General Work - Title
STATE LIFE INSURANCE CORPORATION BUILDING No. 9
BOQ GENERAL WORK

## General Work - BOQ
The contractor is required to store the items temporarily in the storage space provided by the client (if required). Each lot of the salvaged material shall be documented before leaving the site, including acquiring the gate pass. All salvaged items shall be considered as the contractor's property after leaving the site.
GENERAL WORK (TO BE CREDITED TO THE CLIENT)
S. No. | DESCRIPTION | QTY | UNIT | RATE (RS) | AMOUNT (RS)
EMERGENCY STAIR CASE
1 | EMERGENCY MS STAIRCASE
| PROVIDING MAKING, AND FIXING THE M.S. STAIRS EMERGENCY STAIRS WITH 10 SWG CHECKERED PLATE FLOOR, T-SECTION FOR GIRDERS AND ANGLE OF 1.5" BY 2" ON THE INSIDE (1/4"Th) 2" by 3" ON THE PERIPHERY 3/8" TH. HAVING MS RAILING AT EVERY STEP CONNECTED TO THE PLATFORM HAVING 3 EQUIDISTANT SECTION MADE OF MS PIPE 1/2 " TH 10 SWG, HAVING BALUSTERS AT TOP; EPOXY PAINTED ON ALL SIDES WHICH CONNECT ALL FLOORS TO THE GROUND FLOOR. ALL MEMBERS SHOULD BE M.S. 16 SWG. INSTALLED WITH EMERGENCY LIGHTS AND REVOLVING EMERGENCY LIGHTS WITH PANIC BUTTON. COMPLETE IN ALL RESPECTS AS SPECIFIED BY ENGINEER. PROVIDING ALL MATERIALS, LABOUR, CONSTRUCTION EQUIPMENT, SUPERVISION, SCAFFOLDINGS, TOOLS & PLANTS, TRANSPORTATION & STORAGE, AND ALL INCIDENTAL ITEMS NOT SHOWN OR SPECIFIED BUT REASONABLY IMPLIED OR NECESSARY FOR COMPLETION OF THE JOB. NOTE: THE CONTRACTOR IS REQUIRED TO PREPARE AND SUBMIT SHOP DRAWINGS BEFORE EXECUTION OF WORKS. | 7500 | KG |  | 0
SOIL, WASTE VENT AND RAIN WATER DRAINAGE SYSTEM
SUPPLY, FIXING, TESTING AND COMMISSIONING OF EQUIPMENT, PIPE WORK REQUIRED TO COMPLETE THE SOIL, WASTE, VENT AND RAIN WATER SYSTEMS IN ALL RESPECTS WITH ACCESSORIES READY TO OPERATE AS PER SPECIFICATIONS, DRAWINGS AND INSTRUCTIONS OF CONSULTANT.
2 | RISER DRAIN FOR WASTE WATER
uPVC DADEX, AGM, STEELEX OR EQUIVALENT PIPES UPTO 6 BAR AND FITTINGS WITH FUSION JOINTING ALONG WITH ALL TYPES OF UNIONS, TEES, BENDS, SOCKETS, CLAMPS HANGERS, SUPPORTS, SLEEVES, MASKING PLATES, CHISELLING, MAKING HOLES MAKING GOOD, EXCAVATION, BEDDING BACKFILLING AS REQUIRED COMPLETE IN ALL RESPECT.
A. | DIA 4" (GREY WATER) (KITCHEN AND BATHS) | 150 | RFT |  | 0
B. | DIA 4" (GREY WATER) (HVAC) | 150 | RFT |  | 0
C. | DIA 8" (BLACK WATER) | 150 | RFT |  | 0
3 | uPVC COWL FOR VENT PIPE OF THE FOLLOWING DIA. INCLUDING ALL ACCESSORIES COMPLETE.
A. | DIA 4" (HVAC) | 4 | No. |  | 0
B. | DIA 4" | 4 | No. |  | 0
C. | DIA 8" | 4 | No. |  | 0
EXTERNAL SEWER, TRENCH & MANHOLES
SUPPLY, FIXING, TESTING AND COMMISSIONING OF EQUIPMENT, AND PIPE WORK REQUIRED TO COMPLETE THE SEWERAGE DISPOSAL SERVICES IN ALL RESPECTS WITH ACCESSORIES READY TO OPERATE AS PER SPECIFICATIONS, DRAWINGS AND INSTRUCTIONS OF THE ENGINEER.
4 | UPVC PIPES FOR SEWER DRAINAGE WITH PUSH-FIT RUBBER JOINTS INCLUDING EXCAVATION IN ANY TYPE OF SOIL, DEWATERING IF REQUIRED BEDDING, BACK FILLING WITH SELECTED MATERIAL, AND REMOVING OF EXTRA MATERIALS. INCLUDING ALL ACCESSORIES COMPLETE.
A. | DIA 6" (GREY WATER) (HVAC) | 400 | RFT |  | 0
B. | DIA 10" (BLACK WATER) | 400 | No. |  | 0
5 | CONSTRUCTION OF GULLY TRAP WITH MATERIAL INCLUDING, EXCAVATION, 4" SIZE UPVC P-TRAP CC BASE CI COVER WITH FRAME, CC BENCHING WATERPROOF INTERNAL PLASTER INLET/OUT CONNECTIONS ETC.
A. | TYPE GT, SIZE 10"X10" | 4 | No. |  | 0
6 | CONSTRUCTION OF RCC MANHOLE 1:2:4 WITH CRYSTALINE CEMENT ADMIXTURE TO APPROPRIATE DOSAGE MANHOLES WITH COMPACTED BASE: INCLUSIVE OF BITUMINOUS WATER PROOFING WITH MATERIAL INCLUDING, EXCAVATION, BASE TOP RCC SLAB CI COVER WITH FRAME, GI STEPS, CC BENCHING WATERPROOF INTERNAL PLASTER INLET/OUT CONNECTIONS ETC.
A. | SIZE. 24" x 24" 5'-6" DEPTH | 24 | No. |  | 0
7 | CONTRACTOR WILL PRICE THE SUNDRIES ITEMS FOR ALL PLUMBING & SANITARY (P&S) SERVICES AS PER SPECIFICATIONS, DRAWINGS AND INSTRUCTION OF THE CONSULTANT. | 1 | JOB |  | 0
8 | DISMANTLING AND EXCAVATION (GENERAL NATURE)
| DISMANTLING AND EXCAVATION OF GENERAL NATURE IN CC OR EARTH SOIL. INCLUDING DISPOSING OF THE MATERIAL UP TO 10 KM AWAY FROM THE SITE OR TO THE SITE DESIGNATED BY THE CLIENT. | 800 | CFT |  | 0
9 | TRENCH FOR ELECTRICAL CABLE
| > EARTHWORK IN EXCAVATION OF CABLE TRENCHES NOT EXCEEDING 4' IN DEPTH FOR LAYING OF LT CABLE AND CUTTING EXISTING CONCRETE/SOIL / GETTING OUT IN SOFT / LOOSE SOIL COMPLETE ALL AS SPECIFIED AND DIRECTED. > EARTHWORK IN FILLING IN FOUNDATION TRENCHES OR PLINTHS WITH GOOD EARTH, IN LAYERS NOT EXCEEDING 150 MM. INCLUDING WATERING AND RAMMING ETC. LAYER BY LAYER COMPLETE. > INCLUDING 4 PULL BOXES AND 2 MANHOLES > FILLING IN TRENCH BY SILVER SAND IN LAYERS AS DIRECTED AND CONSOLIDATING THE SAME BY THOROUGH SATURATION WITH WATER, RAMMING COMPLETE INCLUDING THE COST OF SUPPLY OF SAND. > CEMENT CONCRETE WITH GRADED STONE BALLAST (40 MM SIZE EXCLUDING SHUTTERING) IN GROUND FLOOR PCC (A) 1:2:4 PROPORTION > RCC CABLE TRENCH. RCC TRENCH COVER ALONG THE BOUNDARY WALL FROM TRANSFORMER TO ELECTRICAL ROOM. THE CABLE TRENCH SHALL BE FILLED WITH RIVER SAND AFTER LAYING OF CABLE AND RCC TRENCH COVERS SHALL BE PLACED IN POSITION WITH AN ADEQUATE NO OF PITS AND PROPERLY FINISHED AS PER INSTRUCTION OF THE ARCHITECT/SITE ENGINEER. | 150 | RFT |  | 0
ELECTRICAL WORKS
SECTION-A MAIN / SUB-MAIN LV PANELS & DISTRIBUTION BOARDS
Supply, testing & commissioning of following Distribution Boards as shown on drawing made with 14 SWG sheet steel housing including all installation accessories such as Rawal bolt etc. Complete in all respects. Note: (Refer Single Line Diagram) 1) All the Panels / DBs should be front accessible and maintainable. 2) Cost of Lighting Control Relays & Power Supplies should be Included in Distribution Boards . 3) The transportation and placement of DBs upto site and respective locations is also included in the work scope, complete in all respects including leveling, grouting etc. 4) Laser engraved tags required as mention in SLDs 5) Space for circuit tagging required with permanent installation on protective sheet via rivets 6) 20% space required in Panels / DBs for future provision 7) Tin platted Imported 99.99% pure Tinned Cu bus bar with heat shrink color coded sleeves to be used. 8) Hindged protective metallic door required with knob/handle. 9) Braided Door earth required. 10) Lockable handle required for main door. 11) As-built drawing pocket. 12) Cable hanging arrangement. 13) MIMIC Diagram is required on doors of all the Panels. 14) Panel Lights and Exhaust Fans with Door Limit Switch & Temperature Sensors are required in all the floor standing Panels. 15) All the Floor Standing Panels shall be Type-Tested Type. 16) MOA to be provided in the ATS of LV Panels. 17) Anti-Condensation Heater to be provided in all the Floor Standing Panels. 18) Bypass Option in-case of synch panel Failiure.
10 | LV PANEL + PFI (with Bus Coupler) | 1 | No. |  | 0
12 | DB-Pump | 1 | No. |  | 0
13 | MUDB-1 | 1 | No. |  | 0
14 | MUDB-2 | 1 | No. |  | 0
15 | DB-Server (for 4th floor) | 1 | No. |  | 0
Note: 1) Supply & Installation of MCCs required for Fire Fighting, HVAC & Plumbing Services shall be in the scope of Mechanical Works.
SECTION-B MEDIUM VOLTAGE SWITCHGEAR
16 | Supply Installation Testing Commissioning Transportation & Placement of following 11KV Incoming MV Switchgears with Phase Reversal Correction (Cassette Type) comprising with motor mechanism, metering and all protection devices CTs, PTs, Over current Protection, IBMS Complied Energy Analyzer, earth Fault Relay including complete interlocking facility by adding blocking coils, UVT, coils etc. Panel shall have provision for Cable Entry & Outgoing from Bottom. Complete with all respects having following specifications: The Cu Bus Bars shall be Tin Plated using Electroplating Method and covered with Heat Shrink Color Coded Sleeves. Complete in all respect. Breaker type: VCB Rate Voltage: 17.5kV Rated Current : 630A TP (2 No. VCB Breakers) BIL: 95kV Supply Frequency: 50 Hz Rated Power Frequency Withstand Voltage: 38 kV Rated Short Circuit Breaking Current Rating : 25KA for 3 sec. MV Panel must be Type Tested with operator safety IAC qualification FLR Cable entry from the Bottom AC supply should be provided by client. DC power supply should be supplied by supplier if required Refer Drawings and Specifications. | 1 | Job
17 | Supply Installation Testing Commissioning Transportation & Placement of following 11KV Outgoing MV Switchgears (Cassette Type) comprising with motor mechanism and all protection devices CTs, PTs, Over current Protection, IBMS Complied Energy Analyzer, earthing switch & Earth Fault Relay including complete interlocking facility by adding blocking coils, UVT, coils etc. Panel shall have provision for Cable Entry & Outgoing from Bottom. Complete with all respects having following specifications: The Cu Bus Bars shall be Tin Plated using Electroplating Method and covered with Heat Shrink Color Coded Sleeves. Complete in all respect. Breaker type: VCB Rate Voltage: 17.5kV Rated Current : 630A TP BIL: 95kV Supply Frequency: 50 Hz Rated Power Frequency Withstand Voltage: 38 kV Rated Short Circuit Breaking Current Rating : 25KA for 3 sec. MV Panel must be Type Tested with operator safety IAC qualification FLR Cable entry from the Bottom AC supply should be provided by client DC power supply should be supplied by supplier if required Refer Drawings and Specifications. | 2 | No. |  | 0
Note: 1) The Bidder shall provide the complete Technical Literature for the system offered. 2) The Transportation & Placement (Basement-1) of Equipment is also included in the work scope. 3) Minimum 3 years warranty is required.
SECTION-C DRY TYPE TRANSFORMER
18 | Supply, Installation, Testing, Commissioning, Transportation & Placement of 750 kVA ANAF Dry Type 11kV/0.415kV Step Down Power Transformer including all protection devices CTs, PTs, relay, enclosure etc. Complete in all respects, and having following specifications: Supply Frequency (HZ) 50 HZ HV winding connection Delta LV winding connection Star Vector group reference Dyn 11 Impedance at 75 ºC 6% With Force cooling Ambient Temperature 45 deg C HV Tapping (% of no-loads volts) ±2.5% , ±5%,-7.5% Method of Cooling ANAF (natural + forced ventilation for at least 40% extra rating) Enclosure IP-31 Secondary voltage at: . @ Full load 400 V . @ No load 415 V . HV Insulation Level 12 KV . Impulse KV Peak 95 BIL - . Winding Material (HV/LV) AL/AL . Insulation Class F Paint finish color Manufacturer Standard HV conductor and type Cu / Top entry Cables LV conductor type Bi-Metallic / Top entry Cables (Refer Specifications) | 2 | No.
19 | Factory Acceptance Test at the manufacturer's premises for 2 Persons (1 No. Client's Representative & 1 No. Consultant's Representative) | 1 | Job |  | 0
Note: 1) The Bidder shall provide the complete Technical Literature for the system offered. 2) The Transportation and Placement of Transformer upto foundation pad is also included in the work scope. 3) Minimum 3 years warranty is required.
SECTION-D DIESEL GENERATOR & ALLIED WORKS
20 | Supply, Installation, testing commissioning and transportation upto the respective location (Basement-1) for following Diesel Generators 415V, 3-phase, water cooled with control panel, AMF (without ATS), exhaust silencer, elbow etc. The work also includes but not limited to - Transportation upto respective location - 1/2" thick neuprene Sheet or vibration isolator and - placement on foundation pads All generators shall be supplied with electronic governor. The gensets shall be with remote radiator including pumps radiator supply & return piping, batteries in with all accessories complete in all respect. Transportation of gensets on site including all accessories complete in all respect. 4000 Operational Hours warranty from the date of commissioning is required. Note: Please find attached drawing of take-off panel for your perusal, specify size & spaces you require to install synchronizing modules and for control cabling into panel. (Refer Specifications)
22 | Supply, Installation, testing and commissioning of Auto Synchronization module (Wood Word, Data com, Deep Sea, ComAp) of 4 No. DG Set (550 kVA + 550 kVA + 250 kVA), electronic governer, Control wiring between DG Set + Synch Module and motorized ACB inside enclosure and all other accessories for above DG Sets system for Auto Synchronizing, Load Sharing and Load Management facilities. The Synch. Modules shall be enclosed in already provided MS Panel with ventilation fan. The work also includes control cabling, cable containment etc. Complete in all respect. Note: Please find attached drawing of take-off panel for your perusal, specify size & spaces you require to install synchronizing modules and for control cabling into panel. | 1 | Job |  | 0
SECTION-E ENCLOSED BUS ASSEMBLIES
Supply, installation, testing and commissioning including transportation, shifting and storing material at site must be included in quoted price. of following imported TP+N+E Compact Busway including imported accessories like elbows, flange ends, U Shape supporting hangers ,mounting accessories, complete in all respects and having attached specifications. Material : Copper Type : Compact Note: - Separate earth bar on 50% basis is required for all busways. - Expansion joints for straight length feeders shall be added in cost as per manufacturer standard without any additional cost. - All Power Busway shall be sandwich type. - All type test certificates are required; site tests shall be carried out in accordance with the provided specifications. - Supplier is advised to confirm the busway running lengths as per site conditions before final ordering to the principal. - Bidder shall submit the shop drawings with isometric views in hard copy and soft copy as well. - Installation will include hangers and other accessories like hanging rods,rawal bolts etc. - Client will not arrange the site security particularly for the material & equipment till its final erection. It will be vendor responsibility. - All Busway lengths will be measured from End to End excluding the Elbows, Flandges, Flexibles etc. - Copper connection between Breaker and Flange shall be included as mentioned below '- Flexible Joints in all the horizontal runs as per manufacturer recommendation shall be included in the quoted amount of straigth length. - Megger testing report shall be submitted by the supplier after site installation and before final testing and commissioning - Minimum 3 Years warranty is required.
40 | Busway (1250A TP+N+E) (IP-65 Rated) Location: Ground Floor Electrical Room to The Last Floor
a | Straight Lengths 1250 AMP TP+N+E | 195 | Rft |  | 0
b | Imported Galvanized Fixing Bracket with threaded rods, bolts and all other required accessories. | 1 | Job |  | 0
41 | Supply, installation, testing and commissioning of following TAP OFF Units including circuit breakers (MCB / MCCB) as per mentioned ratings, to be installed on Bus Way Turnking including all installation accessories as shown on drawing.
a | 100A TP MCCB Tap Off Unit (Icu = 25kA). | 4 | No. |  | 0
b | 300A TP MCCB Tap Off Unit (Icu = 25kA). | 8 | No. |  | 0
SECTION-F MAIN / SUBMAIN CABLES
Supply, installation, testing, commissioning and termination of following 8.7/15kV, CU/XLPE/PVC (MV Cables) in already installed Cable trench / Cable ladder / Cable tray / Duct Bank including all accessories. Complete in all respects.
42 | From K-Electric MV Switch to Consumer Switch Room Termination of Existing Cable at New MV Switch | 1 | Job |  | 0
43 | From MV Switch to MV Switch and MV Switch Transformer 3C, 300 Sq.mm 8.7/15kV, CU/XLPE/PVC | 60 | Rm. |  | 0
44 | Supply, Installation, testing and commissioning of following sizes of Main / Sub main Cables (LV Cables) in already installed cable tray, conduit etc. Including all accessories, lugs, glands etc. complete in all respect as shown on drawing.
47 | From 250kVA Generator to Synchronization Panel 4 N0 1C-240 Sqmm Cu/XLPE/PVC + ECC 1 NO 1C-70 Sqmm Cu/PVC | 30 | Rm. |  | 0
48 | From Synchronization Panel to LV Panel 24 NO 1C-240 Sqmm Cu/XLPE/PVC + ECC 4 NO 1C-70 Sqmm Cu/PVC | 40 | Rm. |  | 0
49 | From 750kVA Trafo 1 to LV Panel 12 NO 1C-240 Sqmm Cu/XLPE/PVC + ECC 2 NO 1C-70 Sqmm Cu/PVC | 30 | Rm. |  | 0
50 | From 750kVA Trafo 2 to LV Panel 12 NO 1C-240 Sqmm Cu/XLPE/PVC + ECC 2 NO 1C-70 Sqmm Cu/PVC | 35 | Rm. |  | 0
51 | From LV Panel to Fire fighting Pump 4C-95 Sqmm Cu/XLPE/PVC + ECC 1C-50 Sqmm Cu/PVC | 50 | Rm. |  | 0
52 | From LV Panel to Busway 1 12 NO 1C-240 Sqmm Cu/XLPE/PVC + ECC 2 NO 1C-70 Sqmm Cu/PVC | 100 | Rm. |  | 0
53 | From LV Panel to Busway 2 12 NO 1C-240 Sqmm Cu/XLPE/PVC + ECC 2 NO 1C-70 Sqmm Cu/PVC | 100 | Rm. |  | 0
54 | From Tap Off Box to MDB-G 4C-35 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 20 | Rm. |  | 0
55 | From Tap Off Box to MUDB-1 4C-35 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 6 | Rm. |  | 0
56 | From Tap Off Box to MUDB-2 4C-35 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 7 | Rm. |  | 0
57 | From MDB-G to DB-Pump 4C-16 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 20 | Rm. |  | 0
58 | From MDB-G to DB-G 4C-10 Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 50 | Rm. |  | 0
59 | From MUDB-1 to DB-Server (4th FIoor) 4C-6Sqmm Cu/PVC/PVC + ECC 1C-6 Sqmm Cu/PVC | 25 | Rm. |  | 0
60 | From MUDB-1 to UDB-1F 4C-10Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 20 | Rm. |  | 0
61 | From MUDB-1 to UDB-2F 4C-10Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 15 | Rm. |  | 0
62 | From MUDB-1 to UDB-3F 4C-10Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 10 | Rm. |  | 0
63 | From MUDB-1 to UDB-4F 4C-10Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 5 | Rm. |  | 0
64 | From MUDB-2 to UDB-5F 4C-10Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 10 | Rm. |  | 0
65 | From MUDB-2 to UDB-6F 4C-10Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 15 | Rm. |  | 0
66 | From MUDB-2 to UDB-7F 4C-10Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 20 | Rm. |  | 0
67 | From MUDB-2 to UDB-8F 4C-10Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 25 | Rm. |  | 0
SECTION-G CABLE CONTAINMENT
68 | Supply & installation of following sizes of 16 SWG MS Powder Coated perforated Cable tray with 18 SWG cover (4 feet covers) duly Painted after degreesing, derusting, phosphating and antirust primer including all installation accessories such as rawal bolts e.t.c. Complete in all respects. Note: - Color Printed Tags to be provided at every 3 Meter Length. - Imported C-Channel Hanger to be used for ladder hanging from ceiling. - Wall Hanger Supports to be provided with ladder moving with walls. - U-shaped fisher plates to be used for cable ladder joints - Earth bonding to be done with every cable ladder joint - Only imported cable ladder mounting accessories to be used make mungo, fischer or equivalent. - Color of cable ladder to be decided with consent of architect.
a | 450mm x 100mm Cable Tray | 200 | Rm. |  | 0
69 | Supply & installation following sizes of GI 14 SWG Cable Ladder with 16 SWG cover duly painted with 100 micron primer after degreesing, derusting, phosphating and antirust primer including all installation accessories such as rawal bolts elbows,tees e.t.c. Complete in all respect. Note: - Color Printed Tags to be provided at every 3 Meter Length. - Imported C-Channel Hanger to be used for ladder hanging from ceiling. - Wall Hanger Supports to be provided with ladder moving with walls. - U-shaped fisher plates to be used for cable ladder joints - Earth bonding to be done with every cable ladder joint - Only imported cable ladder mounting accessories to be used make mungo, fischer or equivalent. - Color of cable ladder to be decided with consent of architect.
a | 750mm x 150mm (Horizontal clipped on wall) (HT Cable) External Area With Wall supports | 30 | Rm. |  | 0
b | 750mm x 150mm (Horizontal on Roof Ceiling) | 50 | Rm. |  | 0
c | 750mm x 150mm (Vertical for HT Cable) With Wall supports | 25 | Rm. |  | 0
d | Vertical Pedestal for Generator Cable Ladder Supports (Approx: 10ft Height) | 2 | No. |  | 0
70 | Sealing all sorts of openings made due to cutting and drilling done in walls, ceiling or other areas of premises for cable containment and allied accessories with Fire resistant Material (Fire Mortar) Make: 3M or equivalent. | 30 | Cb.m |  | 0
71 | Supply and installation of Insulation rubber mat laying in MV/LV rooms (where ever required), including all materials, equipments, labor, tools, transportation, accessories etc. Complete in all respects. Contractor will submit shop drawings for approval from consultant / architect before commencement of work. | 200 | Sqm. |  | 0
72 | Supply, installation, testing and commissioning 3C, 300 Sq.mm 15KV XLPE-CU Cable MV Termination Kits with Boots including all termination accessories like HT tape etc. | 12 | No. |  | 0
Note: Contractor is advised to confirm the sizes, running lengths and termination as per site conditions before commencement of work. All the conduits / cable tray crossings through partition walls shall be properly sealed by fire retardant material after installation.
SECTION-H EARTHING / GROUNDING SYSTEM
Supply, installation, testing and commissioning of following items for Earthing / Grounding System for lightning protection and grounding of other systems including all material, boring, labor, tools, transportation, accessories etc. Complete in all respects with detailed test reports.
73 | Imported Chemical Enhanced Earth using 20 mm dia Tin Plated copper Rod including 6" dia, 11' deep boring and back filled chemical to enhance conductivity. Complete with termination clamps, 12" dia heavy duty round cover. | 9 | No. |  | 0
74 | Earth Connecting Point (ECP) or Equipotential bar made with 250mm wide, 50mm high and 8mm thick tin plated Copper, as shown in drawings. Bar shall be provided with holes suitable for installation of 6 No. 70 sqmm bare copper conductor. ECP shall be enclosed in appropriate size of powder coated metal enclosure with front accessible cover. | 6 | No. |  | 0
75 | Supply, installation, testing and commissioning of following size of Single core PVC Cables from ECP to several equipments in following sizes of PVC Conduit, including all material, labor, tools, transportation, accessories etc. Complete in all respects with detailed test reports.
a | 1C, 70 Sq.mm PVC (Green) in 32mm dia PVC Conduit | 120 | Rm. |  | 0
76 | Stranded bare copper conductors of following sizes laid in floor/raft from Earth Station to ECP. Complete in all respects including termination at ECP.
a | 95 Sq.mm Bare Copper Conductor | 150 | Rm. |  | 0
Note: Contractor is advised to confirm the cable running lengths and termination as per site conditions before commencement of work.
SUBMITTALS, INSPECTIONS, OPERATION, DRAWINGS ETC.
77 | SUBMITTALS, SAMPLES, INSPECTIONS, ETC.
| SUBMITTALS, SAMPLES, INSPECTIONS, OPERATION AND MAINTENANCE MANUALS AND THE LIKE AS REQUIRED BY SPECIFICATION. | 1 | JOB |  | 0
78 | SHOP DRAWINGS & AS-BUILT DRAWINGS
| PREPARATION AND SUBMISSION OF HARD AND SOFT (.dwg) COPIES OF SHOP DRAWINGS & AS-BUILT DRAWINGS OF EACH JOB AT THE END OF THE EXECUTION. | 1 | JOB |  | 0
| COST OF GENERAL WORKS |  |  |  | 0