## TITLE PAGE-8
STATE LIFE INSURANCE CORPORATION BUILDING No. 9 BOQ 8th FLOOR SUMMARY

## Summary-8th Floor
8th FLOOR - SUMMARY
S # N | DESCRIPTION | AMOUNT RS.
1 | Cost of Civil Work | 0
2 | Cost of Furniture | NTQ
3 | Cost of Electrical Works | 0
4 | Cost of Plumbing Works | 4584850
5 | Cost of HVAC | 24349000
| Total Cost of 8th Floor | 28933850
| LESS SALVAGE COST | 0
| NET TOTAL COST OF 8TH FLOOR | 28933850
AII taxes are incIusive
Total Amount in Words Rs.
Contractor's Signature with Stamp
Dated:

## Salvage - Title
STATE LIFE INSURANCE CORPORATION BUILDING No. 9
BOQ 8th FLOOR SALVAGEABLE MATERIAL

## Salvage BOQ
The contractor is required to store the items temporarily in the storage space provided by the client (if required). Each lot of the salvaged material shall be documented before leaving the site, including acquiring the gate pass. All salvaged items shall be considered as the contractor's property after leaving the site.
8th FLOOR - SALVAGABLE MATERIAL (TO BE CREDITED TO THE CLIENT)
S. No. | DESCRIPTION | QTY | UNIT | RATE (RS) | AMOUNT (RS)
1 | SERVICEABLE MATERIAL DEMOLITION
A. | TAKING OUT WOODEN / VIN BOARD PARTITION WALLS, WINDOWS, DOOR SHUTTERS TAKING OUT CAREFULLY AND STACKING SERVICE ABLE AT THE DESIGNATED PLACE AND CREDIT FOR THE COST OF SALVAGE TO THE CLIENT AND THEN IT WILL BE THE PROPERTY OF THE CONTRACTOR. | 4000 | Sft |  | 0
B. | TAKING OUT GLAZED ALUMINUM DOORS & WINDOWS CAREFULLY AND STACKING SERVICEABLE AT DESIGNATED PLACES AND DISPOSAL OF UNSERVICEABLE AS PER DIRECTION | 425 | Each |  | 0
C. | TAKING OUT GI PIPES, FITTINGS AND FIXTURES AND STACKING THE SERVICEABLE AT SOME DESIGNATED PLACE AS PER DIRECTION | 1 | LS |  | 0
D. | TAKING OUT ELECTRICAL WIRES, FITTINGS & FIXTURES, SWITCHBOARDS ETC. AND STACKING THE SERVICE AT SOME DESIGNATED PLACE AS PER DIRECTION. | 1 | LS |  | 0
E. | TAKING OUT CAREFULLY ELECTRICAL DISTRIBUTION BOARDS AND SUB MAIN DISTRIBUTION BOARDS AND STAKING THE SERVICEABLE IT OUT AT SOME DESIGNATED PLACE AS PER DIRECTION | 1 | LS |  | 0
F. | TAKING OUT CAREFULLY HVAC DUCTS AND STACKING THE SERVICEABLE IT AT SOME DESIGNATED PLACE AS PER DIRECTION | 1 | LS |  | 0
G. | TAKING OUT WOODEN /METALLIC RAILINGS AND STACKING THE SERVICEABLE AT SOME DESIGNATED PLACE AS PER DIRECTION. | 1 | LS |  | 0
H. | TAKING OUT CAREFULLY DOOR, WINDOWS HARDWARE ETC COMPLETE | 1 | LS |  | 0
I. | TAKING OUT CAREFULLY WINDOW BLINDS AND STACKING THE SERVICEABLE | 1 | LS |  | 0
J. | TAKING OUT CAREFULLY BUS BAR AND ACCESSORIES AND STACKING THE SERVICEABLE | 1 | LS |  | 0
| TOTAL AMOUNT TO BE CREDITED TO THE CLIENT EIGHTH |  |  |  | 0

## Electrical - Title
STATE LIFE INSURANCE CORPORATION BUILDING No. 9
BOQ 8th FLOOR ELECTRICAL WORK

## Electrical BOQ
The BOQ document shall be read in conjunction with the Compliance sheet. The rates of all the items quoted should be done considering specifications and special conditions and including the following nature of the project its shape, angle, curve, bends, size etc. to be made at any depth and height with the use of all steel formwork properly supported as required and as directed by the Engineer/ Architect to the entire satisfaction of the Architect / Engineer/ Architect-in-Charge.
8th FLOOR - ELECTRICAL WORKS
S. No. | DESCRIPTION | QTY | UNIT | RATE (RS) | AMOUNT (RS)
NOTE: SAMPLES & TECHNICAL SPECIFICATIONS TO BE SUBMITTED FOR EACH ITEM FOR APPROVAL PRIOR TO EXECUTION.
SECTION-A MAIN / SUB-MAIN LV PANELS & DISTRIBUTION BOARDS
Supply, testing & commissioning of following Distribution Boards as shown on drawing made with 14 SWG sheet steel housing including all installation accessories such as Rawal bolt etc. Complete in all respects. Note: (Refer Single Line Diagram) 1) All the Panels / DBs should be front accessible and maintainable. 2) Cost of Lighting Control Relays & Power Supplies should be Included in Distribution Boards . 3) The transportation and placement of DBs upto site and respective locations is also included in the work scope, complete in all respects including leveling, grouting etc. 4) Laser engraved tags required as mention in SLDs 5) Space for circuit tagging required with permanent installation on protective sheet via rivets 6) 20% space required in Panels / DBs for future provision 7) Tin platted Imported 99.99% pure Tinned Cu bus bar with heat shrink color coded sleeves to be used. 8) Hindged protective metallic door required with knob/handle. 9) Braided Door earth required. 10) Lockable handle required for main door. 11) As-built drawing pocket. 12) Cable hanging arrangement. 13) MIMIC Diagram is required on doors of all the Panels. 14) Panel Lights and Exhaust Fans with Door Limit Switch & Temperature Sensors are required in all the floor standing Panels. 15) All the Floor Standing Panels shall be Type-Tested Type. 16) MOA to be provided in the ATS of LV Panels. 17) Anti-Condensation Heater to be provided in all the Floor Standing Panels. 18) Bypass Option in-case of synch panel Failiure.
1 | DB-Lift | 1 | No. |  | 0
2 | DB-8F | 1 | No. |  | 0
3 | LPDB-8F | 1 | No. |  | 0
4 | UDB-8F | 1 | No. |  | 0
5 | Breaker Box with 125A TP MCCB For HVAC Large Wing Area | 1 | No. |  | 0
6 | Breaker Box with 100A TP MCCB For HVAC Small Wing Area | 1 | No. |  | 0
Note: 1) Supply & Installation of MCCs required for Fire Fighting, HVAC & Plumbing Services shall be in the scope of Mechanical Works.
SECTION-F MAIN / SUBMAIN CABLES
Supply, installation, testing, commissioning and termination of following 8.7/15kV, CU/XLPE/PVC (MV Cables) in already installed Cable trench / Cable ladder / Cable tray / Duct Bank including all accessories. Complete in all respects.
6 | From Tap Off Box to DB-8F 4C-120 Sqmm Cu/XLPE/PVC + ECC 1C-70 Sqmm Cu/PVC | 5 | Rm. |  | 0
7 | From Tap Off Box to DB-Lift 4C-35 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 5 | Rm. |  | 0
8 | From DB-Lift to Respective Lift Isolator 4C-10 Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 30 | Rm. |  | 0
9 | From DB-8F to LPDB-8F (Large Wing) 4C-16 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 5 | Rm. |  | 0
10 | From DB-8F to LPDB-8F (Small Wing) 4C-10 Sqmm Cu/PVC/PVC + ECC 1C-10 Sqmm Cu/PVC | 5 | Rm. |  | 0
11 | From DB-8F to Breaker Box For HVAC 8F1 (Large Wing) 4C-50 Sqmm Cu/PVC/PVC + ECC 1C-25 Sqmm Cu/PVC | 75 | Rm. |  | 0
12 | From DB-8F to Breaker Box For HVAC 8F2 (Small Wing) 4C-35 Sqmm Cu/PVC/PVC + ECC 1C-16 Sqmm Cu/PVC | 45 | Rm. |  | 0
WIRING
13 | CIRCUIT / POINT WIRING & SWITCH ACCESSORIES
| PROVIDING, FIXING & LAYING OF WIRING FOR LIGHTS AND EXHAUST/ FALSE CEILING/ CEILING FANS, WITH COMPLETE INSTALLATION ON WHATEVER SURFACE; THE PRICE IS TO INCLUDE ANY FABRICATION/ BOXING MADE OF ANODIZED GI FRAME OR WOODEN FRAME AS ADVISED BY THE ARCHITECT ON-SITE IF NEEDED TO BE MOUNTED ON THE CEILING DIRECTLY. ALL MOUNTINGS AND VERTICAL SUSPENSIONS WILL BE DONE USING FISCHER OR EQUIVALENT ANCHORS WITH M10 THREADED GI RODS. IN 20/25 mm DIA PVC GALCO CONDUIT RECESSED IN WALLS, COLUMNS AND CEILING ETC. (IF REQUIRED) COMPLETE WITH BENDS, SOCKETS, AND OTHER ACCESSORIES WITH 3X2.5 mm PVC INSULATED WIRE OF PAKISTAN CABLES /FAST/NEWAGE WITH 16 SWG SHEET STEEL SWITCH BOXES DULY APPLIED WITH RED OXIDE BASE PAINT SPRAY PAINTED AS REQUIRED AND THE BOX TO BE CONCEALED AND INCLUDING P/F OF 10A CLIPSAL/ CLOPAL/ SIEMENS MAKE SWITCH WITH CLIPSAL/ CLOPAL/ SIEMENS COVER GANG PLATE ETC. AND CONCEALED WITH CEILING ROSE COMPLETE IN ALL RESPECT AS REQUIRED. | 70 | No. |  | 0
14 | SAME AS (A) BUT POINT TO POINT WIRING | 450 | No. |  | 0
15 | PROVIDING, FIXING & LAYING OF WIRING POWER CIRCUITS FROM DB TO MULTI- SWITCHBOARD (S) (MB-1) WITH 2 X 4 SQ. mm + ECC 1X2.5 SQ. mm PVC INSULATED WIRE OF PAKISTAN CABLES /FAST /NEWAGE IN 20/25 mm DIA PVC GALCO CONDUIT RECESSED IN WALLS, COLUMNS AND CEILING ETC. (IF REQUIRED) COMPLETE WITH BENDS, SOCKETS AND OTHER ACCESSORIES COMPLETE IN ALL RESPECT AS REQUIRED. | 55 | No. |  | 0
16 | PROVIDING, FIXING & LAYING OF WIRING POWER CIRCUITS FROM DB TO SWITCHBOARD (S) (INDUSTRIAL SOCKETS) WITH 2 X 4 SQ. mm + ECC 1X2.5 SQ. mm PVC INSULATED WIRE OF PAKISTAN CABLES /FAST /NEWAGE IN 20/25 MM DIA PVC GALCO CONDUIT RECESSED IN WALLS, COLUMNS AND CEILING ETC. (IF REQUIRED). INCLUDING I/O FACE PLATE. COMPLETE WITH BENDS, SOCKETS AND OTHER ACCESSORIES COMPLETE IN ALL RESPECT AS REQUIRED. | 45 | No. |  | 0
17 | PROVIDING, FIXING, INSTALLING, TESTING AND COMMISSIONING OF NETWORKING TWO (2) CABLE CAT 6 CLIPSAL / 3M CABLE IN 20 MM DIA PVC GALCO CONDUIT /CHANNEL TERMINATED AT DESIGNATED I/O FACE PLATE HAVING 02 No. CAT6 CONNECTORS, CLIPSAL MAKE OR EQUIVALENT WITH 16 SWG MS BACK BOX COMPLETE IN ALL RESPECTS. NOTE: ALL DATA CABLES SHALL HAVE SEPARATE CONDUITS FROM POWER LINES TO AVOID ELECTROMAGNETIC FIELD (EMF) INTERFERENCE AND ATTENUATION. | 55 | No. |  | 0
18 | PROVIDING, FIXING, INSTALLING, TESTING AND COMMISSIONING OF TELEPHONE RJ45 CLIPSAL / 3M CABLE IN 20 MM DIA PVC GALCO CONDUIT /CHANNEL TERMINATED AT DESIGNATED I/O FACE PLATE HAVING 01 No. RJ-45/RJ11 CONNECTORS, CLIPSAL MAKE OR EQUIVALENT WITH 16 SWG MS BACK BOX COMPLETE IN ALL RESPECTS. | 6 | No. |  | 0
19 | CORE CUTTING
CORE CUTTING / DRILLING TO DRILL HOLES OF SPECIFIED SIZE IN WALLS OR SLABS OF CONCRETE TO FACILITATE INSTALLATION AND REPAIR OF UTILITY SYSTEMS AND EQUIPMENT. INCLUDING MARKING POSITION FOR DRILL BASE, USING RULER AND CHALK.
A. | 4" DIA | 15 | No. |  | 0
B. | 6" DIA | 5 | No. |  | 0
C. | 8" DIA | 1 | No. |  | 0
SWITCH SOCKET OUTLET (SSO)
NOTE: SAMPLES & TECHNICAL SPECIFICATIONS ARE TO BE SUBMITTED FOR EACH ITEM FOR APPROVAL PRIOR TO EXECUTION.
20 | SUPPLY & INSTALLATION OF THE FOLLOWING SWITCH SOCKET OUTLETS (SSO) OF MAKE CLOPAL, SIEMENS, CLIPSAL, AND ORANGE, WITH 16 SWG MS BACK BOXES MADE OF 1.2 MM POWER COATED SHEET STEEL WITH EARTH TERMINALS, AS PER SPECIFICATION AND RECOMMENDATION OF ARCHITECT AFTER APPROVAL OF PHYSICAL SAMPLE, INSULATED WIRE OF PAKISTAN CABLES /FAST /NEWAGE IN 20/25 MM DIA PVC GALCO CONDUIT RECESSED IN WALLS, COLUMNS AND CEILING ETC. (IF REQUIRED) COMPLETE WITH BENDS, SOCKETS AND OTHER ACCESSORIES COMPLETE IN ALL RESPECT AS REQUIRED
A. | 13AMP UNIVERSAL/INTERNATIONAL 3 PIN SSO PVC INSULATED WIRE | 30 | No. |  | 0
B. | 15AMP UNIVERSAL/INTERNATIONAL 3PIN SSO (INDUSTRIAL SOCKETS) | 15 | No. |  | 0
GANG SWITCHES
NOTE: SAMPLES & TECHNICAL SPECIFICATIONS ARE TO BE SUBMITTED FOR EACH ITEM FOR APPROVAL PRIOR TO EXECUTION.
21 | SUPPLY AND INSTALLATION OF FOLLOWING 10 AMPS, ONE-WAY GANG TYPE SWITCHES OF MAKE CLOPAL, SIEMENS, CLIPSAL OR EQUIVALENT, INCLUDING BACK BOXES, RECESSED ON WALL OR COLUMN AS PER DESIGN DRAWINGS, AS PER SPECIFICATION AND RECOMMENDATION OF ARCHITECT AFTER APPROVAL OF PHYSICAL SAMPLE, COMPLETE WITH ALL ACCESSORIES & CONNECTIONS IN ALL RESPECTS.
A. | 3 GANG SWITCHES | 1 | No. |  | 0
B. | 4 GANG SWITCHES | 60 | No. |  | 0
TECHNOLOGY BOX / BOARD
NOTE: SAMPLES & TECHNICAL SPECIFICATIONS ARE TO BE SUBMITTED FOR EACH ITEM FOR APPROVAL PRIOR TO EXECUTION.
22 | SUPPLY AND INSTALLATION OF TECHNOLOGY BOX / BOARD OF MAKE CLOPAL, SIEMENS, CLIPSAL OR EQUIVALENT, INCLUDING WATERPROOF BACK BOXES, WATERPROOF HOUSING WITH LID AND POWER SWITCH, FIXED ON A WORKSTATION, GYPSUM OR ANY OTHER SURFACE WALL AS PER DESIGN DRAWINGS, AS PER SPECIFICATION AND RECOMMENDATION OF ARCHITECT AFTER APPROVAL OF PHYSICAL SAMPLE, INCLUDING CABLE MANAGEMENT VIA SQUARE MATCHING PIPE OF 18 SWG EARTHED OR CABLE MANAGEMENT SLEEVES OF BEST QUALITY AS PER APPROVAL OF TECHNICAL SPECIFICATIONS AND SAMPLES BY THE ARCHITECT ON SITE. ALL CABLES ARE TO BE TAGGED VISIBLY END TO END. APPROPRIATE DATA/ POWER CABLES/ WIRES WILL RUN THROUGH APPROPRIATE CONDUITS INSIDE THE ALUMINIUM CHANNEL. COMPLETE WITH ALL ACCESSORIES & CONNECTIONS IN ALL RESPECTS HAVING THE FOLLOWING SWITCH AND SOCKETS.
A. | TECHNOLOGY BOX A (FOR GENERAL WORKSTATIONS) A. 2 x 16 AMP UNIVERSAL /INT. 3 PIN SSO LIVE POWERED. B. 1 x 10 AMP UNIVERSAL /INT. 3 PIN SSO UPS POWERED. C. 2 x CAT 6 D. 0 x HDMI CABLE (FROM DESK TO TV SCREEN) | 48 | No. |  | 0
B. | TECHNOLOGY BOX B (FOR EXECUTIVE DESK) A. 3 x 16 AMP UNIVERSAL /INT. 3 PIN SSO LIVE POWERED. B. 1 x 10 AMP UNIVERSAL /INT. 3 PIN SSO UPS POWERED. C. 3 x CAT 6 D. 1 x HDMI CABLE (FROM DESK TO TV SCREEN) | 4 | No. |  | 0
C. | TECHNOLOGY BOX C (EXECUTIVE TV / MEETING TV) A. 2 x 16 AMP UNIVERSAL /INT. 3 PIN SSO LIVE POWERED. B. 1 x 10 AMP UNIVERSAL /INT. 3 PIN SSO UPS POWERED. C. 2 x CAT 6 D. 1 x HDMI CABLE (FROM DESK TO TV SCREEN) | 5 | No. |  | 0
D. | TECHNOLOGY BOX D (ATTENDANCE MACHINE) A. 0 x 16 AMP UNIVERSAL /INT. 3 PIN SSO LIVE POWERED. B. 1 x 10 AMP UNIVERSAL /INT. 3 PIN SSO UPS POWERED. C. 1 x CAT 6 D. 0 x HDMI CABLE (FROM DESK TO TV SCREEN) | 4 | No. |  | 0
LIGHT FITTINGS AND FIXTURES
NOTE: SAMPLES & TECHNICAL SPECIFICATIONS ARE TO BE SUBMITTED FOR EACH ITEM FOR APPROVAL PRIOR TO EXECUTION.
23 | LED CEILING RECESSED DOWN LIGHT
P/F, CONNECTING, TESTING & COMMISSIONING OF OPPLE/ SOGO/ PHILIPS/ BRITLITE/ ORANGE RECESSED MOUNTED DOWNLIGHT HAVING APPROVED COLOUR TEMPERATURE with PF >0.90 AS PER SPECIFICATION AND RECOMMENDATION OF ARCHITECT AFTER APPROVAL OF PHYSICAL SAMPLE, COMPLETE WITH MAKING A HOLE AS MAY BE REQUIRED AND TO FINISH THE SURFACE SUITABLY AFTER INSTALLATION AND WITH ALL NECESSARY CONNECTIONS, COMPLETE IN ALL RESPECTS. NOTE: ALL SAMPLES/TECHNICAL SPECIFICATIONS ARE TO BE APPROVED BY THE ARCHITECT PRIOR TO THE EXECUTION OF WORKS.
A. | 6W TO 9W | 30 | No. |  | 0
B. | 10W TO 12W | 185 | No. |  | 0
C. | 13W TO 15W | 63 | No. |  | 0
24 | CEILING RECESSED LINEAR LIGHT MAGNETIC TRACK
| PROVIDING, INSTALLING, CONNECTING, TESTING, AND COMMISSIONING OF APPROX. 1 METER LONG CEILING RECESSED LINEAR MAGNETIC TRACK LIGHT CONNECTED TO MAKE TRACKS OF SUITABLE DIMENSIONS WITH COMPLETE ACCESSORIES AND JOINERIES SUCH AS POWER ADPATER 200 WATTS, CONTINUITY TRACK TO TRACK CONNECTOR. RECESSED IN FALSE CEILING USING THREADED RODS AS ANCHORS. EACH TRACK TO HAVE ATLEAST 4 LIGHTS HAVING 12 LED POINTS RATED AT 12 WATTS EACH MAGENTIC LIGHT WITH REFLECTORS. OF ARCHITECTS CHOICE AND APPROVAL. NOTE: CONTRACTOR TO SUBMIT SAMPLES OF EACH ITEM TO BE USED ALONG WITH SPECIFICATION TO CONSULTANT FOR APPROVAL. THE CONTRACTOR MUST PROVIDE DETAILED SHOP DRAWINGS BEFORE THE COMMENCEMENT OF WORK. | 10 | No. |  | 0
25 | LINEAR TRACK LIGHT
PROVIDING, INSTALLING, CONNECTING, TESTING, AND COMMISSIONING OF APPROX. 3' 0" LINEAR TRACK LIGHT. HAVING 2 LIGHTS PER FEET 6 WATTS LED. NOTE: CONTRACTOR TO SUBMIT SAMPLES OF EACH ITEM TO BE USED ALONG WITH SPECIFICATION TO CONSULTANT FOR APPROVAL. THE CONTRACTOR MUST PROVIDE DETAILED SHOP DRAWINGS BEFORE THE COMMENCEMENT OF WORK.
A. | LIFT LOBBY | 20 | No. |  | 0
B. | LIBRARY | 16 | No. |  | 0
26 | WALL SCONCE DOWNLIGHT (STAIRS)
PROVIDING, INSTALLING, CONNECTING, TESTING, AND COMMISSIONING OF WALL SCONE DOWNLIGHT APPROX 15 WATT. OF APPROVED DESIGN. NOTE: CONTRACTOR TO SUBMIT SAMPLES OF EACH ITEM TO BE USED ALONG WITH SPECIFICATION TO CONSULTANT FOR APPROVAL. THE CONTRACTOR MUST PROVIDE DETAILED SHOP DRAWINGS BEFORE THE COMMENCEMENT OF WORK.
A. | LIFT LOBBY | 10 | No. |  | 0
27 | HANGING LIGHT LINEAR L1 (WORKSTATIONS)
| PROVIDING, INSTALLING, CONNECTING, TESTING, AND COMMISSIONING OF APPROX. 5' 3" LONG 30WATTS LINEAR DC LIGHT ALUMINUM BODY WITH LIGHT DIFFUSE KIT WITH • DIFFUSED LIGHTING AND GRID LIGHTING TO BE AVILABLE IN ONE UNIT HAVING POLYCARBONATE SHEET AS PER LENGTH SPECIFIED AND AGREED BY ARCHITECT. WITH LED LIGHT DRIVER. COMPLETE WITH HANGING ACCESSORIES. PHILIPS GREENUP LINEAR FLEX OR EQUIVALENT NOTE: CONTRACTOR TO SUBMIT SAMPLES OF EACH ITEM TO BE USED ALONG WITH SPECIFICATION TO CONSULTANT FOR APPROVAL. THE CONTRACTOR MUST PROVIDE DETAILED SHOP DRAWINGS BEFORE THE COMMENCEMENT OF WORK. | 14 | No. |  | 0
28 | HANGING LIGHT LINEAR L2
| PROVIDING, INSTALLING, CONNECTING, TESTING, AND COMMISSIONING OF APPROX. 3' 0" LONG 20 WATTS LINEAR DC LIGHT ALUMINUM BODY WITH LIGHT DIFFUSE KIT.. WITH LED LIGHT DRIVER DIFFUSED LIGHTING AND GRID LIGHTING TO BE AVILABLE IN ONE UNIT HAVING POLYCARBONATE SHEET AS PER LENGTH SPECIFIED AND AGREED BY ARCHITECT. WITH LED LIGHT DRIVER. COMPLETE WITH HANGING ACCESSORIES. PHILIPS GREENUP LINEAR FLEX OR EQUIVALENT. NOTE: CONTRACTOR TO SUBMIT SAMPLES OF EACH ITEM TO BE USED ALONG WITH SPECIFICATION TO CONSULTANT FOR APPROVAL. THE CONTRACTOR MUST PROVIDE DETAILED SHOP DRAWINGS BEFORE THE COMMENCEMENT OF WORK. | 4 | No. |  | 0
29 | HANGING LIGHT LINEAR L3 (CHIEF DESK & MEETING ROOM)
| PROVIDING, INSTALLING, CONNECTING, TESTING, AND COMMISSIONING OF APPROX. 5' 6" LONG 30 WATTS LINEAR DC LIGHT ALUMINUM BODY WITH LIGHT DIFFUSE KIT. DIFFUSED LIGHTING AND GRID LIGHTING TO BE AVILABLE IN ONE UNIT HAVING POLYCARBONATE SHEET AS PER LENGTH SPECIFIED AND AGREED BY ARCHITECT. WITH LED LIGHT DRIVER. COMPLETE WITH HANGING ACCESSORIES. PHILIPS GREENUP LINEAR FLEX OR EQUIVALENT NOTE: CONTRACTOR TO SUBMIT SAMPLES OF EACH ITEM TO BE USED ALONG WITH SPECIFICATION TO CONSULTANT FOR APPROVAL. THE CONTRACTOR MUST PROVIDE DETAILED SHOP DRAWINGS BEFORE THE COMMENCEMENT OF WORK. | 4 | No. |  | 0
30 | CHANDELIER LIGHT
| PROVIDING, INSTALLING, CONNECTING, TESTING, AND COMMISSIONING CHANDELIER LIGHT. HAVING CLUSTER OF 4 NOTE: CONTRACTOR TO SUBMIT SAMPLES OF EACH ITEM TO BE USED ALONG WITH SPECIFICATION TO CONSULTANT FOR APPROVAL. THE CONTRACTOR MUST PROVIDE DETAILED SHOP DRAWINGS BEFORE THE COMMENCEMENT OF WORK. | 2 | No. |  | 0
31 | FLOOR STANDING LAMP
| PROVIDING, INSTALLING, CONNECTING, TESTING, AND COMMISSIONING FLOOR STANDING LAMP. NOTE: CONTRACTOR TO SUBMIT SAMPLES OF EACH ITEM TO BE USED ALONG WITH SPECIFICATION TO CONSULTANT FOR APPROVAL. THE CONTRACTOR MUST PROVIDE DETAILED SHOP DRAWINGS BEFORE THE COMMENCEMENT OF WORK. | 5 | No. |  | 0
32 | WALL / MIRROR LIGHTS
| PROVIDING, INSTALLING, CONNECTING, TESTING, AND COMMISSIONING WALL / MIRROR LIGHTS. NOTE: CONTRACTOR TO SUBMIT SAMPLES OF EACH ITEM TO BE USED ALONG WITH SPECIFICATION TO CONSULTANT FOR APPROVAL. THE CONTRACTOR MUST PROVIDE DETAILED SHOP DRAWINGS BEFORE THE COMMENCEMENT OF WORK. | 8 | No. |  | 0
33 | EMERGENCY LIGHT
P/F OF EMERGENCY LIGHT OF MAKE "OPPLE/ SOGO/ ORIENT/ OR PHILIPS” BRITLITE/ 2 X 8W FLUORESCENT LAMPS HAVING COLOUR TEMPERATURE 3500 K WITH BATTERY CHARGER. CONTRACTOR TO ENSURE THE PERFECT SOLUTION FOR HANGING, AND FIXING ON THE WALL ALONG WITH A POWER CABLE AND PLUG FOR CONNECTION. CONTRACTOR TO ENSURE LIVE WIRING IS TO BE PROVIDED ALONG WITH MALE/ FEMALE CONNECTION SECURED & TIED AWAY.
A. | CEILING / WALL MOUNTED | 30 | No. |  | 0
34 | COMPLETE DOCUMENTATION TESTING COMMISSIONING OF THE LIGHTING SYSTEM ALONG WITH A LEDGER FORMAT DOCUMENT FOR ALL THE COMPONENTS USED AND ACCESSORIES INSTALLED MARKING THE ROUTES AND OTHER NECESSARY ITEMS. | 1 | JOB |  | 0
APPLIANCES
35 | FALSE CEILING FAN
| PROVIDING, INSTALLING, TESTING AND COMMISSIONING OF FALSE CEILING FAN 14" IN 2'X2' SQUARE SIZE OF MAKE "VOLDAM OR EQUIVALENT" WITH REMOTE CONTROL IMPORTED COMPLETE WITH CONNECTIONS, AS PER SPECIFICATION AND RECOMMENDATION OF ARCHITECT. NOTE: ALL ELECTRICAL WIRING, SWITCHES AND HOISTING OF REMOTE CONTROLLER ON WALLS TO BE INCLUDED IN THE ITEM. | 30 | No. |  | 0
36 | LED MONITOR
SUPPLYING, FIXING, INSTALLATION & COMMISSIONING OF LED MONITOR OF MAKE SAMSUNG, L.G., SONY OR EQUIVALENT WITH , HDMI PORTS COAXIAL PORT, AUDIO VIDEO PORT, VGA PORT VIDEO INPUT PORT. WITH ALL NECESSARY CONNECTIONS, COMPLETE IN ALL RESPECTS AS PER SPECIFICATION AND RECOMMENDATION OF ARCHITECT/ ENGINEER. NOTE: > EASYLINK (HDMI-CEC) > SMARTVIEW > WIFI DIRECT > CONNECTIVITY PORTS: HDMI PORTS 4(SIDE) USB SUPPORTS AUDIO, VIDEO, IMAGE RF INPUT ANALOG COAXIAL PORTS 1(REAR) COMPOSITE INPUT AUDIO VIDEO CABLE PORTS 1(REAR) USB PORTS 3 DIGITALOPTICAL AUDIO OUTPUT PORTS 1 > VENDORS OFFERING LOCAL AFTER SALE SERVICES SHALL BE PREFERRED.
A. | 55" | 6 | No. |  | 0
B. | 65" | 0 | No. |  | 0
C. | HDMI CABLE 5 METER (SONY, UGREEN OR EQUIVALENT) | 6 | No. |  | 0
37 | WATER DISPENSER
| SUPPLY AND INSTALLATION OF WATER DISPENSER OF ANY RENOWNED BRAND (PEL, ORIENT, DAWLANCE OR EQUIVALENT) | 4 | No. |  | 0
38 | GLASS HOOD (KITCHEN)
| SUPPLY AND INSTALLATION OF GLASS HOOD OF ANY RENOWNED BRAND (PEL, ORIENT, DAWLANCE OR EQUIVALENT). | 2 | No. |  | 0
39 | MICROWAVE OVEN
SUPPLY AND INSTALLATION OF MICROWAVE OWEN OF ANY RENOWNED BRAND (PEL, ORIENT, DAWLANCE OR EQUIVALENT).
A. | IN-BUILT INTO CABINET | 1 | No. |  | 0
B. | NORMAL | 2 | No. |  | 0
40 | REFRIGERATOR
| SUPPLY AND INSTALLATION OF REFRIGERATOR OF ANY RENOWNED BRAND (PEL, ORIENT, DAWLANCE OR EQUIVALENT). | 2 | No. |  | 0
41 | EXHAUST FAN (WITH FALSE CELING PIPE )
| PROVIDING, INSTALLING, TESTING AND COMMISSIONING OF 6" DIA INLINE FAN OF MAKE "VOLDAM OR EQUIVALENT" WITH CENTRIFUGAL BLOWER AND MOTOR ENCASED IN SHEET METAL CASING, AS PER SPECIFICATIONS. THE MOTOR SHALL BE SUITABLE FOR 220 ± 6% V, 50 HZ AC SUPPLY. THE PRICE SHALL INCLUDE FAN SPEED REGULATOR AND COWL WITH BIRD SCREEN. CAPACITY 3600 CMH AT 15 MM STATIC PRESSURES (FOR PNEUMATIC TEST SCREEN OF WORKSHOP OFFICES BUILDING). | 10 | No. |  | 0
42 | HAND DRYER
| P/F OF AUTOMATIC HAND DRYER OF BRAND SIEMENS OR EQUIVALENT COMPLETE IN ALL RESPECTS. NOTE: TECHNICAL SPECIFICATION TO BE APPROVED BY THE ARCHITECT PRIOR TO PROCUREMENT. | 6 | No. |  | 0
TELEPHONES
NOTE: SAMPLES & TECHNICAL SPECIFICATIONS ARE TO BE SUBMITTED FOR EACH ITEM FOR APPROVAL PRIOR TO EXECUTION.
43 | TELEPHONE 5 PAIR CABLE
| SOLID ANNEALED COPPER WIRE, PLAIN OR TINNED ACCORDING TO IEC 60228 CLASS 1, INSULATED WITH PVC (POLYVINYL CHLORIDE) RATED 70°C, TWO CORES ARE TWISTED TO FORM A PAIR, PAIRS ASSEMBLED TOGETHER DEPENDING ON THE CABLE CONSTRUCTION, FOR CABLES UP TO 5 PAIRS , PAIRS ARE ASSEMBLED TOGETHER DIRECTLY IN CONCENTRIC LAYERS, ALL PAIRS ARE IDENTIFIED WITH IDENTIFICATION TAPES, OUTER SHEATH IS A FLAME RETARDANT POLYVINYL CHLORIDE 70°C, GRAY COLOR. | 45 | METER |  | 0
44 | JUNCTION BOX
| PROVIDING AND FIXING OF TELEPHONE JUNCTION HAVING CONNECTION OF NOT LESS THAN 10 WIRES, WALL MOUNTED. | 1 | No. |  | 0
45 | P/L OF TELEPHONE WIRING IN PVC CONDUIT GALCO 32MM DIA 10 PAIR TELEPHONE CABLE CLIPSAL MAKE FROM MDF PANEL TO PTCL CABINET AND PABX. COMPLETE WITH 12SWG COPPER ECC AND CONNECTIONS AT TERMINAL BOXES COMPLETE IN ALL RESPECTS AS REQUIRED AT SITE. | 1500 | METER |  | 0
47 | PROVIDING, FIXING, INSTALLING, TESTING AND COMMISSIONING OF NETWORKING CABLE CAT 6 CLIPSAL / 3M CABLE IN 20 MM DIA PVC GALCO CONDUIT /CHANNEL TERMINATED AT DESIGNATED CAT6 CONNECTORS, INCLUSIVE OF IO SWITCH PLATE HAVING CAT 6 INTERFACE CLIPSAL MAKE OR EQUIVALENT WITH 16 SWG MS BACK BOX COMPLETE IN ALL RESPECTS. NOTE: ALL DATA CABLES SHALL HAVE SEPARATE CONDUITS FROM POWER LINES TO AVOID ELECTROMAGNETIC FIELD (EMF) INTERFERENCE AND ATTENUATION. | 45 | No. |  | 0
NETWORKING
53 | FIBRE OPTIC CABLE (FROM DISTRIBUTOR TO FLOOR SWITCH) | 150 | METER |  | 0
SECURITY SYSTEM
ALL NETWORK ACCESSORIES ARE TO BE A PART OF THIS ITEM, INCLUDING RACKS, MOUNTING SCREWS, RAWL BOLTS, ANCHORS, MOUNTING BRACKETS AND ETC.
56 | BIOMETRIC ATTENDANCE MACHINE / CCTV CAMERA SUPPLY, INSTALLATION, CONFIGURATION, TESTING AND COMMISSIONING OF BIOMETRIC (FINGERPRINT CUM CARD, FACIAL ID) BASED TIME ATTENDANCE & ACCESS CONTROL MACHINES INCLUDING RELATED SOFTWARE. > BIOMETRIC/ CARD ENROLLMENT/ FACIAL ID- RFID TAGS OF 100 PERSONS (INCLUDING COLLECTION, ENTRY AND VALIDATION OF DATA) OF ALL RELEVANT INFORMATION OF THE EMPLOYEES LIKE FINGERPRINTS, PHOTOGRAPHS, CONTACT INFORMATION ETC. TO ENSURE A COMPREHENSIVE DATABASE OF INFORMATION FOR THE FUNCTIONING OF THE TIME AND ATTENDANCE BIOMETRIC SYSTEM. | 1 | No. |  | 0
57 | SUPPLY & INSTALLATION OF FIXED TYPE CEILING MOUNTED DOME CAMERA TRUE DAY / NIGHT WITH IR ILLUMINATOR,2-MP, FIXED LENS OF 4 MM, WDR, FACE RECOGNITION TILL MINIMUM 10 METER COMPLETE WITH HOUSING, MOUNTING BRACKETS, ENCLOSURE FOR POWER SUPPLY ETC AS PER DRAWING & SPECIFICATION & SCHEDULE OF CAMERA COMPLETE IN ALL RESPECTS. | 10 | No. |  | 0
58 | SUPPLY & INSTALLATION OF PoE (POWER OVER ETHERNET) CABLE FROM NVR TO CAMERA LOCATION. COMPLETE WITH HOUSING, MOUNTING BRACKETS, ENCLOSURE FOR POWER SUPPLY ETC AS PER DRAWING & SPECIFICATION & SCHEDULE OF CAMERA COMPLETE IN ALL RESPECTS. AVERAGE LENGTH 170 RFT | 10 | No. |  | 0
59 | SUPPLY & INSTALLATION OF 2U SERVER RACK AS PER DRAWING & SPECIFICATION COMPLETE IN ALL RESPECT | 1 | No. |  | 0
60 | SUPPLY & INSTALLATION OF CABLE MANAGEMENT KIT FOR 2U RACK CABLE MANAGER TYPE: HORIZONTAL D-RING NUMBER OF D-RINGS: 5 D-RING MATERIAL: PLASTIC BACK PLATE MATERIAL: 18 GAUGE COLD ROLLED STEEL BACK PLATE FINISH: POWDER COATED COMPLETE IN ALL RESPECT | 1 | No. |  | 0
61 | SUPPLY & INSTALLATION OF 32 CHANNEL NVR HAVING NOT LESS THAN 24 PoE POINTS STACKBALE VIRTUALLY TO ACCOMMODATE ALL THE CAMERAS AND STORAGE CAPACITY OF 30 DAYS (16TB HARDISK) AT HIGH QUALITY, 25 FPS, AND ADJUSTABLE NOISE RATIO AS PER DRAWING & SPECIFICATION COMPLETE IN ALL RESPECT | 1 | No. |  | 0
62 | COMPLETE DOCUMENTATION TESTING COMMISSIONING OF THE SECURITY SURVEILLANCE SYSTEM ALONG WITH A LEDGER FORMAT DOCUMENT FOR ALL THE COMPONENTS USED AND ACCESSORIES INSTALLED MARKING THE ROUTES AND OTHER NECESSARY ITEMS.INCLUSIVE OF ALL THE LICENSE | 1 | JOB |  | 0
63 | COMPLETE TRAINING OF LOCAL TECHNICIANS FOR OPERATION, MAINTENANCE OF SECURITY SYSTEM | 1 | JOB |  | 0
FIRE ALARM SYSTEM
ALL NETWORK ACCESSORIES ARE TO BE A PART OF THIS ITEM, INCLUDING RACKS, MOUNTING SCREWS, RAWL BOLTS, ANCHORS, MOUNTING BRACKETS AND ETC.
64 | SUPPLY & INSTALLATION OF ADDRESSABLE MANUAL CALL POINTS WITH ISOLATOR MODULE, BASE & MOUNTING ACCESSORIES COMPLETED IN ALL RESPECTS AS PER DRAWINGS AND SPECIFICATIONS. | 10 | No. |  | 0
65 | SUPPLY & INSTALLATION OF ADDRESSABLE DIRECTIONAL ELECTRONIC SOUNDER WITH FLASHER WITH MOUNTING ACCESSORIES, AND BACK BOX. COMPLETE IN ALL RESPECTS AS PER DRAWINGS AND SPECIFICATIONS. | 10 | No. |  | 0
66 | SUPPLY AND INSTALLATION OF INTELLIGENT CELING RECESSED/SURFACE MOUNTED SMOKE DETECTORS WITH ISOLATOR MODULE, BASE & MOUNTING ACCESSORIES COMPLETE IN ALL RESPECTS AS PER DRAWINGS AND SPECIFICATIONS. | 10 | No. |  | 0
67 | SUPPLY AND INSTALLATION OF CEILING RECESSED/SURFACE MOUNTED HEAT DETECTORS WITH ISOLATOR MODULE, BASE & MOUNTING ACCESSORIES COMPLETE IN ALL RESPECTS AS PER DRAWINGS AND SPECIFICATIONS. | 2 | No. |  | 0
68 | SUPPLY AND INSTALLATION OF 4 ZONES INTELLIGENT ADDRESSABLE NETWORKED FIRE ALARM CONTROL PANEL(FACP) WITH POWER SUPPLY AND BATTERY BACKUP FOR 3 HOURS WITH INSTALLATION ACCESSORIES COMPLETE IN ALL RESPECTS AS PER DRAWINGS AND SPECIFICATIONS. TO BE INTEGRATED TO BUILDING FACP SYSTEM. | 1 | No. |  | 0
69 | SUPPLY & INSTALLATION OF LOOP WIRING FROM FACP TO FIELD DEVICES WITH 2X2.5 SQ.MM FP- 200 CLASS A CABLE WITH 3HRS FIRE RATING IN 1" DIA 16-GAUGE MS PIPE SURFACE AS PER DRAWINGS WITH ALL CONDUIT ACCESSORIES, JUNCTION BOXES, PULL BOXES ETC. COMPLETE IN ALL RESPECTS AS PER DRAWINGS AND SPECIFICATIONS. ACTUAL MEASUREMENT SHALL BE TAKEN FROM THE SITE. | 7000 | RFT |  | 0
70 | SPARE PARTS FOR FIRE ALARM SYSTEM FOR 2 YEAR OPERATION | 1 | JOB |  | 0
71 | COMPLETE TRAINING OF LOCAL TECHNICIANS FOR OPERATION, MAINTENANCE OF FIRE ALARM SYSTEM | 1 | JOB |  | 0
72 | 2 YEARS WARRANTY ALONG WITH COMPLETE PREVENTIVE MAINTENANCE OF ALL COMPONENTS OF FIRE ALARM SYSTEM. | 1 | JOB |  | 0
73 | COMPLETE DOCUMENTATION TESTING COMMISSIONING OF THE FIRE ALARM SYSTEM ALONG WITH A LEDGER FORMAT DOCUMENT FOR ALL THE COMPONENTS USED AND ACCESSORIES INSTALLED MARKING THE ROUTES AND OTHER NECESSARY ITEMS. INCLUSIVE OF ALL THE LICENSE | 1 | JOB |  | 0
AUDITORIUM
74 | SPEAKERS (REFERENCE SERIES)
SUPPLYING, FIXING OF BEST QUALITY 14 CHANNELS, 4 ZONES SPEAKERS AND AMPLIFIERS
A. | SPEAKERS (8 Watts CEILING MOUNTED SPEAKERS DC. WITH TOP GRILLS. COMPLETE IN ALL ASPECTS.) TOA, BOSE, OR EQUIVALENT. | 14 | No. |  | 0
B. | AMPLIFIERS 5 INPUT FOR MICS. AND AV FOR EACH AMPLIFIER SYNCHRONIZED TO EACH OTHER TO WORK AS ONE. ITEM TO INCLUDE ANY ADDITIONAL ACCESSORY AS PER MANUFACTURER TO FULFILL THE FUNCTION. | 3 | No. |  | 0
C. | AUDIO MIXER FOR ADDITIONAL INPUTS 8 INPUTS. | 1 | No. |  | 0
75 | MICROPHONES
SUPPLYING, FIXING OF BEST QUALITY MICS AND ALL OTHER NECESSARY EQUIPMENTS TOA OR EQUIVALENT REFERENCE SERIES
A. | GOOSE-NECK MIC | 2 | No. |  | 0
B. | WIRELESS MICS | 4 | No. |  | 0
C. | TABLE MICS | 2 | No. |  | 0
D. | COLLAR MICS | 2 | No. |  | 0
SUBMITTALS, INSPECTIONS, OPERATION, DRAWINGS ETC.
76 | SUBMITTALS, SAMPLES, INSPECTIONS, ETC.
| SUBMITTALS, SAMPLES, INSPECTIONS, OPERATION AND MAINTENANCE MANUALS AND THE LIKE AS REQUIRED BY SPECIFICATION. | 1 | JOB |  | 0
77 | SHOP DRAWINGS & AS-BUILT DRAWINGS
| PREPARATION AND SUBMISSION OF HARD AND SOFT (.dwg) COPIES OF SHOP DRAWINGS & AS-BUILT DRAWINGS OF EACH JOB AT THE END OF THE EXECUTION. | 1 | JOB |  | 0
| TOTAL COST OF ELECTRICAL WORKS |  |  |  | 0

## Plumbing - Title
STATE LIFE INSURANCE CORPORATION BUILDING No. 9
BOQ 8th FLOOR PLUMBING WORK

## Plumbing BOQ
The BOQ document shall be read in conjunction with the Compliance sheet. The rates of all the items quoted should be done considering specifications and special conditions and including the following nature of the project its shape, angle, curve, bends, size etc. to be made at any depth and height with the use of all steel formwork properly supported as required and as directed by the Engineer/ Architect to the entire satisfaction of the Architect / Engineer/ Architect-in-Charge.
8th FLOOR - PLUMBING WORKS
S. No. | DESCRIPTION | QTY | UNIT | RATE (RS) | AMOUNT (RS)
1 | FREE STANDING WASH BASIN STALL
| PROVIDING AND FIXING GLAZED EARTHENWARE FREE STANDING WASH BASIN STALL COMPLETE WITH INCLUDING THE COST OF INTERNAL FITTING AND FLUSH PIPE WITH BEND AND MAKING REQUISITE NUMBER OF HOLES IN WALLS PLINTH AND FLOOR FOR PIPE CONNECTION AND MAKING GOOD IN CEMENT CONCRETE 1:2:4 (FOREIGN EQUIVALENT). THE CONTRACTOR IS TO ENSURE ALL FITTINGS AND PROPER FLUSHING IS PERFORMED ON-SITE AS PER SITE CONDITIONS. NOTE: FAUCET, BIB COCKS, AND ALL OTHER FITTINGS ARE TO BE INCLUDED IN THE COST OF ITEM CONTRACTOR MUST SUBMIT TECHNICAL SPECIFICATIONS AND SAMPLES BEFORE EXECUTION ALONG WITH SHOP DRAWINGS EXPRESSING ALL FIXTURES/ ROUTES TO BE USED AS PER SITE CONDITIONS. | 5 | No. | 52000 | 260000
2 | WESTERN W.C. (COMMODE)
| PROVIDING AND FIXING SQUATTING TYPE WHITE GLAZED EARTHEN WARE W.C. PAN WITH FRONT FLUSH INLET AND COMPLETE WITH INCLUDING THE COST OF FLUSHING CISTERN WITH INTERNAL FITTING AND FLUSH PIPE WITH BEND AND MAKING REQUISITE NUMBERATE ONLYF HOLES IN WALLS PLINTH AND FLOOR FOR PIPE CONNECTION AND MAKING GOOD IN CEMENT CONCRETE 1:2:4 (FOREIGN EQUIVALENT) WITH 4" DIA C.I. TRAP. CONTRACTOR TO ENSURE ALL FITTINGS AND PROPER FLUSHING IS PERFORMED END TO END UTILISING PERFECT SLOPE ON SITE AS PER SITE CONDITIONS. NOTE: CONTRACTOR MUST SUBMIT TECHNICAL SPECIFICATIONS AND SAMPLES PRIOR TO EXECUTION ALONG WITH SHOP DRAWINGS EXPRESSING ALL FIXTURES/ ROUTES TO BE USED AS PER SITE CONDITIONS. | 12 | No. | 105000 | 1260000
3 | EASTERN (SQUATTING) WATER CLOSET
| PROVIDING AND FIXING SQUATTING TYPE WHITE GLAZED EARTHEN WARE W.C. PAN WITH FRONT FLUSH INLET AND COMPLETE WITH INCLUDING THE COST OF FLUSHING CISTERN WITH INTERNAL FITTING AND FLUSH PIPE WITH BEND AND MAKING REQUISITE NUMBERATE ONLYF HOLES IN WALLS PLINTH AND FLOOR FOR PIPE CONNECTION AND MAKING GOOD IN CEMENT CONCRETE 1:2:4 (FOREIGN EQUIVALENT) WITH 4" DIA C.I. TRAP. CONTRACTOR TO ENSURE ALL FITTINGS AND PROPER FLUSHING IS PERFORMED END TO END UTILISING PERFECT SLOPE ON SITE AS PER SITE CONDITIONS. NOTE: CONTRACTOR MUST SUBMIT TECHNICAL SPECIFICATIONS AND SAMPLES PRIOR TO EXECUTION ALONG WITH SHOP DRAWINGS EXPRESSING ALL FIXTURES/ ROUTES TO BE USED AS PER SITE CONDITIONS. | 4 | No. | 38000 | 152000
4 | HAND SHOWERS (MUSLIM SHOWER)
| MASTER, SONEX OR EQUIVALENT TOILET HAND SPRAY WITH FLEXIBLE CHAIN & TELEPHONE TYPE SHOWER INCLUDING TEE STOP COCK ETC. COMPLETE IN ALL RESPECT. | 16 | No. | 7000 | 112000
5 | BASIN MIXER TAP
MASTER, SONEX OR EQUIVALENT WASH BASIN HOT AND COLD WATER MIXER, ETC.
A. | VANITY | 16 | No. | 9000 | 144000
B. | DOUBLE BIB COCK FOR TOILETS | 16 | No. | 4800 | 76800
6 | TOILET ACCESSORIES COMPLETE SET
A. | SOAP DISPENSER | 16 | No. | 9000 | 144000
B. | SOAP DISH
| PROVIDING AND FIXING SOAP-DISH OF MAKE "MASTER, VICTORIAN OR AN APPROVED EQUIVALENT". COMPLETE IN ALL RESPECT. | 16 | No. | 3000 | 48000
C | TOWEL ROD
| PROVIDING AND FIXING CHROMIUM PLATED TOWEL RAIL 24'' LONG AND 3/4'' DIA, OF MAKE "MASTER, VICTORIAN OR AN APPROVED EQUIVALENT". COMPLETE IN ALL RESPECT. | 16 | No. | 8500 | 136000
D. | PAPER HOLDER
| PROVIDING AND FIXING TOILET PAPER-HOLDER ONLY MAKE "MASTER, VICTORIAN OR AN APPROVED EQUIVALENT". COMPLETE IN ALL RESPECT. | 16 | No. | 3000 | 48000
E | COAT HOOKS | 16 | No. | 3000 | 48000
7 | LOOKING MIRROR
| LOOKING MIRROR 5mm BEST QUALITY BELGIUM OR EQUIVALENT MADE FIXED WITH CLIPS COMPLETE IN ALL RESPECT AND SIZE AS PER SITE REQUIREMENT | 150 | Sft | 1800 | 270000
8 | KITCHEN SINK
| PROVIDING AND FIXING STAINLESS STEEL KITCHEN SINK BOWL 24"x18" WITH DRY TRAY/ WASHING SURFACE OF 18 GAUGE MAKE MASTER OR EQUIVALENT FIXED IN COUNTER OVER PRE CAST SLAB, PASTING WITH JELLY/ SILICON WITH 15mm DIA C.P. BRASS T. STOP COCK OF MASTER, SONEX, 40mm DIA HEAVY DUTY WASTE COUPLING AND PVC FLEXIBLE WASTE PIPE OF APPROVED MAKE AND QUALITY COMPLETE IN ALL RESPECTS. AS PER THE MANUFACTURER'S REQUIREMENT. | 2 | No. | 50000 | 100000
9 | SECTION-02 WATER SUPPLY SYSTEM
SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF COMPLETE PIPE WORK FOR COLD AND HOT WATER SYSTEM INCLUDING ALL ACCESSORIES REQUIRED TO COMPLETE SYSTEMS READY TO OPERATE AS PER SPECIFICATION, DRAWINGS & INSTRUCTION OF CONSULTANT.
A. | POLYPROPYLENE RANDOM DADEX, AGM, STEELEX OR EQUIVALENT PP-R PIPES PN 20 AND FITTINGS WITH FUSION JOINTING ALONG WITH ALL TYPES OF UNIONS, TEES, BENDS, SOCKETS, CLAMPS HANGERS, SUPPORTS, SLEEVES, MASKING PLATES, CHISELLING, MAKING HOLES MAKING GOOD, EXCAVATION, BEDDING BACKFILLING AS REQUIRED COMPLETE IN ALL RESPECT.
i. | DIA. 1-1/2" | 60 | Rft | 450 | 27000
ii. | DIA. 2" | 70 | Rft | 980 | 68600
B. | PROVIDING & FIXING JOINING TESTING G.I. PIPE ILL MADE LINES FOR WATER SUPPLY AS PER BS 1387 MEDIUM QUALITY IIL. INCLUDING SPECIALS SOCKETS TEE, ELBOW, BEDN, REDUCER PLUG AND UNION ETC) SUPPORTED ON WALLS SUSPENDED FROM ROOF SLAB, INCLUDING PROTECTIVE COATING AS PER DRAWING AND SPECIFICATION INCLUDING COLOR CODING COMPLETE IN ALL RESPECT.
i. | DIA. 1-1/4" | 75 | Rft | 450 | 33750
ii. | DIA. 1-1/2" | 40 | Rft | 480 | 19200
iii. | DIA. 2" | 30 | Rft | 550 | 16500
iv. | DIA.3" | 20 | Rft | 900 | 18000
C | BRASS BODY GATE-VALVES / BALL-VALVES WITH UNIONS.
i. | SIZE 1-1/4" | 8 | No. | 8500 | 68000
ii. | SIZE 1-1/2" | 8 | No. | 11000 | 88000
iii. | SIZE 2" | 13 | No. | 19000 | 247000
iv. | SIZE 3" (CI BODY) | 3 | No. | 65000 | 195000
10 | DRAIN PLUMBING
PVC DADEX, AGM, STEELEX OR EQUIVALENT PVC PIPES UPTO 4 BAR AND FITTINGS WITH FUSION JOINTING ALONG WITH ALL TYPES OF UNIONS, TEES, BENDS, SOCKETS, CLAMPS HANGERS, SUPPORTS, SLEEVES, MASKING PLATES, CHISELLING, MAKING HOLES MAKING GOOD, EXCAVATION, BEDDING BACKFILLING AS REQUIRED COMPLETE IN ALL RESPECT. NOTE: THE JOB INCLUDES PLUGGING OF DRAIN INTO RISER DRAIN LINE.
A. | DIA 2" | 100 | RFT | 600 | 60000
B. | DIA 4" | 100 | RFT | 1100 | 110000
11 | CORE CUTTING
CORE CUTTING / DRILLING TO DRILL HOLES OF SPECIFIED SIZE IN R.C.C. WALLS OR SLABS WITH HILTE CORE CUTTING MACHINE TO FACILITATE INSTALLATION AND REPAIR OF UTILITY SYSTEMS AND EQUIPMENT. INCLUDING MARKING POSITION FOR DRILL BASE, USING RULER AND CHALK, COST OF DISPOSAL OF CONCRETE CORES, COMPLETE IN ALL RESPECTS AS DIRECTED BY THE ENGINEER.
A. | 4" DIA | 4 | No. | 2000 | 8000
B. | 6" DIA | 5 | No. | 3000 | 15000
C. | 8" DIA | 20 | No. | 5000 | 100000
12 | PLANTER DRAIN WITH DOME GRATING
PLANTER DRAIN WITH DOME-TYPE GRATING, GRAVELS, AND OUTLET PIPE.
A. | PD 4" DIA | 24 | No. | 28000 | 672000
SUBMITTALS, INSPECTIONS, OPERATION, DRAWINGS ETC.
13 | SUBMITTALS, SAMPLES, INSPECTIONS, ETC.
| SUBMITTALS, SAMPLES, INSPECTIONS, OPERATION AND MAINTENANCE MANUALS AND THE LIKE AS REQUIRED BY SPECIFICATION. | 1 | JOB | 20000 | 20000
14 | SHOP DRAWINGS & AS-BUILT DRAWINGS
| PREPARATION AND SUBMISSION OF HARD AND SOFT (.dwg) COPIES OF SHOP DRAWINGS & AS-BUILT DRAWINGS OF EACH JOB AT THE END OF THE EXECUTION. | 1 | JOB | 20000 | 20000
| TOTAL COST OF PLUMBING WORKS |  |  |  | 4584850

## HVAC - Title
STATE LIFE INSURANCE CORPORATION BUILDING No. 9
BOQ 8th FLOOR HVAC WORK

## HVAC BOQ
The BOQ document shall be read in conjunction with the Compliance sheet. The rates of all the items quoted should be done considering specifications and special conditions and including the following nature of the project its shape, angle, curve, bends, size etc. to be made at any depth and height with the use of all steel formwork properly supported as required and as directed by the Engineer/ Architect to the entire satisfaction of the Architect / Engineer/ Architect-in-Charge.
8th FLOOR - HVAC WORK
S. No. | DESCRIPTION | QTY | UNIT | RATE (RS) | AMOUNT (RS)
1 | VRF CASSETTES
P/F COMISSIONING INSTALLATION, TESTING OF VRF AC/DC INDOOR UNITS CASSETTE TYPE INCLUSIVE OF ALL ACCESSORIES, COPPER PIPING, Y SECTIONS, ALL COPPER ACCESSORIES AND HANGING ACCESSORIES TO BE A PART OF THIS ITEM, INSULATION BOUND IN A PVC CONDUIT FOR EACH CASSETTE. DRAIN RISER AND DRAIN PIPES SHALL BE INCLUSIVE OF THIS COST CONNECTED TO BUILDING SERVICE CORE AT THE END. COMPLETE ELECTRICAL SCOPE I.E. CONTROL WIRE, SENSING WIRE, PANEL WIRE, COMMUNICATION WIRE, POWER WIRE TO INTERNAL UNIT. INCLUSIVE OF TWO REMOTE CONTROL. FOR EACH CASSETTE INCLUSIVE OF ROOM PANEL AND IR REMOTE COST. ISOLATION VALVE FOR REFIREGERANT ON THE BEFORE THE CASSETE TO BE INCLUSIVE OF THE COST. COMPLETE INSTALLATION IN ALL ASPECTS. VRF DRAIN PIPE FROM VRF CASSETTE TO THE PERIPHERY OF THE BUILDING TO BE INCLUSIVE OF THE COST WHICH WILL BE CONNECTED TO DRAIN RISER VIA 3 " UPVC PIPE (3 INCHES PIPE IS A SEPARATE ITEM). WHEREVER THE VRF CASSETTE IS EXPOSED A DECO PAINTED MS BOX of 12SWG ON THE SIDE AS SLEEVE OF THE CASSETE WITH OPENABLE SECTIONS FOR MAINTAINANCE AS PER ARCHITECTS RECOMMENDATION AND COLOUR.
A. | 2 TON | 36 | No. | 100000 | 3600000
B. | 2.5 TON | 0 | No. | 100000 | 0
C. | 4 TON | 2 | No. | 100000 | 200000
2 | STRUCTURAL STEEL WORK
| PROVIDING, FABRICATING & FIXING OF MS TEE BARS, CHECKERED SHEETS (10 SWG) ANGLES 3" X 2" X 1/4" TH ETC FOR STRUCTURAL WORKS REQUIRED FOR FIXING OF HVAC OUTDOOR UNIT ON PLATFORM INCLUSIVE OF PLATFORM CONSTRUCTION AND ITS MOUNTING TO THE BUILDING STRUCTURAL COMPONENT. THE JOB SHALL INCLUDE ANY OR ALL REPAIRS AND NECESSARY ADJUSTMENTS AND OTHER NECESSARY WORKS. COMPLETE WITH WASHERS AND MOUNTING RUBBERIZED ABSORBERS TO PREVENT VIBRATIONS AND ITS EFFECT ON BUILDING. ALL STRUCTURAL WORKS TO BE EPOXY PAINTED TO DARK BLUE COLOR | 1200 | KG | 450 | 540000
3 | OUTDOOR UNIT
REMOVAL CLEANING, WRAPPING, REINSULATION AND REFIXING OF PLANUM BOXES ON NEW LOCATIONS INCLUDING WRAPPING OF INSULATION FABRIC AND PAINTING OF APPROVED COLOUR 2x 30 TON UNIT (FOR LARGE WING) 1x 20 TON UNIT ( FOR LARGE WING)
A. | VRF OUTDOOR UNIT PER TON COST WITH COPPER PIPING FROM OUTER TO INNER WITH ALTERNATE PIPES FOR EACH INDOOR CONNECTION; INTEGRATION AND COPPER PIPING MAIN AS PER EACH VRF OUTDOOR UNIT ALL VRF OUTDOOR UNITS TO HAVE ISOLATION VALVES FOR REFRIGERANT CAPTURE AND MAINTAINANCE. ALL OUTDOOR UNITS TO BE SYNCHROZIED WITH EACH OTHER FOR FAIL SAFE OPERATION USING COPPER PIPES AND RELEVANT ACCESSORIES: ENSURING SYNCHRONIZATION AMONGST EACH OTHER. ALL COPPER PIPING INCLUSIVE OF NETWORK COPPER PIPING VIA Y AND STRAIGHT SECTIONS OF APPROPRIATE SIZES AS PER VRF REQUIREMENTS TO BE INCLUSIVE OF THIS JOB HAVING PROPER INSULATION TO INDUSTRY STANDARD AS PER MANUFACTURER. INCLUSIVE OF REFRIGRANT COST AND ITS TOP UP COST WHEN SYSTEM IS RUN AS PER OEM. VRF OUTDOOR UNITS AND ITS CARDS TO BE VALIDATED AND MADE PROPER USING ALL WEATHER SILICON PROTECTION IN ADDITION TO THE OEM PROTECTION. THE CONTRACTOR SHALL PRODUCE SAMPLES OF ADDITIONAL PROTECTION OF CARDS ALONG WITH INSTALLATION OF PROTECTION DEVICES SUCH AS SURGE PROTECTIONS AND OTHERS AS REQUIRED FOR SMOOTH OPERATION | 80 | TON | 225000 | 18000000
4 | DISTRIBUTION BOARDS
SUPPLY AND INSTALLATION OF THE FOLLOWING DISTRIBUTION BOARDS OF MAKE HUSSAIN & CO., A TO Z, UNIVERSAL MADE WITH 14 SWG SHEET STEEL HOUSING WITH APPROVED COLOR AND HAVING SPECIFIED CIRCUIT BREAKERS USING TP MCCB, VOLTMETER, AMMETER, INDICATION LIGHTS, WITH K- ELECTRIC APPROVED ENERGY METERS AND ENERGY LOGGERS. AS SHOWN IN THE DRAWING. (REFER SINGLE LINE DIAGRAM). NOTE: SPECIFIED MULTIMETER SHOULD BE INCLUDED IN THE DBs
A. | FOR LARGE WING | 1 | No. | 350000 | 350000
5 | DRAIN PIPING (HVAC)
PVC DADEX, AGM, STEELEX OR EQUIVALENT PVC PIPES UPTO 4 BAR AND FITTINGS WITH FUSION JOINTING ALONG WITH ALL TYPES OF UNIONS, TEES, BENDS, SOCKETS, CLAMPS HANGERS, SUPPORTS, SLEEVES, MASKING PLATES, CHISELLING, MAKING HOLES MAKING GOOD, EXCAVATION, BEDDING BACKFILLING AS REQUIRED COMPLETE IN ALL RESPECT. NOTE: THE JOB INCLUDES PLUGGING OF DRAIN INTO RISER DRAIN LINE.
A. | DIA 3" | 700 | RFT | 850 | 595000
B. | DIA 1" | 400 | RFT | 460 | 184000
6 | COMMISSIONING OF HVAC SYSTEM
| COMPLETE DOCUMENTATION TESTING COMMISSIONING OF THE HVAC SYSTEM ALONG WITH A LEDGER FORMAT DOCUMENT FOR ALL THE COMPONENTS USED AND ACCESSORIES INSTALLED MARKING THE ROUTES AND OTHER NECESSARY ITEMS. INCLUSIVE OF ALL THE LICENSE | 1 | JOB | 250000 | 250000
7 | 2 YEARS WARRANTY ALONG WITH COMPLETE PREVENTIVE MAINTENANCE OF ALL COMPONENTS OF HVAC SYSTEM. | 1 | JOB | 500000 | 500000
8 | COMPLETE TRAINING OF LOCAL TECHNICIANS FOR OPERATION, MAINTENANCE OF HVAC SYSTEM | 1 | JOB | 25000 | 25000
9 | CORE CUTTING
CORE CUTTING / DRILLING TO DRILL HOLES OF SPECIFIED SIZE IN R.C.C. WALLS OR SLABS WITH HILTE CORE CUTTING MACHINE TO FACILITATE INSTALLATION AND REPAIR OF UTILITY SYSTEMS AND EQUIPMENT. INCLUDING MARKING POSITION FOR DRILL BASE, USING RULER AND CHALK, COST OF DISPOSAL OF CONCRETE CORES, COMPLETE IN ALL RESPECTS AS DIRECTED BY THE ENGINEER.
A. | 1.5" DIA | 20 | No. | 2000 | 40000
B. | 4" DIA | 5 | No. | 3000 | 15000
C. | 6" DIA | 1 | No. | 5000 | 5000
SUBMITTALS, INSPECTIONS, OPERATION, DRAWINGS ETC.
10 | SUBMITTALS, SAMPLES, INSPECTIONS, ETC.
| SUBMITTALS, SAMPLES, INSPECTIONS, OPERATION AND MAINTENANCE MANUALS AND THE LIKE AS REQUIRED BY SPECIFICATION. | 1 | JOB | 30000 | 30000
11 | SHOP DRAWINGS & AS-BUILT DRAWINGS
| PREPARATION AND SUBMISSION OF HARD AND SOFT (.dwg) COPIES OF SHOP DRAWINGS & AS-BUILT DRAWINGS OF EACH JOB AT THE END OF THE EXECUTION. | 1 | JOB | 15000 | 15000
TOTAL COST OF HVAC WORK |  |  |  |  | 24349000
*END OF BOQ*