## Summary
Bank Al-Falah Head Office Karachi
Overhauling, Repairing & Replacement |  |  |  | 2025-04-21
of Air Handling Units
SUMMARY OF BILL
S.No | Description | Material Amount | Labour Amount | Total Amount
1 | 2nd FLOOR A/B AHU UNIT | 639000 | 172000 | 811000
3 | 1ST FLOOR A/B AHU UNIT | 639000 | 172000 | 811000
2 | MEZZAINE A FLOOR AHU UNIT | 521500 | 146000 | 667500
4 | GROUND B FLOOR AHU UNIT | 521500 | 146000 | 667500
5 | 5th FLOOR CANTEEN UNIT
6 | 4th, Mezzanine B & Ground A UNIT | 272970 | 62300 | 335270
7 | 5TH FLOOR FRESH AIR UNIT | 0 | 0 | 0
8 | 5TH FLOOR ELEVATOR & BMS ROOM FAN COIL UNITS 04 NOS | 0 | 0 | 0
9 | PLANT ROOM (CHILLERS) | 5584000 | 301000 | 5885000
| Total Amount | 8177970 | 999300 | 9177270
| SST 15% |  | 149895 | 149895
| Grand Total Amount | 8177970 | 1149195 | 9327165
PIONEER SERVICES

## AHUs
BOQ OF OVERHAULING, REPAIRING AND REPLACEMENT WORKS OF AIR HANDLING UNITS (AHU) OF BA BUILDING KARACHI
BILL OF QUANTITIES | [7 empty] | RUNNING BILL NO 1
S.NO | DESCRIPTION | Qty | Unit | Material Rate | Labour Rate | Material Amount | Labour Amount | Work Done % | Material Amount | Labour Amount
2ND FLOOR A/B AHU UNIT
1 | Cutting / removal of MS Floor of air handling unit to remove existing isolator including supply and installation of new newpron isolator according air handler weight. | 1 | Job | 70000 | 20000 | 70000 | 20000 | 50% | 35000 | 10000
2 | Removal and dismantle of rusted MS channel frame foundation floor coloumns and othe r supports to be replaced with new MS channel frame foundation floor coloumns and paint 2 coat primer and 2 coat epoxy complete in all respenct. | 1 | job | 80000 | 40000 | 80000 | 40000 | 70% | 56000 | 28000
3 | Overhauling of Air handling units motor ball bearing replaced with new (Make SKF) including setting of motor frame / foundation repaired if required and fix belt guard properly including motor pully. | 1 | job | 120000 | 40000 | 120000 | 40000 | 70% | 84000 | 28000
4 | AHU blower repaire including balancing of blower and shaft polish and alignment, replace pillow block bearing 68mm with new (make SKF) including provide grease niple for lubrication. (And test with grease gun). - Blower dia 34" - Blower Lenght 24" - Housing Lenght 57" - Housing Height 63" - Housing Width 53" | 1 | job | 200000 | 50000 | 200000 | 50000 | 70% | 140000 | 35000
5 | Supply and installation of Water proof light for enternal area AHU of approx 40 watt. | 1 | job | 20000 | 3000 | 20000 | 3000 | 0% | 0 | 0
6 | AHU Chilled water coil channel frame around the coil clean with rust and dust and vanished with epoxy paint as required | 1 | job | 20000 | 20000 | 20000 | 20000 | 0% | 0 | 0
7 | Descaling of AHU chilled water coil complete in all respect | 1 | job | 30000 | 20000 | 30000 | 20000 | 0% | 0 | 0
8 | AHU Blower including louvor and blower housing paint with 2 coat primer & 2 coat epoxy complete in all respect. | 1 | job | 30000 | 20000 | 30000 | 20000 | 50% | 15000 | 10000
9 | Removal of existing insulation from inside the AHU including supply and installation of aluminum faced foam insulation complete in all respect. | 1 | job | 300000 | 40000 | 300000 | 40000 | 50% | 150000 | 20000
10 | Supply and installation of flexible duct connector in AHU room including replaced fiber glass insulation in AHU room including supply and installation of canvas cloth with anti fungus paint . | 1 | job | 70000 | 30000 | 70000 | 30000 | 30% | 21000 | 9000
11 | Cleaning / paint AHU from outer area with primer and finished with oil paint. (Berger / ICI) | 1 | job | 70000 | 30000 | 70000 | 30000 | 20% | 14000 | 6000
12 | Cleaning / descalling of chilled water line, Gate valve Globe valve, strainer motorized valve complete in all respect. | 1 | job | 20000 | 15000 | 20000 | 15000 | 0% | 0 | 0
13 | Removal of existing Gate valve including suppy and isntallation of Gate valve 4" dia (make GALA) with flanges, nut bolt gasket, insulation, fabric, anti fungus paint complete in all respect. | 2 | Nos | 75000 | 15000 | 150000 | 30000 | 40% | 60000 | 12000
14 | Chilled water supply / return line damaged insulation repleced with new including AHU room all chilled water line fix new canvas cloth and anti fungus paint complete in all respect. | 1 | job | 85000 | 30000 | 85000 | 30000 | 0% | 0 | 0
15 | Existing AHU V-belt replaced with new (Make: Continental or approved equal) according number and type. | 1 | Set | 23000 | 5000 | 23000 | 5000 | 0% | 0 | 0
16 | Supply & installation of aluminum filter including repair / replace of filter frame as required complete in all respect. | 1 | job | 80000 | 20000 | 80000 | 20000 | 30% | 24000 | 6000
17 | Door hinges & lock repaired / replaced with new if required | 1 | job | 10000 | 5000 | 10000 | 5000 | 0% | 0 | 0
18 | Exisitng condensate Drain pipe replaced with new UPVC SCH-40 1.5'' dia including U-trap and insulation complete in all respect. | 1 | job | 15000 | 5000 | 15000 | 5000 | 0% | 0 | 0
19 | Supply of SS Nut, Bolts, Washers, Screws & Rivits for completion of AHU overhauling work complete in all respect. | 1 | job | 30000 | 5000 | 30000 | 5000 | 80% | 24000 | 4000
20 | Providing and installation of flexible pipe connector with flange nut bolt gasket etc complete in all respect. for chilled water supply / return line of AHU | 2 | NOs | 20000 | 5000 | 40000 | 10000 | 40% | 16000 | 4000
Sub Total Amount Rs | [8 empty] | 639000 | 172000
1ST FLOOR A/B AHU UNIT
1 | Cutting / removal of MS Floor of air handling unit to remove existing isolator including supply and installation of new newpron isolator according air handler weight. | 1 | Job | 70000 | 20000 | 70000 | 20000 | 50% | 35000 | 10000
2 | Removal and dismantle of rusted MS channel frame foundation floor coloumns and othe r supports to be replaced with new MS channel frame foundation floor coloumns and paint 2 coat primer and 2 coat epoxy complete in all respenct. | 1 | job | 80000 | 40000 | 80000 | 40000 | 70% | 56000 | 28000
3 | Overhauling of Air handling units motor ball bearing replaced with new (Make SKF) including setting of motor frame / foundation repaired if required and fix belt guard properly including motor pully. | 1 | job | 120000 | 40000 | 120000 | 40000 | 70% | 84000 | 28000
4 | AHU blower repaire including balancing of blower and shaft polish and alignment, replace pillow block bearing 68mm with new (make SKF) including provide grease niple for lubrication. (And test with grease gun). - Blower dia 34" - Blower Lenght 24" - Housing Lenght 57" - Housing Height 63" - Housing Width 53" | 1 | job | 200000 | 50000 | 200000 | 50000 | 70% | 140000 | 35000
5 | Supply and installation of Water proof light for enternal area AHU of approx 40 watt. | 1 | job | 20000 | 3000 | 20000 | 3000 | 0% | 0 | 0
6 | AHU Chilled water coil channel frame around the coil clean with rust and dust and vanished with epoxy paint as required | 1 | job | 20000 | 20000 | 20000 | 20000 | 0% | 0 | 0
7 | Descaling of AHU chilled water coil complete in all respect | 1 | job | 30000 | 20000 | 30000 | 20000 | 0% | 0 | 0
8 | AHU Blower including louvor and blower housing paint with 2 coat primer & 2 coat epoxy complete in all respect. | 1 | job | 30000 | 20000 | 30000 | 20000 | 50% | 15000 | 10000
9 | Removal of existing insulation from inside the AHU including supply and installation of aluminum faced foam insulation complete in all respect. | 1 | job | 300000 | 40000 | 300000 | 40000 | 50% | 150000 | 20000
10 | Supply and installation of flexible duct connector in AHU room including replaced fiber glass insulation in AHU room including supply and installation of canvas cloth with anti fungus paint . | 1 | job | 70000 | 30000 | 70000 | 30000 | 30% | 21000 | 9000
11 | Cleaning / paint AHU from outer area with primer and finished with oil paint. (Berger / ICI) | 1 | job | 70000 | 30000 | 70000 | 30000 | 20% | 14000 | 6000
12 | Cleaning / descalling of chilled water line, Gate valve Globe valve, strainer motorized valve complete in all respect. | 1 | job | 20000 | 15000 | 20000 | 15000 | 0% | 0 | 0
13 | Removal of existing Gate valve including suppy and isntallation of Gate valve 4" dia (make GALA) with flanges, nut bolt gasket, insulation, fabric, anti fungus paint complete in all respect. | 2 | Nos | 75000 | 15000 | 150000 | 30000 | 40% | 60000 | 12000
14 | Chilled water supply / return line damaged insulation repleced with new including AHU room all chilled water line fix new canvas cloth and anti fungus paint complete in all respect. | 1 | job | 85000 | 30000 | 85000 | 30000 | 0% | 0 | 0
15 | Existing AHU V-belt replaced with new (Make: Continental or approved equal) according number and type. | 1 | Set | 23000 | 5000 | 23000 | 5000 | 0% | 0 | 0
16 | Supply & installation of aluminum filter including repair / replace of filter frame as required complete in all respect. | 1 | job | 80000 | 20000 | 80000 | 20000 | 30% | 24000 | 6000
17 | Door hinges & lock repaired / replaced with new if required | 1 | job | 10000 | 5000 | 10000 | 5000 | 0% | 0 | 0
18 | Exisitng condensate Drain pipe replaced with new UPVC SCH-40 1.5'' dia including U-trap and insulation complete in all respect. | 1 | job | 15000 | 5000 | 15000 | 5000 | 0% | 0 | 0
19 | Supply of SS Nut, Bolts, Washers, Screws & Rivits for completion of AHU overhauling work complete in all respect. | 1 | job | 30000 | 5000 | 30000 | 5000 | 80% | 24000 | 4000
20 | Providing and installation of flexible pipe connector with flange nut bolt gasket etc complete in all respect. for chilled water supply / return line of AHU | 2 | NOs | 20000 | 5000 | 40000 | 10000 | 40% | 16000 | 4000
Sub Total Amount Rs | [8 empty] | 639000 | 172000
MEZZAINE A FLOOR AHU UNIT
1 | Cutting / removal of MS Floor of air handling unit to remove existing isolator including supply and installation of new newpron isolator according air handler weight. | 1 | Job | 70000 | 25000 | 70000 | 25000 | 50% | 35000 | 12500
2 | Removal and dismantle of rusted MS channel frame foundation floor coloumns and othe r supports to be replaced with new MS channel frame foundation floor coloumns and paint 2 coat primer and 2 coat epoxy complete in all respenct. | 1 | job | 75000 | 30000 | 75000 | 30000 | 70% | 52500 | 21000
3 | Overhauling of Air handling units motor ball bearing replaced with new (Make SKF) including setting of motor frame / foundation repaired if required and fix belt guard properly including motor pully. | 1 | job | 90000 | 30000 | 90000 | 30000 | 70% | 63000 | 21000
4 | AHU blower repaire including balancing of blower and shaft polish and alignment, replace pillow block bearing 62mm with new (make SKF) including provide grease niple for lubrication. (And test with grease gun). - Blower dia 24" - Blower Lenght 22" - Housing Lenght 32" - Housing Height 37" - Housing Width 29" | 1 | job | 120000 | 40000 | 120000 | 40000 | 70% | 84000 | 28000
5 | Supply and installation of Water proof light for enternal area AHU of approx 40 watt. | 1 | job | 15000 | 3000 | 15000 | 3000 | 0% | 0 | 0
6 | AHU Chilled water coil channel frame around the coil clean with rust and dust and vanished with epoxy paint as required | 1 | job | 15000 | 15000 | 15000 | 15000 | 0% | 0 | 0
7 | Descaling of AHU chilled water coil complete in all respect | 1 | job | 20000 | 15000 | 20000 | 15000 | 0% | 0 | 0
8 | AHU Blower including louvor and blower housing paint with 2 coat primer & 2 coat epoxy complete in all respect. | 1 | job | 15000 | 15000 | 15000 | 15000 | 50% | 7500 | 7500
9 | Removal of existing insulation from inside the AHU including supply and installation of aluminum faced foam insulation complete in all respect. | 1 | job | 275000 | 30000 | 275000 | 30000 | 50% | 137500 | 15000
10 | Supply and installation of flexible duct connector in AHU room including replaced fiber glass insulation in AHU room including supply and installation of canvas cloth with anti fungus paint . | 1 | job | 70000 | 30000 | 70000 | 30000 | 30% | 21000 | 9000
11 | Cleaning / paint AHU from outer area with primer and finished with oil paint. (Berger / ICI) | 1 | job | 60000 | 30000 | 60000 | 30000 | 20% | 12000 | 6000
12 | Cleaning / descalling of chilled water line, Gate valve Globe valve, strainer motorized valve complete in all respect. | 1 | job | 20000 | 15000 | 20000 | 15000 | 0% | 0 | 0
13 | Removal of existing Gate valve including suppy and isntallation of Gate valve 4" dia (make GALA) with flanges, nut bolt gasket, insulation, fabric, anti fungus paint complete in all respect. | 2 | Nos | 70000 | 15000 | 140000 | 30000 | 40% | 56000 | 12000
14 | Chilled water supply / return line damaged insulation repleced with new including AHU room all chilled water line fix new canvas cloth and anti fungus paint complete in all respect. | 1 | job | 65000 | 30000 | 65000 | 30000 | 0% | 0 | 0
15 | Existing AHU V-belt replaced with new (Make: Continental or approved equal) according number and type. | 1 | Set | 15000 | 5000 | 15000 | 5000 | 0% | 0 | 0
16 | Supply & installation of aluminum filter including repair / replace of filter frame as required complete in all respect. | 1 | job | 70000 | 20000 | 70000 | 20000 | 30% | 21000 | 6000
17 | Door hinges & lock repaired / replaced with new if required | 1 | job | 10000 | 5000 | 10000 | 5000 | 0% | 0 | 0
18 | Exisitng condensate Drain pipe replaced with new UPVC SCH-40 1.5'' dia including U-trap and insulation complete in all respect. | 1 | job | 5000 | 5000 | 5000 | 5000 | 0% | 0 | 0
19 | Supply of SS Nut, Bolts, Washers, Screws & Rivits for completion of AHU overhauling work complete in all respect. | 1 | job | 25000 | 5000 | 25000 | 5000 | 80% | 20000 | 4000
20 | Providing and installation of flexible pipe connector with flange nut bolt gasket etc complete in all respect. for chilled water supply / return line of AHU | 2 | NOs | 15000 | 5000 | 30000 | 10000 | 40% | 12000 | 4000
Sub Total Amount Rs | [8 empty] | 521500 | 146000
GROUND B FLOOR AHU UNIT
1 | Cutting / removal of MS Floor of air handling unit to remove existing isolator including supply and installation of new newpron isolator according air handler weight. | 1 | Job | 70000 | 25000 | 70000 | 25000 | 50% | 35000 | 12500
2 | Removal and dismantle of rusted MS channel frame foundation floor coloumns and othe r supports to be replaced with new MS channel frame foundation floor coloumns and paint 2 coat primer and 2 coat epoxy complete in all respenct. | 1 | job | 75000 | 30000 | 75000 | 30000 | 70% | 52500 | 21000
3 | Overhauling of Air handling units motor ball bearing replaced with new (Make SKF) including setting of motor frame / foundation repaired if required and fix belt guard properly including motor pully. | 1 | job | 90000 | 30000 | 90000 | 30000 | 70% | 63000 | 21000
4 | AHU blower repaire including balancing of blower and shaft polish and alignment, replace pillow block bearing 62mm with new (make SKF) including provide grease niple for lubrication. (And test with grease gun). - Blower dia 24" - Blower Lenght 22" - Housing Lenght 32" - Housing Height 37" - Housing Width 29" | 1 | job | 120000 | 40000 | 120000 | 40000 | 70% | 84000 | 28000
5 | Supply and installation of Water proof light for enternal area AHU of approx 40 watt. | 1 | job | 15000 | 3000 | 15000 | 3000 | 0% | 0 | 0
6 | AHU Chilled water coil channel frame around the coil clean with rust and dust and vanished with epoxy paint as required | 1 | job | 15000 | 15000 | 15000 | 15000 | 0% | 0 | 0
7 | Descaling of AHU chilled water coil complete in all respect | 1 | job | 20000 | 15000 | 20000 | 15000 | 0% | 0 | 0
8 | AHU Blower including louvor and blower housing paint with 2 coat primer & 2 coat epoxy complete in all respect. | 1 | job | 15000 | 15000 | 15000 | 15000 | 50% | 7500 | 7500
9 | Removal of existing insulation from inside the AHU including supply and installation of aluminum faced foam insulation complete in all respect. | 1 | job | 275000 | 30000 | 275000 | 30000 | 50% | 137500 | 15000
10 | Supply and installation of flexible duct connector in AHU room including replaced fiber glass insulation in AHU room including supply and installation of canvas cloth with anti fungus paint . | 1 | job | 70000 | 30000 | 70000 | 30000 | 30% | 21000 | 9000
11 | Cleaning / paint AHU from outer area with primer and finished with oil paint. (Berger / ICI) | 1 | job | 60000 | 30000 | 60000 | 30000 | 20% | 12000 | 6000
12 | Cleaning / descalling of chilled water line, Gate valve Globe valve, strainer motorized valve complete in all respect. | 1 | job | 20000 | 15000 | 20000 | 15000 | 0% | 0 | 0
13 | Removal of existing Gate valve including suppy and isntallation of Gate valve 4" dia (make GALA) with flanges, nut bolt gasket, insulation, fabric, anti fungus paint complete in all respect. | 2 | Nos | 70000 | 15000 | 140000 | 30000 | 40% | 56000 | 12000
14 | Chilled water supply / return line damaged insulation repleced with new including AHU room all chilled water line fix new canvas cloth and anti fungus paint complete in all respect. | 1 | job | 65000 | 30000 | 65000 | 30000 | 0% | 0 | 0
15 | Existing AHU V-belt replaced with new (Make: Continental or approved equal) according number and type. | 1 | Set | 15000 | 5000 | 15000 | 5000 | 0% | 0 | 0
16 | Supply & installation of aluminum filter including repair / replace of filter frame as required complete in all respect. | 1 | job | 70000 | 20000 | 70000 | 20000 | 30% | 21000 | 6000
17 | Door hinges & lock repaired / replaced with new if required | 1 | job | 10000 | 5000 | 10000 | 5000 | 0% | 0 | 0
18 | Exisitng condensate Drain pipe replaced with new UPVC SCH-40 1.5'' dia including U-trap and insulation complete in all respect. | 1 | job | 5000 | 5000 | 5000 | 5000 | 0% | 0 | 0
19 | Supply of SS Nut, Bolts, Washers, Screws & Rivits for completion of AHU overhauling work complete in all respect. | 1 | job | 25000 | 5000 | 25000 | 5000 | 80% | 20000 | 4000
20 | Providing and installation of flexible pipe connector with flange nut bolt gasket etc complete in all respect. for chilled water supply / return line of AHU | 2 | NOs | 15000 | 5000 | 30000 | 10000 | 40% | 12000 | 4000
Sub Total Amount Rs | [8 empty] | 521500 | 146000
5th FLOOR CANTEEN UNIT
1 | Cutting / removal of MS Floor of air handling unit to remove existing isolator including supply and installation of new newpron isolator according air handler weight. | 1 | Job | 25000 | 10000 |  |  |  | 25000 | 10000
2 | Removal and dismantle of rusted MS channel frame foundation floor coloumns and othe r supports to be replaced with new MS channel frame foundation floor coloumns and paint 2 coat primer and 2 coat epoxy complete in all respenct. | 1 | job | 35000 | 15000 |  |  |  | 35000 | 15000
3 | Overhauling of Air handling units motor ball bearing replaced with new (Make SKF) including setting of motor frame / foundation repaired if required and fix belt guard properly including motor pully. | 1 | job | 40000 | 15000 |  |  |  | 40000 | 15000
4 | AHU blower repaire or replaced including balancing of blower and shaft polish and alignment, replace pillow block bearing 62mm with new (make SKF) including provide grease niple for lubrication. (And test with grease gun). - Blower dia 15" - Blower Lenght 18" - Housing Lenght 24" - Housing Height 22" - Housing Width 18" | 1 | job | 85000 | 25000 |  |  |  | 85000 | 25000
5 | Supply and installation of Water proof light for enternal area AHU of approx 40 watt. | 1 | job | 10000 | 3000 |  |  |  | 10000 | 3000
6 | AHU Chilled water coil channel frame around the coil clean with rust and dust and vanished with epoxy paint as required | 1 | job | 15000 | 15000 |  |  |  | 15000 | 15000
7 | Descaling of AHU chilled water coil complete in all respect | 1 | job | 60000 | 30000 |  |  |  | 60000 | 30000
8 | AHU Blower including louvor and blower housing paint with 2 coat primer & 2 coat epoxy complete in all respect. | 1 | job | 30000 | 20000 |  |  |  | 30000 | 20000
9 | Removal of existing insulation from inside the AHU including supply and installation of aluminum faced foam insulation complete in all respect. | 1 | job | 80000 | 25000 |  |  |  | 80000 | 25000
10 | Supply and installation of flexible duct connector in AHU room including replaced fiber glass insulation in AHU room including supply and installation of canvas cloth with anti fungus paint . | 1 | job | 20000 | 10000 |  |  |  | 20000 | 10000
11 | Cleaning / paint AHU from outer area with primer and finished with oil paint. (Berger / ICI) | 1 | job | 70000 | 30000 |  |  |  | 70000 | 30000
12 | Cleaning / descalling of chilled water line, Gate valve Globe valve, strainer motorized valve complete in all respect. | 1 | job | 20000 | 20000 |  |  |  | 20000 | 20000
13 | Removal of existing Gate valve including suppy and isntallation of Gate valve 4" dia (make GALA) with flanges, nut bolt gasket, insulation, fabric, anti fungus paint complete in all respect. | 2 | Nos | 75000 | 15000 |  |  |  | 150000 | 30000
14 | Chilled water supply / return line damaged insulation repleced with new including AHU room all chilled water line fix new canvas cloth and anti fungus paint complete in all respect. | 1 | job | 60000 | 25000 |  |  |  | 60000 | 25000
15 | Existing AHU V-belt replaced with new (Make: Continental or approved equal) according number and type. | 1 | Set | 10000 | 5000 |  |  |  | 10000 | 5000
16 | Supply & installation of aluminum filter including repair / replace of filter frame as required complete in all respect. | 1 | job | 72000 | 15000 |  |  |  | 72000 | 15000
17 | Door hinges & lock repaired / replaced with new if required | 1 | job | 10000 | 3000 |  |  |  | 10000 | 3000
18 | Exisitng condensate Drain pipe replaced with new UPVC SCH-40 1.5'' dia including U-trap and insulation complete in all respect. | 1 | job | 15000 | 5000 |  |  |  | 15000 | 5000
19 | Supply of SS Nut, Bolts, Washers, Screws & Rivits for completion of AHU overhauling work complete in all respect. | 1 | job | 45000 | 8000 |  |  |  | 45000 | 8000
20 | Providing and installation of flexible pipe connector with flange nut bolt gasket etc complete in all respect. for chilled water supply / return line of AHU | 2 | NOs | 20000 | 5000 |  |  |  | 40000 | 10000
21 | Dismantle, lifting and shifting of AHU in chiller plant room. | 1 | Job | 10000 | 70000 |  |  |  | 10000 | 70000
22 | Installation of AHUs. | 1 | Job | 10000 | 20000 |  |  |  | 10000 | 20000
23 | Providing and installation of G.I Sheet metal duct for supply and return air. | 1200 | SFT | 425 | 75 |  |  |  | 510000 | 90000
24 | Providing and installation of insulation 3/4" thick for supply and return air ducts. | 1200 | SFT | 450 | 50 |  |  |  | 540000 | 60000
25 | Providing and installation of motorized valve 02" Dia. | 1 | No | 180000 | 10000 |  |  |  | 180000 | 10000
26 | Providing and installation of air devices | 1600 | Sqin | 28 | 5 |  |  |  | 44800 | 8000
27 | Providing and installation of volume control dammper | 1600 | Sqin | 25 | 5 |  |  |  | 40000 | 8000
28 | Supply and installation of electrical panel. | 1 | No | 265000 | 20000 |  |  |  | 265000 | 20000
29 | Supply and installation of temperature controller stand alone. | 1 | Job | 60000 | 15000 |  |  |  | 60000 | 15000
30 | Supply and installation of hangers and supports. | 1 | Job | 30000 | 10000 |  |  |  | 30000 | 10000
31 | Testing and commissioing of the system. | 1 | Job |  | 25000 |  |  |  | 0 | 25000
Sub Total Amount Rs | [8 empty] | 2581800 | 655000
4th,Mezzanine B & Ground A UNIT
1 | 4th floor AHU Unit Gate valve 4''old valve removing and new valve installation make GALA with flenges EPS thermocol insulation, fabric, anti fungus paint. | 2 | Nos | 75000 | 10000 | 150000 | 20000 | 60% | 90000 | 12000
2 | Supply and installation of rubber bellow 4" Dia for chilled water inlet and outlet of AHU including flang nut bolt gasket etc complete in all respect. | 2 | Nos | 19500 | 5000 | 39000 | 10000 | 51% | 19890 | 5100
3 | Mezzanine B AHU Unit Gate valve 2.5'' old valve removing and new valve installation make GALA with flenges EPS thermocol insulation, fabric, anti fungus paint. | 2 | Nos | 45000 | 10000 | 90000 | 20000 | 50% | 45000 | 10000
4 | Supply and installation of rubber bellow 2.5" Dia for chilled water inlet and outlet of AHU including flang nut bolt gasket etc complete in all respect. | 2 | Nos | 12000 | 5000 | 24000 | 10000 | 95% | 22800 | 9500
5 | Ground A AHU Unit Gate valve 2.5''old valve removing and new valve installation make GALA with flenges EPS thermocol insulation,fabric,anti fungus paint. | 2 | Nos | 45000 | 10000 | 90000 | 20000 | 80% | 72000 | 16000
6 | Supply and installation of rubber bellow 2.5" Dia for chilled water inlet and outlet of AHU including flang nut bolt gasket etc complete in all respect. | 2 | Nos | 12000 | 5000 | 24000 | 10000 | 97% | 23280 | 9700
Sub Total Amount Rs | [8 empty] | 272970 | 62300
5TH FLOOR FRESH AIR UNIT
1 | Evaporator Coil descaling internal and external | 1 | Job | 30000 | 20000 | 30000 | 20000 | 0% | 0 | 0
2 | Globe valve,moterized valve & strainer descalling of chilled water line | 1 | job | 20000 | 20000 | 20000 | 20000 | 0% | 0 | 0
3 | Gate valve 2.5''old valve removing and new valve installation make GALA with flenges EPS thermocol insulation,fabric,anti fungus paint with almunium cladding . | 2 | Nos | 45000 | 10000 | 90000 | 20000 | 0% | 0 | 0
4 | Replacement of motor bearing, Make SKF & motor foundation & belt guard safety cover | 1 | job | 60000 | 20000 | 60000 | 20000 | 0% | 0 | 0
5 | AHU belt replacement make continental | 1 | job | 20000 | 5000 | 20000 | 5000 | 0% | 0 | 0
6 | Chilled water line supply & return aslo anti fungus paint & another paint with EPS thermocol insulation. | 1 | job | 30000 | 20000 | 30000 | 20000 | 0% | 0 | 0
7 | Drain pipe UPVC size 1.5'' | 1 | job | 15000 | 5000 | 15000 | 5000 | 0% | 0 | 0
8 | FAHU room oil base mate finish NIPPON paint. | 1 | job | 40000 | 30000 | 40000 | 30000 | 0% | 0 | 0
9 | Supply & installation of complete filter frame,bag filter & alluminium air filter | 1 | job | 130000 | 25000 | 130000 | 25000 | 0% | 0 | 0
10 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 40000 | 10000 | 40000 | 10000 | 0% | 0 | 0
Sub Total Amount Rs | [8 empty] | 0 | 0
5TH FLOOR ELEVATOR & BMS ROOM FAN COIL UNITS 04 NOS
1 | Evaporator Coil descaling internal and external with epoxy paint. | 1 | Job | 10000 | 10000 | 10000 | 10000 | 0% | 0 | 0
2 | supply & installation of alluminium air filter | 1 | job | 15000 | 5000 | 15000 | 5000 | 0% | 0 | 0
3 | Replacement of motor bearing, Make SKF | 1 | job | 15000 | 10000 | 15000 | 10000 | 0% | 0 | 0
4 | Chilled water line supply & return aslo anti fungus paint & another paint with EPS thermocol insulation. | 1 | job | 25000 | 10000 | 25000 | 10000 | 0% | 0 | 0
5 | BMS room oil base mate finish NIPPON paint. | 1 | job | 60000 | 30000 | 60000 | 30000 | 0% | 0 | 0
6 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | 30000 | 10000 | 30000 | 10000 | 0% | 0 | 0
Sub Total Amount Rs | [8 empty] | 0 | 0

## Plant Room
BOQ OF REPAIRING AND REPLACEMENT AND MAINTENANCE WORKS OF CHILLERS AND COOLING TOWERS OVERHAULING OF BA BUILDING KARACHI
BILL OF QUANTITIES | [7 empty] | RUNNING BILL NO 1
S.NO | DESCRIPTION | Qty | Unit | Material Rate | Labour Rate | Material Amount | Labour Amount | Work Done % | Material Amount | Labour Amount
PLANT ROOM (CHILLERS)
1 | Providing and installation of Strainer 08" dia for main Condenssor water with flange, nut bolt, gaskte etc complete in all respect Make GALA | 4 | Nos | 450000 | 10000 | 1800000 | 40000 | 95% | 1710000 | 38000
2 | Removal of existing 8" dia gate valve from secondary chilled water pump including supply / installation of 8" dia Gate valve with related fittings including new insulation and cladding Make GALA | 6 | Job | 265000 | 15000 | 1590000 | 90000 | 90% | 1431000 | 81000
3 | Removal of existing 6" dia gate valve from primary chilled water pump including supply / installation of 6" dia Gate valve with related fittings including new insulation and cladding Make GALA | 6 | Job | 180000 | 15000 | 1080000 | 90000 | 90% | 972000 | 81000
4 | Removal of existing 8" dia gate valve from secondary condenser water pump including supply / installation of 8" dia Gate valve with related fittings Make GALA | 6 | Job | 265000 | 15000 | 1590000 | 90000 | 90% | 1431000 | 81000
5 | Supply and installation of booster pump set 1 stand-by & 1 on duty (make: Calpeda / Lowara) including VFD (make ABB) for cooling tower and chilled water system with 2Hp motor, electrical panel and related material. | 1 | Set | 1750000 | 30000 | 1750000 | 30000 | 0% | 0 | 0
6 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | Job | 40000 | 20000 | 40000 | 20000 | 100% | 40000 | 20000
7 | Providing and installation of horizontal expansion tank 600 Ltr with related fittings such as valves, hangers supports etc complete in all respect. | 1 | No | 1350000 | 50000 | 1350000 | 50000 | 0% | 0 | 0
8 | Water cooled Chillers Conddenssor descaling with chemical and brushing complete in all respect. | 6 | Nos | 40000 | 10000 | 240000 | 60000 | 0% | 0 | 0
Sub Total Amount Rs | [8 empty] | 5584000 | 301000
[9 empty] | 0 | 0
ROOF TOP (COOLING TOWERS)
1 | Dismantle of cooling tower structure frame and other metal accessories removed & galvanized hot dipped and reinstalled accordingly. | 3 | Job
2 | Overhauling of cooling tower gear box / motor replaced existing ball bearing with new and provide grease nipple for lubricant complete in all respect. | 6 | Job
3 | Providing and installation of new Fan blade, New hub with alignment of gear box. | 6 | Job
4 | Upper hot water distribution basin with new showering box fiber material need & lower cool basin & fan stack frame & metal fan guard replaced with fiber coating 3 layer apply & fiber material minor repairing required. | 12 | Job
5 | Complete new fills (1150x3=3450) with new fills foundation fiber metarial & louvers required | 6 | Job
6 | 1ST FLOOR A/B AHU UNIT
7 | Hydroplast Butterfly valve 4" replaced with flange | 12 | Nos
8 | GROUND B FLOOR AHU UNIT | 3 | Nos
9 | 5th FLOOR CANTEEN UNIT | 9 | Nos
10 | Schneider Motorized Butterfly valve 8" Outlet side need to be change with flenges. | 3 | Nos
11 | Schneider Motorized Butterfly valve 6" Inlet side need to be change with flenges. | 3 | Nos
12 | Cooling tower foundation steel beams/ girders outside area walk way platform and complete m/s pipe with pipe foundation need to be bitumen paint with enimel paint required. NIPPON | 3000 | Sft.
13 | Electrical wires proper dress up upvc pipe fitting. | 1 | Job
14 | Nut Bolts, Washers, Screws & Rivits Need Stainless Steel required . | 1 | Job
15 | Cooling towers Pipeline header inlet & outlet 12'' Washing required. | 1 | Job
4 | Chilled water line supply & return also anti fungus paint & another paint with EPS thermocol insulation. | 1 | Job | [5 empty] | 0 | 0
5 | gate valve make hartsley 6" provide & installation. | 6 | Nos | [5 empty] | 0 | 0
6 | supply & installation of complete filter frame,bag filter & alluminium air filter for Fresh Air Unit | 1 | job | [5 empty] | 0 | 0
8 | Nut Bolts, Washers, Screws & Ribits Need Stainless Steel required . | 1 | job | [5 empty] | 0 | 0
Sub Total Amount Rs | [8 empty] | 0 | 0