## HVAC
Bill of Quantities
ACMV Works
SPAR SUPERMARKET | [8 empty] | Rev.00
DHA, Karachi | [8 empty] | Date: 12-08-2024
[5 empty] | MATERIAL |  | LABOUR |  | TOTAL
S. No. |  | DESCRIPTION | UNIT | QTY | RATE | AMOUNT | RATE | AMOUNT | AMOUNT
All works shall be completed, tested and commissioned as per drawings, specifications and as per instruction of Consultant
1 |  | Unloading, rigging, lifting, placement, installation, testing and commissioning of (OWNER SUPPLIED) VRF / VRV air conditioning units with multiple indoor evaporative units of different capacities with central controller complete in all respects, ready to operate including supply & installation of supports, brackets, flexible duct connector / connection, rubber isolators, flashing, power wiring from isolation box to unit (10' to 15' radius), control wiring termination etc, complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant.
| 1.1 | GF-FACU-01 (03 Indoors + 1 Outdoor Condensing Unit Consisted of Different Modules) | Set | 1 | 25200 | 25200 | 25200 | 25200 | 50400 | 4032 | 21168
| 1.2 | CU-01 (1-2) (07 Indoors + 1 Outdoor Condensing Unit Consisted of Different Modules) | Set | 1 | 25200 | 25200 | 25200 | 25200 | 50400 | 4032 | 21168
| 1.3 | CU-01 (2-2) (08 Indoors + 1 Outdoor Condensing Unit Consisted of Different Modules) | Set | 1 | 25200 | 25200 | 25200 | 25200 | 50400 | 4032 | 21168
| 1.4 | CU-02 (1-2) (08 Indoors + 1 Outdoor Condensing Unit Consisted of Different Modules) | Set | 1 | 25200 | 25200 | 25200 | 25200 | 50400 | 4032 | 21168
| 1.5 | CU-02 (2-2) (08 Indoors + 1 Outdoor Condensing Unit Consisted of Different Modules) | Set | 1 | 25200 | 25200 | 25200 | 25200 | 50400 | 4032 | 21168
| 1.6 | CU-03 (1-2) (13 Indoors + 1 Outdoor Condensing Unit Consisted of Different Modules) | Set | 1 | 25200 | 25200 | 25200 | 25200 | 50400 | 4032 | 21168
| 1.7 | CU-03 (2-2) (12 Indoors + 1 Outdoor Condensing Unit Consisted of Different Modules) | Set | 1 | 25200 | 25200 | 25200 | 25200 | 50400 | 4032 | 21168
2 |  | Unloading, installation, testing and commissioning of (OWNER SUPPLIED) single split units of different capacities including supply & installation of supports, brackets, rubber isolators, flashing, power wiring from isolation box to unit (10' to 15' radius), control wiring termination etc, complete in all respects ready to operate as per schedule, specification, drawings and as per instruction of consultant. |  |  |  |  | 0 |  |  | 0 | 0
| 2.1 | AC-01 | Nos. | 5 | 6720 | 33600 | 5040 | 25200 | 58800 | 806.4 | 4233.6
| 2.2 | FS-01 | Nos. | 4 | 6720 | 26880 | 5040 | 20160 | 47040 | 806.4 | 4233.6
3 |  | Supply & installation of refrigerant pipes for all units (liquid + gas) with 1/2" thick expended close cell rubber foam insulation, PVC tape wrapping including additional gas charging if required and installation of branch distributor (supplied with VRF / VRV units) complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. (VRF / VRV Units copper pipes sizes & quantities shall be vary according to the equipment brand / selection) |  |  |  |  | 0 |  |  | 0 | 0
| A | All hard pipes except 1/4" |  |  |  |  | 0 |  |  | 0 | 0
| 3.1 | 1/4" dia | Rft | 65 | 348.6 | 22659 | 126 | 8190 | 30849 | 20.16 | 105.84
| 3.2 | 3/8" dia | Rft | 1730 | 403.2 | 697536 | 126 | 217980 | 915516 | 20.16 | 105.84
| 3.3 | 1/2" dia | Rft | 670 | 882 | 590940 | 126 | 84420 | 675360 | 20.16 | 105.84
| 3.4 | 5/8" dia | Rft | 1565 | 1008 | 1577520 | 168 | 262920 | 1840440 | 26.88 | 141.12
| 3.5 | 3/4" dia | Rft | 605 | 1139.88 | 689627.4 | 168 | 101640 | 791267.4 | 26.88 | 141.12
| 3.6 | 7/8" dia | Rft | 205 | 1470 | 301350 | 168 | 34440 | 335790 | 26.88 | 141.12
| 3.7 | 1 1/8" dia (also for 1") | Rft | 945 | 1764 | 1666980 | 168 | 158760 | 1825740 | 26.88 | 141.12
| 3.8 | 1 3/8" dia (also for 1-1/4") | Rft | 215 | 2604 | 559860 | 168 | 36120 | 595980 | 26.88 | 141.12
| 3.9 | 1 5/8" dia (also for 1-1/2") | Rft | 85 | 4032 | 342720 | 168 | 14280 | 357000 | 26.88 | 141.12
| 3.1 | 2 1/8" dia (also for 1-3/4") | Rft | 5 | 7770 | 38850 | 210 | 1050 | 39900 | 33.6 | 176.4
| B | Soft pipes for wall mounted single split unit only |  |  | 0 |  | 0 |  |  | 0 | 0
| 3.11 | 1/4" dia | Rft | 250 | 378 | 94500 | 126 | 31500 | 126000 | 20.16 | 105.84
| 3.12 | 1/2" dia | Rft | 250 | 693 | 173250 | 126 | 31500 | 204750 | 20.16 | 105.84
4 |  | Supply & installation of control wiring in G.I. conduit for external / PVC conduit for internal area from outdoor unit to indoor unit including microprocessor & central controller wiring & fixing / installation of central controller supplied with units complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Lot | 1 | 504000 | 504000 | 210000 | 210000 | 714000 | 33600 | 176400
5 |  | Supply & installation of 18 SWG powder quoted G.I. sheet metal tray with cover for refrigerant pipes and control wiring exposed to weather area and for main hall internal area complete in all respects including hangers, supports brackets complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqft | 500 | 483 | 241500 | 84 | 42000 | 283500 | 13.44 | 70.56
6 |  | Supply & installation of uPVC make class D SCH-40 pipe for internal area with 3/8" thick expanded closed cell rubber foam insulation, PVC tape wrapping for condensate drain including support hangers, excavation, cutting, chiseling and making good complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. |  |  | 0 |  | 0 |  |  | 0 | 0
| 6.1 | 1" dia | Rft | 900 | 336 | 302400 | 50.4 | 45360 | 347760 | 8.064 | 42.336
| 6.2 | 1.25" dia | Rft | 450 | 378 | 170100 | 58.8 | 26460 | 196560 | 9.408 | 49.392
| 6.3 | 1.5" dia | Rft | 10 | 655.2 | 6552 | 67.2 | 672 | 7224 | 10.752 | 56.448
| 6.4 | 2" dia | Rft | 10 | 882 | 8820 | 84 | 840 | 9660 | 13.44 | 70.56
7 |  | Supply & installation of air curtains including, supports, electrical connection etc, complete in all respects ready to operate as per drawings, specification & as per instruction of consultant. |  |  | 0 |  | 0 |  |  | 0 | 0
| 7.1 | 5 Feet length | Nos. | 3 | 71400 | 214200 | 2520 | 7560 | 221760 | 403.2 | 2116.8
8 |  | Supply, installation, testing and commissioning of ventilation fans as per mentioned in schedule, including supply & installation of vibration isolator, flexible duct connection / connector, support & hangers, power wiring from isolation box to unit (10' to 15' radius) etc, complete in all respects ready to operate as per drawings, specification and as per instruction of consultant. |  |  | 0 |  | 0 |  |  | 0 | 0
| 8.1 | EAF-01 | No. | 1 | 43612.8 | 43612.8 | 1680 | 1680 | 45292.8 | 268.8 | 1411.2
| 8.2 | EAF-02 | No. | 1 | 50551.2 | 50551.2 | 4200 | 4200 | 54751.2 | 672 | 3528
| 8.3 | EAF-03 | No. | 1 | 231000 | 231000 | 5040 | 5040 | 236040 | 806.4 | 4233.6
| 8.4 | EAF-04 | No. | 1 | 315000 | 315000 | 6720 | 6720 | 321720 | 1075.2 | 5644.8
| 8.5 | SEF-01 | No. | 1 | 365400 | 365400 | 8400 | 8400 | 373800 | 1344 | 7056
| 8.6 | FAF-01 | No. | 1 | 407400 | 407400 | 8400 | 8400 | 415800 | 1344 | 7056
| 8.7 | FAF-02 | No. | 1 | 415800 | 415800 | 8400 | 8400 | 424200 | 1344 | 7056
9 |  | Supply, fabrication and installation of epoxy painted M.S sheet metal welded duct of (18 Gauge) for condensing units exhaust air, complete in all respects including all changes in direction, transformation, plenums chambers, connection pecs of hood round to square, supports & hangers etc. complete in all respects ready to operate as per drawings, specification, instruction and approval of consultant. | Sqft | 700 | 474.6 | 332220 | 105 | 73500 | 405720 | 16.8 | 88.2
10 |  | Supply, fabrication and installation of M.S sheet metal welded duct of 2.0 mm (16 Gauge) thickness for kitchen exhasut duct, complete in all respects including 300x150mm access doors at all changes in direction, transformation, plenums chambers, connection pecs of hood round to square, supports & hangers etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant.. | Sqft | 650 | 462 | 300300 | 84 | 54600 | 354900 | 13.44 | 70.56
11 |  | Supply, fabrication and installation of 2" thick rockwool (double layar) insulation of 50kg/m3 density with wire mesh reinforcement over M.S sheet metal ducts of kitchen exhaust air duct, complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Sqft | 700 | 92.4 | 64680 | 42 | 29400 | 94080 | 6.72 | 35.28
12 |  | Supply, fabrication and installation of 26 SWG gauge G.I. cladding for over rockwool insulation etc. complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Sqft | 700 | 294 | 205800 | 58.8 | 41160 | 246960 | 9.408 | 49.392
13 |  | Supply, fabrication and installation of machine made G.I sheet metal duct different sections supply, return, fresh & exhaust air including plenums, splitter dampers, guide vanes, flexible duct connector/connection, access door, transformation, plenums chambers, wooden frame, anchors supports & hangers complete in all respects ready to operate as per drawings, specification, instruction of consultant. | Sqft | 6200 | 348.6 | 2161320 | 50.4 | 312480 | 2473800 | 8.064 | 42.336
14 |  | Supply & installation of 3/4" thick 25kg/m3 density rubber foam (XLPE) adhesive insulation with aluminum foil for condition area fresh air ducts only, complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqft | 2250 | 357 | 803250 | 42 | 94500 | 897750 | 6.72 | 35.28
15 |  | Supply & installation of acoustical duct sound liner adhesive with aluminum facing 1/2" thick in supply air duct complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Sqft | Rate only | 462 |  | 42 |  |  | 6.72 | 35.28
16 |  | Supply & installation of aluminum fabricated powder coated exhaust & fresh Air louvers including wooden frame, rain protection sheet bird mesh etc complete in all respects ready to operate as per specification, drawings and as per instruction of consultant. | Sqin | 11500 | 21 | 241500 | 2.52 | 28980 | 270480 | 0.4032 | 2.1168
17 |  | Supply, installation of Aluminum fabricated, powder coated Grills, Diffusers and Registers for supply air, return air, exhaust air & fresh air of different sizes (Grade A ), wooden frame, supports and other accessories etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. |  |  | 0 |  | 0 |  |  | 0 | 0
| 17.1 | Registers / Diffuser with Damper | Sqin | 5400 | 23.52 | 127008 | 2.52 | 13608 | 140616 | 0.4032 | 2.1168
| 17.2 | Grills | Sqin | 3000 | 19.32 | 57960 | 2.52 | 7560 | 65520 | 0.4032 | 2.1168
| 17.3 | S.S Mesh with G.I Frame | Sqin | 15500 | 15.12 | 234360 | 1.68 | 26040 | 260400 | 0.2688 | 1.4112
| 17.4 | Exhaust Air Disc Valves 6" dia | Nos. | 3 | 2520 | 7560 | 588 | 1764 | 9324 | 94.08 | 493.92
18 |  | Supply & installation of 6" dia flexible duct including hangers, jubilee clamp complete in all respects as per specification, drawings & as per instruction of consultant. | Rft | 5 | 378 | 1890 | 126 | 630 | 2520 | 20.16 | 105.84
19 |  | Supply & installation of 6" dia butterfly damper for above flexible duct with gas kits, nut bolts, complete in all respects, ready to operate as per specification, drawings & as per instruction of consultant. | Nos. | 1 | 3360 | 3360 | 420 | 420 | 3780 | 67.2 | 352.8
20 |  | Supply & installation of Volume Control Damper in 16 SWG G.I sheet metal with gas kits, nut bolts, complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Sqin | 5900 | 21 | 123900 | 2.52 | 14868 | 138768 | 0.4032 | 2.1168
21 |  | Supply, fabrication & installation of pre-insulated Volume Control Damper, blades to be constructed with extruded aluminum in airfoil shape with thermal isolation gape & shall have seals, pvc / aluminum profiles duct connection at both end etc. complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Sqin | 1000 | 42 | 42000 | 4.2 | 4200 | 46200 | 0.672 | 3.528
22 |  | Supply and installation of fire damper with linkage & fuse complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant. | Sqin | 2000 | 25.2 | 50400 | 2.52 | 5040 | 55440 | 0.4032 | 2.1168
23 |  | Supply and installation of back draft damper in MS Sheet with gas kits, nut botls. complete in all respects ready to operate as per specification, drawings & as per instruction of Consultant. | Sqin | 2500 | 20.16 | 50400 | 2.52 | 6300 | 56700 | 0.4032 | 2.1168
24 |  | Supply, installation of motorized damper with gas kits, nut bolts, including pressure transmeter, controller & control wiring, complete in all respects, ready to operate as per specification, drawings & as per instruction of consultant. |  |  | 0 |  | 0 |  |  | 0 | 0
| 24.1 | 20" x 22" | No. | 1 | 71400 | 71400 | 4200 | 4200 | 75600 | 672 | 3528
| 24.2 | 50" x 10" | No. | 1 | 74760 | 74760 | 4200 | 4200 | 78960 | 672 | 3528
25 |  | Integration of smoke control system using I/O modules with the fire alarm control panel of building with fire resistant wiring & fixing accessories, complete in all respects, ready to operate as per drawings, specification and instruction of consultant. | Lot | 1 | 294000 | 294000 | 42000 | 42000 | 336000 | 6720 | 35280
26 |  | Painting & Identification work on supports, hangers, platform of condensing units etc complete in all respects with one coat of ICI make Red lead oxide primer & two coats of ICI make enamel paint complete in all respects ready to operate as per drawings, specification, instruction and approval of Consultant. | Lot | 1 | 50400 | 50400 | 8400 | 8400 | 58800 | 1344 | 7056
27 |  | Testing, balancing and commissioning of air side of the system (from independent agency) complete in all respects including air measurement & balancing, temp, pressure & electrical data of related equipment etc. complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job. | 1 | 0 | 0 | 105000 | 105000 | 105000 | 16800 | 88200
28 |  | Making of Shop drawings on Auto CAD (latest version) with section details, equipment foundation details and Making of As Built drawings, Documentation Technical / Operational Manual & LOG Book for each equipment complete in all respects ready to operate as per specification, drawings and as per instruction of Consultant. | Job. | 1 | 12600 | 12600 | 12600 | 12600 | 25200 | 2016 | 10584
|  | Total Cost of Works with I. Tax Rs. |  |  |  | 15580076.4 |  | 2471742 | 18051818.4 | 2888290.944 |  | SPAR SUPERMARKET
[10 empty] | 15163527.456 | HVAC | HVAC | 18051818.4
Note: | [7 empty] | After deletion of fire scope, HVAC amount will be revised |  |  |  | FIRE Option -1 | 14944500
1) | MS Platform for placement of outdoor units not included in this BOQ, it will be provided by client / structural contractor. | [10 empty] | FIRE Option -2 | 12524700
2) | The refrigerant pipes sized + quantity provided for reference only. The contractor / supplier shall calculate the refrigerant pipes, sized & length as per the drawing provided and shall submitted refrigerant piping layout to consultant for approval. | [10 empty] | Plumbing | 4050500
3) | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
4) | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
5) | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## BOQ Option-01
Bill of Quantities (Option-01)
Fire Suppression Services
Spar Supermarket | [8 empty] | Rev.00
DHA, Karachi. | [8 empty] | Date: 12-08-2024
S.No. |  | Description | Unit | Qty | Material |  | Labour |  | Total
[5 empty] | Rate | Amount | Rate | Amount | Amount Rs.
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression services including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1 |  | Fire hose cabinet double height 32" x 60" x 14", stainless steel front, powder coated back including 1" dia x 100 Rft. rubber hose reel, nozzle guide, lock shield valve, automatic 180 deg. swing type, with 2-1/2" dia size landing valve, 2-fire extinguishers as shown on drawing.
| i. | Type FHC-LV | Nos. | 4 | 315000 | 1260000 | 7500 | 30000 | 1290000
2 |  | Fire hose cabinet size 42" x 36" x 12" for spare hose pipes including 4 Nos. 2-1/2" x 100 Rft. synthetic hose pipe, jet/spray/fog nozzle with aluminum instantaneous coupling, 2-Nos. fire blanket 6'-0" X 6'-0", fireman's axe, 2-pairs of fire proof gloves, front breakable glass, lock and all other accessories as specified, complete in all respects as per drawings, specified.
| i. | Type FHC-S | No. | 1 | 550000 | 550000 | 7500 | 7500 | 557500
3 |  | MS Sch-40 seamless pipes including all specials fittings UL listed FM approved, threaded, welded joints, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, supports and hangers, sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
| i. | Dia 1" (Threaded fitting) | Rft. | 1100 | 550 | 605000 | 180 | 198000 | 803000
| ii. | Dia 1-1/4" (Threaded fitting) | Rft. | 440 | 700 | 308000 | 200 | 88000 | 396000
| iii. | Dia 1-1/2" (Threaded fitting) | Rft. | 280 | 850 | 238000 | 225 | 63000 | 301000
| iv. | Dia 2" (Threaded fitting) | Rft. | 120 | 950 | 114000 | 250 | 30000 | 144000
| v. | Dia 2-1/2" (Welded joints fitting) | Rft. | 130 | 1600 | 208000 | 300 | 39000 | 247000
| vi. | Dia 3" (Welded joints fitting) | Rft. | 190 | 1950 | 370500 | 350 | 66500 | 437000
| vii. | Dia 4" (Welded joints fitting) | Rft. | 140 | 2800 | 392000 | 400 | 56000 | 448000
4 |  | Sprinkler Heads
| i. | Sprinkler Upright Type Standard Response K = 5.6 (Opening Temperature 68ºC) | Nos. | 198 | 2200 | 435600 | 600 | 118800 | 554400
| ii. | Dry Sprinkler Side Wall Type Quick Response K = 5.6 (Opening Temperature 57ºC) | No. | 1 | 7500 | 7500 | 1000 | 1000 | 8500
5 |  | Fire extinguishers with fixing accessories.
| i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 8 | 25250 | 202000 | 750 | 6000 | 208000
| ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 8 | 14250 | 114000 | 750 | 6000 | 120000
| iii. | Automatic fire extinguisher (10 Kg. Dry Chemical Powder) | Nos. | 3 | 29900 | 89700 | 1000 | 3000 | 92700
6 |  | Zone Control Valve assembly 4" dia UL Listed/FM Approved complete with following.
| i. | OS & Y Gate valve 4" size with tamper switch
| ii. | Check valve 4" size | No. | 1 | 635000 | 635000 | 10000 | 10000 | 645000
| iii. | Pressure Gauge
| iv. | Water flow switch 4" dia
| v. | 2" dia test valve with sight glass & sectional drain valve.
7 |  | Alarm Check valve assembly with alarm gong and pipe work. with retarding chamber.
| i. | Size. 6" | No. | 1 | 492000 | 492000 | 10000 | 10000 | 502000
8 |  | Pressure relief valve size 3" dia | No. | 1 | 464400 | 464400 | 10000 | 10000 | 474400
9 |  | Automatic air relief valve, 1" connection | No. | 1 | 12000 | 12000 | 1000 | 1000 | 13000
10 |  | Float Switch for low water level cut off. | No. | 1 | 45000 | 45000 | 5000 | 5000 | 50000
11 |  | Anti vortex suction plates for 6" dia. suction pipe | No. | 1 | 115000 | 115000 | 15000 | 15000 | 130000
12 |  | Flow meter 6" dia. | No. | 1 | 400000 | 400000 | 10000 | 10000 | 410000
13 |  | OS & Y Gate valve matching flanges with tamper switch.
| i. | Size. 6" | Nos. | 4 | 175000 | 700000 | 7000 | 28000 | 728000
14 |  | Throttling type butterfly valve with matching flanges.
| i. | Size. 6" | Nos. | 2 | 41500 | 83000 | 7000 | 14000 | 97000
15 |  | C.I body check valve with matching flanges.
| i. | Size. 6" | Nos. | 2 | 112000 | 224000 | 7000 | 14000 | 238000
16 |  | Fire Pumps Set 500 gpm @ 7 bar comprising of 1 No. multistage in line Jockey Pump + 1 No. main horizontal pump with electrical motor + 1 No. Standby horizontal pump with diesel engine, diesel storage tank including pump controllers mounted on common MS skid, inter connecting pipes, wiring, OS&Y valve, check valves and all accessories as per requirement of NFPA 20, drawings and engineer instruction. | Set. | 1 | 4450000 | 4450000 | 150000 | 150000 | 4600000
17 |  | Supervisory Fire Control Panel for sensing and monitoring of flow and monitoring OS&Y valves switching with true alarm including batteries and charger. | Job. | 1 | 465000 | 465000 | 35000 | 35000 | 500000
18 |  | MS insulated 6" dia Diesel Engine Flue pipe with 2" Rockwool insulation up to outside the building as per Consultant's approval. | Job. | 1 | 180000 | 180000 | 20000 | 20000 | 200000
19 |  | Allied electrical work including power cables to pumps motors, control cables and wires from sensing, monitoring and indicating devices such as valves and flow switches and switches to Electrical Control Panel and Fire Control Panel and supervisory switch including GI/PVC conduits and tray, termination, luxes and all accessories complete in all respects. Note: Contractor shall perform allied electrical works within the pump room. Power to the pump room shall be provided by the client. | Job. | 1 | 175000 | 175000 | 35000 | 35000 | 210000
20 |  | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1 | 60000 | 60000 | 20000 | 20000 | 80000
21 |  | Making of As-Built & Shop Drawings on AutoCAD 2018 or latest version with sectional details complete in all respects as per instructions of consultant. | Job. | 1 | 15000 | 15000 | 15000 | 15000 | 30000
22 |  | Painting, identification and tagging to the installations and equipments. | Job. | 1 | 150000 | 150000 | 50000 | 50000 | 200000
23 |  | Flushing of entire fire pipe work according to (NFPA-13). | Job. | 1 | 40000 | 40000 | 40000 | 40000 | 80000
24 |  | Testing, and commissioning of entire fire fighting installation as per Consultant's approval. | Job. | 1 |  | 0 | 150000 | 150000 | 150000
|  | Total Cost of Fire Suppression Services Rs. |  |  |  | 13599700 |  | 1344800 | 14944500
Note:
> | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## BOQ Option-02
Bill of Quantities (Option-02)
Fire Suppression Services
Spar Supermarket | [8 empty] | Rev.00
DHA, Karachi. | [8 empty] | Date: 12-08-2024
S.No. |  | Description | Unit | Qty | Material |  | Labour |  | Total
[5 empty] | Rate | Amount | Rate | Amount | Amount Rs.
FIRE FIGHTING SERVICES
Supply, installation, testing & commissioning of fire suppression system including all equipment, pipe works and accessories ready to operate as per specifications, drawings and instructions of consultants.
1 |  | Fire hose cabinet double height 32" x 60" x 14", stainless steel front, powder coated back including 1" dia x 100 Rft. rubber hose reel, nozzle guide, lock shield valve, automatic 180 deg. swing type, with 2-1/2" dia size landing valve, 2-fire extinguishers as shown on drawing.
| i. | Type FHC-LV | Nos. | 4 | 375000 | 1500000 | 7500 | 30000 | 1530000
2 |  | Fire hose cabinet size 42" x 36" x 12" for spare hose pipes including 4 Nos. 2-1/2" x 100 Rft. synthetic hose pipe, jet/spray/fog nozzle with aluminum instantaneous coupling, 2-Nos. fire blanket 6'-0" X 6'-0", fireman's axe, 2-pairs of fire proof gloves, front breakable glass, lock and all other accessories as specified, complete in all respects as per drawings, specified.
| i. | Type FHC-S | No. | 1 | 615000 | 615000 | 7500 | 7500 | 622500
3 |  | MS Sch-40 seamless pipes including all specials fittings UL listed FM approved, threaded, welded joints, flexible pipe, flanges, coupling, masking plates, bends, tees, clamps, supports and hangers, sleeves, masking plates chiseling, cutting holes, making good where required, painting and protection treatment etc. Complete in all respects.
| i. | Dia 1" (Threaded fitting) | Rft. | 250 | 550 | 137500 | 200 | 50000 | 187500
| ii. | Dia 1-1/4" (Threaded fitting) | Rft. | 100 | 700 | 70000 | 225 | 22500 | 92500
| iii. | Dia 1-1/2" (Threaded fitting) | Rft. | 40 | 850 | 34000 | 250 | 10000 | 44000
| iv. | Dia 2" (Threaded fitting) | Rft. | 40 | 950 | 38000 | 300 | 12000 | 50000
| v. | Dia 2-1/2" (Welded joints fitting) | Rft. | 70 | 1600 | 112000 | 400 | 28000 | 140000
| vi. | Dia 3" (Welded joints fitting) | Rft. | 30 | 1950 | 58500 | 500 | 15000 | 73500
| vii. | Dia 4" (Welded joints fitting) | Rft. | 10 | 2800 | 28000 | 750 | 7500 | 35500
4 |  | Sprinkler Heads
| i. | Sprinkler Upright Type Standard Response K = 5.6 (Opening Temperature 57ºC) | Nos. | 34 | 2150 | 73100 | 500 | 17000 | 90100
| ii. | Dry Sprinkler Side Wall Type Quick Response K = 5.6 (Opening Temperature 57ºC) | No. | 1 | 7500 | 7500 | 1000 | 1000 | 8500
5 |  | Fire extinguishers with fixing accessories.
| i. | Type Class B&C FX-3 (5 Kg. CO2 Carbon Dioxide Gas) | Nos. | 8 | 25250 | 202000 | 750 | 6000 | 208000
| ii. | Type Class A,B&C FX-4 (6 Kg. Dry Chemical Powder) | Nos. | 8 | 14250 | 114000 | 750 | 6000 | 120000
| iii. | Automatic fire extinguisher (6 Kg. Dry Chemical Powder) | Nos.
| v. | Automatic fire extinguisher (10 Kg. Dry Chemical Powder) | Nos. | 3 | 29900 | 89700 | 1000 | 3000 | 92700
6 |  | Zone Control Valve assembly 3" dia UL Listed/FM Approved complete with following.
| i. | OS & Y Gate valve 3" size with tamper switch
| ii. | Check valve 3" size
| iii. | Pressure Gauge | No. | 1 | 619000 | 619000 | 8000 | 8000 | 627000
| iv. | Water flow switch 3" dia
| v. | 1-1/2" dia test valve with sight glass & sectional drain valve.
7 |  | Alarm Check valve assembly with alarm gong and pipe work. with retarding chamber.
| i. | Size. 6" | No. | 1 | 492000 | 492000 | 10000 | 10000 | 502000
8 |  | Pressure relief valve size 3" dia | No. | 1 | 467400 | 467400 | 10000 | 10000 | 477400
9 |  | Automatic air relief valve, 1" connection | No. | 1 | 39500 | 39500 | 1000 | 1000 | 40500
10 |  | Float Switch for low water level cut off. | No. | 1 | 45000 | 45000 | 5000 | 5000 | 50000
11 |  | Anti vortex suction plates for 6" dia. suction pipe | No. | 1 | 115000 | 115000 | 10000 | 10000 | 125000
12 |  | Flow meter 6" dia. | No. | 1 | 400000 | 400000 | 10000 | 10000 | 410000
13 |  | OS & Y Gate valve matching flanges with tamper switch.
| i. | Size. 6" | Nos. | 4 | 211000 | 844000 | 5000 | 20000 | 864000
14 |  | Throttling type butterfly valve with matching flanges.
| i. | Size. 6" | Nos. | 2 | 41500 | 83000 | 5000 | 10000 | 93000
15 |  | C.I body check valve with matching flanges.
| i. | Size. 6" | Nos. | 2 | 93000 | 186000 | 5000 | 10000 | 196000
16 |  | Fire Pumps Set 500 gpm @ 7 bar comprising of 1 No. multistage in line Jockey Pump + 1 No. main horizontal pump with electrical motor + 1 No. Standby horizontal pump with diesel engine, diesel storage tank including pump controllers mounted on common MS skid, inter connecting pipes, wiring, OS&Y valve, check valves and all accessories as per requirement of NFPA 20, drawings and engineer instruction. | Set. | 1 | 4450000 | 4450000 | 150000 | 150000 | 4600000
17 |  | Supervisory Fire Control Panel for sensing and monitoring of flow and monitoring OS&Y valves switching with true alarm including batteries and charger. | Job. | 1 | 465000 | 465000 | 35000 | 35000 | 500000
18 |  | MS insulated 6" dia Diesel Engine Flue pipe with 2" Rockwool insulation up to outside the building as per Consultant's approval. | Job. | 1 | 180000 | 180000 | 20000 | 20000 | 200000
19 |  | Allied electrical work including power cables to pumps motors, control cables and wires from sensing, monitoring and indicating devices such as valves and flow switches and switches to Electrical Control Panel and Fire Control Panel and supervisory switch including GI/PVC conduits and tray, termination, luxes and all accessories complete in all respects. Note: Contractor shall perform allied electrical works within the pump room. Power to the pump room shall be provided by the client. | Job. | 1 | 175000 | 175000 | 35000 | 35000 | 210000
20 |  | Supply & installation of fire stop material (for passive fire fighting / smoke barrier) in all MEP openings and penetrations, either in slab or wall, complete in all respects, ready to operate as per fire stopper recommended material, and as per instruction of Consultant. | Job. | 1 | 60000 | 60000 | 20000 | 20000 | 80000
21 |  | Making of As-Built & Shop Drawings on AutoCAD 2018 or latest version with sectional details complete in all respects as per instructions of consultant. | Job. | 1 | 15000 | 15000 | 15000 | 15000 | 30000
22 |  | Painting, identification and tagging to the installations and equipments. | Job. | 1 | 40000 | 40000 | 35000 | 35000 | 75000
23 |  | Flushing of entire fire pipe work according to (NFPA-13). | Job. | 1 | 20000 | 20000 | 30000 | 30000 | 50000
24 |  | Testing, and commissioning of entire fire fighting installation as per Consultant's approval. | Job. | 1 |  | 0 | 100000 | 100000 | 100000
|  | Total Cost of Fire Suppression Services Rs. |  |  |  | 11775200 |  | 749500 | 12524700
Note:
> | Above quantities based on tender drawing, material should be procured as per approved shop drawing & as per site requirement.
> | Contractor is instructed to visit the site, understand the nature of work & then fill the rates accordingly and submit the quotation. No argument and discussion will be entertained after awarding of work.
> | Miscellaneous work which was not included in BOQ but necessary to complete the project in all respects and ready to operate as per instructions of Consultant. (Bidder should mentioned the type of works).

## Bill of Quantities
Bill of Quantities
Plumbing & Sanitary Services
Spar Supermarket
DHA, Karachi.
S.No. |  | Description | Unit | Qty | Material |  | Labour |  | Total
[5 empty] | Rate | Amount | Rate | Amount | Amount Rs.
SECTION - 01, PLUMBING FIXTURES.
Supply and Installation of plumbing fixtures & faucets complete in all respects including all accessories, support, hangers, etc. ready to use as per specifications, drawings and instructions of Consultant.
1.1 |  | European style coupled water closet floor mounted with seat cover, flush tank C.P. (chrome plated) connector, thimble, etc.
| i. | Type - EWC | Nos. | 2 | 42000 | 84000 | 10000 | 20000 | 104000
1.2 |  | Toilet Hand Spray with flexible chain & telephone type shower Including tee stop cock etc. complete in all respect.
| i. | Type - TS (for EWC) | Nos. | 2 | 14500 | 29000 | 2000 | 4000 | 33000
1.3 |  | Wash basin (WB) including bottle trap, waste, stop cocks, etc.
| i. | Type - WB (Vanity) | Nos. | 2 | 32000 | 64000 | 8000 | 16000 | 80000
1.4 |  | Wash basin hot and cold water mixer, etc.
| i. | Type - WB (Vanity) | Nos. | 2 | 27000 | 54000 | 7000 | 14000 | 68000
1.5 |  | Stainless steel kitchen sink including stop cocks, P-trap / Bottle trap, waste pipe etc complete in all respects.
| i. | SK - 1, 34" x 20" single bowl and single drainer. | Nos. | 3 | 49500 | 148500 | 7500 | 22500 | 171000
1.6 |  | Sink hot and cold water mixer, etc.
| i. | SK - 1 | Nos. | 3 | 37250 | 111750 | 1000 | 3000 | 114750
1.7 |  | S.S Grease Trap 7.5 Kg. capacity, inlet/outlet 2" dia connections. | Nos. | 3 | 175000 | 525000 | 10000 | 30000 | 555000
1.8 |  | Macerating pump for Grease Trap valves & accessories complete in all respects. | No. | 1 | 215000 | 215000 | 20000 | 20000 | 235000
1.9 |  | Toilet accessories complete set.
| i. | Soap Dispenser | Nos. | 2 | 5000 | 10000 | 1000 | 2000 | 12000
| ii. | Towel Rail | Nos. | 2 | 7500 | 15000 | 1000 | 2000 | 17000
| iii. | Paper Holder | Nos. | 2 | 8500 | 17000 | 1000 | 2000 | 19000
| iv. | Coat Hooks | Nos. | 4 | 3500 | 14000 | 1000 | 4000 | 18000
| v. | Automatic Hand Dryer | Nos. | 2 | 27500 | 55000 | 3000 | 6000 | 61000
|  | Sub Total Rs. |  |  |  | 1342250 |  | 145500 | 1487750
SECTION-02 WATER SUPPLY SYSTEM
Supply, installation, testing and commissioning of complete pipe work for cold and hot water system including all accessories required to complete systems ready to operate as per specification, drawings & instruction of Consultant.
2.1 |  | Polypropylene Random PP-R pipes PN 20 and fittings with fusion jointing along with all types of unions, tees, bends, sockets, clamps, hangers, supports, sleeves, masking plates, chiseling, making holes making good, excavation, bedding backfilling as required complete in all respect.
| i. | Dia. OD 25 mm | Rft. | 260 | 350 | 91000 | 100 | 26000 | 117000
| ii. | Dia. OD 32 mm | Rft. | 100 | 515 | 51500 | 100 | 10000 | 61500
| iii. | Dia. OD 40 mm | Rft. | 30 | 750 | 22500 | 125 | 3750 | 26250
2.2 |  | Brass body gate valves / ball valves with unions.
| i. | Size 3/4" | Nos. | 5 | 5500 | 27500 | 1000 | 5000 | 32500
| ii. | Size 1-1/4" | No. | 1 | 9000 | 9000 | 1000 | 1000 | 10000
|  | Sub Total Rs. |  |  |  | 201500 |  | 45750 | 247250
SECTION-03 SOIL, WASTE VENT AND RAIN WATER DRAINAGE SYSTEM
Supply, fixing, testing and commissioning of equipment, pipe work required to complete the soil, waste, vent and rain water systems in all respects with accessories ready to operate as per specifications, drawings and instructions of Consultant.
3.1 |  | uPVC pipes of approved make along with specials, fittings, bends, wye, tees, sockets, flexible connectors, sleeves, masking plates, chiseling, making hole, excavation, backfilling making good where as required jointing solvent.
| i. | Dia. 1-1/2" | Rft. | 20 | 400 | 8000 | 100 | 2000 | 10000
| ii. | Dia. 2" | Rft. | 160 | 650 | 104000 | 150 | 24000 | 128000
| iii. | Dia. 3" | Rft. | 120 | 1450 | 174000 | 200 | 24000 | 198000
| iv. | Dia. 4" | Rft. | 30 | 1800 | 54000 | 300 | 9000 | 63000
3.2 |  | Floor trap including S.S grating floor trap, inlet outlet connection complete in all respects.
| i. | FT- with 3" P - trap | Nos. | 8 | 8000 | 64000 | 1000 | 8000 | 72000
| ii. | FT- with 4" P - trap | Nos. | 3 | 8000 | 24000 | 1000 | 3000 | 27000
3.3 |  | Cleanout for soil, waste pipes of approved make.
| i. | For 2" dia. Pipe with SS floor cover plate (FCO) | Nos. | 1 | 9000 | 9000 | 1000 | 1000 | 10000
| ii. | For 4" dia. Pipe with SS floor cover plate (FCO) | Nos. | 2 | 8750 | 17500 | 1000 | 2000 | 19500
3.4 |  | uPVC cowl for vent pipe of the following dia. including all accessories complete.
| i. | Size. 2" | No. | 1 | 1000 | 1000 | 1000 | 1000 | 2000
| ii. | Size. 3" | Nos. | 4 | 1500 | 6000 | 1000 | 4000 | 10000
|  | Sub Total Rs. |  |  |  | 461500 |  | 78000 | 539500
SECTION-04 EXTERNAL SERVICES
Supply, fixing, testing and commissioning of equipment, pipe work required to complete the sewerage disposal services in all respects with accessories ready to operate as per specifications, drawings and instructions of Consultant.
4.1 |  | C.I (Cast Iron) grating with frame for catch pit.
| i. | Size. 18" x 18" | Nos. | 17 | 21000 | 357000 | 1000 | 17000 | 374000
4.2 |  | C.I (cast Iron) grating with frame and fixing material including, excavation, base, water proof internal plaster inlet/outlet connections etc.
| i. | Size. 8" wide | Rft. | 27 | 14500 | 391500 | 500 | 13500 | 405000
4.3 |  | Construction of sump pit tank with material including, excavation, base top slab bedding, GI steps, CI cover, internal CC water proof plasters, uPVC tees, CC benching, inlet/outlet connection etc, complete in all respect.
| i. | Size 4'-0" x 4'-0" x 4'-0" water depth | Nos. | 1 | 115000 | 115000 | 35000 | 35000 | 150000
4.4 |  | Submersible pump for waste water drainage including float switch, water proof cable, ball valve, check valve with union, lifting chain.
| i. | SP-01 | Set | 1 | 492000 | 492000 | 10000 | 10000 | 502000
4.5 |  | Motor Control panel for Duplex (2 Nos.) submersible pumps including auto Lead/Lag sequencing of pumps, pump starters, auto on / off, float switches, high level alarm, power and control wiring. | Job | 1 | 215000 | 215000 | 15000 | 15000 | 230000
|  | Sub Total Rs. |  |  |  | 1570500 |  | 90500 | 1661000
SECTION-05 SUNDRIES
Contractor will priced the sundries items for all Plumbing & Sanitary (P&S) services as per specifications, drawings and instruction of consultant.
5.1 |  | Submittals, samples, shop drawings, inspections, As-Built drawings, operation and maintenance manuals and the like as required by specification. | Job. | 1 | 25000 | 25000 | 15000 | 15000 | 40000
5.2 |  | Painting, identification and tagging to the P&S installations and equipments. | Job. | 1 | 10000 | 10000 | 15000 | 15000 | 25000
5.3 |  | Testing, and commissioning entire P&S installation as per Engineer's approval. | Job. | 1 | 0 | 0 | 50000 | 50000 | 50000
|  | Sub Total Rs. |  |  |  | 35000 |  | 80000 | 115000
|  | TOTAL OF ALL SECTIONS RS. |  |  |  | 3610750 |  | 439750 | 4050500