## Sheet1
2024-05-15
MEEZAN BANK (GUJRANWALA)
SUMMARY OF BILL OF QUANTITIES
S.No | Description | Material | Labour | Amount
1 | HVAC Work | 140045430.7 | 7379433.6283 | 147424864.3283
2 | Plumbing Works |  |  | 32904220
3 | Tube Well Works |  |  | 6428022.5
| Grand Total Amount | 140045430.7 | 7379433.6283 | 186757106.8283
| Add SST 13% |  | 959326.3717 | 959326.3717
| Grand Total After SST |  |  | 187716433.2

## HVAC
MEEZAN BANK GUJRANWALA
HVAC BILL OF QUANTITIES
| Item # | Description | Unit of Measurement | Quantity | Unit Rate (PKR) |  | Amount (PKR) |  | Total
Sr. No |  |  |  |  | Cost of Supply | Cost of Installation | Cost of Supply | Cost of Installation
VARIABLE REFRIGERANT FLOW (VRF) CONDENSING UNIT
| 1 | Supply, Installation, testing and commissioning of All DC Inverter Controlled Variable Refrigerant Flow (VRF) Heat Pump T3 Type complete with built-in Auto Control System & Central Controller System with display (Tablet) for each Zone including unloading, Lifting, Placing and Fixing at foundation at locations shown on drawing
| i) | CU-1 | Each | 1 | 6461449.05 | 44247.7876 | 6461449.05 | 44247.7876 | 6505696.8376 | 39157.3342
| ii) | CU-2 | Each | 1 | 8538757.5 | 44247.7876 | 8538757.5 | 44247.7876 | 8583005.2876 | 39157.3342
| iii) | CU-3 | Each | 1 | 8169640.5 | 44247.7876 | 8169640.5 | 44247.7876 | 8213888.2876 | 39157.3342
| iv) | CU-4 | Each | 1 | 5527527.6 | 44247.7876 | 5527527.6 | 44247.7876 | 5571775.3876 | 39157.3342
| v) | CU-5 | Each | 1 | 7249923.45 | 44247.7876 | 7249923.45 | 44247.7876 | 7294171.2376 | 39157.3342
| vi) | CU-6 | Each | 1 | 6726666.45 | 44247.7876 | 6726666.45 | 44247.7876 | 6770914.2376 | 39157.3342
| vii) | CU-7 | Each | 1 | 7249923.45 | 44247.7876 | 7249923.45 | 44247.7876 | 7294171.2376 | 39157.3342
| viii) | CU-8 | Each | 1 | 5840443.35 | 44247.7876 | 5840443.35 | 44247.7876 | 5884691.1376 | 39157.3342
| ix) | CU-9 | Each | 1 | 7249923.45 | 44247.7876 | 7249923.45 | 44247.7876 | 7294171.2376 | 39157.3342
|  | VARIABLE REFRIGERANT FLOW (VRF) FAN COIL UNIT |  |  |  | 0 |  |  |  | 0
| 2 | Supply, Installation, testing & commissioning of Fan Coil Units direct expansion (D.X) connected with VRF refrigerant network, unit as per equipment schedule for air capacity & cooling total/sensible capacities. Unit shall be complete with casing, fan, motor, cooling direct expansion coil and filter section, drain pump and vent connections, fixing, wireless remote for cassette and wired thermostat for ceiling concealed, related valves, instrumentation, and fitting connections as per drawing and other data on schedule and Specification. |  |  |  | 0 |  |  |  | 0
| i) | 4-way Cassette Type Unit |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | CIU-C | Each | 1 | 471105.6 | 7079.646 | 471105.6 | 7079.646 | 478185.246 | 6265.1735
| b) | CIU-D | Each | 6 | 534543.45 | 7079.646 | 3207260.7 | 42477.8761 | 3249738.5761 | 6265.1735
| c) | CIU-E | Each | 9 | 602696.85 | 7079.646 | 5424271.65 | 63716.8142 | 5487988.4642 | 6265.1735
| d) | CIU-F | Each | 7 | 695281.65 | 7079.646 | 4866971.55 | 49557.5221 | 4916529.0721 | 6265.1735
| ii) | 2-way Cassette Type Unit |  |  | 0 | 0 | 0 | 0 | 0 | 0
| a) | CIU-Z | Each | 2 | 404697.3 | 7079.646 | 809394.6 | 14159.292 | 823553.892 | 6265.1735
| iv) | Ducted Type Unit |  |  | 0 | 0 | 0 | 0 | 0 | 0
| a) | DIU-A | Each | 10 | 274324.05 | 7079.646 | 2743240.5 | 70796.4602 | 2814036.9602 | 6265.1735
| b) | DIU-B | Each | 6 | 301842.45 | 7079.646 | 1811054.7 | 42477.8761 | 1853532.5761 | 6265.1735
| c) | DIU-C | Each | 6 | 327067.65 | 7079.646 | 1962405.9 | 42477.8761 | 2004883.7761 | 6265.1735
| d) | DIU-D | Each | 3 | 398614.65 | 7079.646 | 1195843.95 | 21238.9381 | 1217082.8881 | 6265.1735
| e) | DIU-E | Each | 17 | 398614.65 | 7079.646 | 6776449.05 | 120353.9823 | 6896803.0323 | 6265.1735
| f) | DIU-F | Each | 2 | 488509.35 | 7079.646 | 977018.7 | 14159.292 | 991177.992 | 6265.1735
| g) | DIU-G | Each | 10 | 579319.65 | 7079.646 | 5793196.5 | 70796.4602 | 5863992.9602 | 6265.1735
|  | SPLIT AC UNITS |  |  |  | 0 | 0 | 0 | 0 | 0
| 3 | Supply, installation testing & commissioning of inveter split A/C units heat & cool with 0 ODP capable to operate at high temperature 48C˚, environmental friendly gas of approved brand following capacity with latest (model/year) indoor unit, outdoor unit, Refrigerant Pipe, base plate wall mounted or ceiling hanging type, wall brackets for outdoor unit rawal plug, suitable length of control cable and etc. complete in all respect as shown on drawings and specified. |  |  |  | 0 | 0 | 0 | 0 | 0
| i) | Wall Mounted Unit |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | SAC-1 TR | Each | 4 | 269000 | 5309.7345 | 1076000 | 21238.9381 | 1097238.9381 | 4698.8801
| b) | SAC-2 TR | Each | 4 | 416000 | 5309.7345 | 1664000 | 21238.9381 | 1685238.9381 | 4698.8801
|  | REFRIGERANT PIPING FOR VRF SYSTEM |  |  |  | 0 | 0 | 0 | 0 | 0
| 4 | Supply and Installation of Gas & Liquid Copper Piping of Type-L ASTM B-280 & Fittings Complete with Elastomeric Closed Cell Foam insulation of density 40-55 Kg/m3 with factory applied fiberglass aluminum embossed jacketing, control wiring between Indoor Units & Outdoor Unit, clamps/hangers/supports, covered cable tray for outdoor piping and all other related material for installation purpose complete in all respect as specified. | Lot | 1 | 15200000 | 1637168.1416 | 15200000 | 1637168.1416 | 16837168.1416 | 1448821.3642
|  | Note: The Refrigerant pipe sizes and route as shown in drawing are indicative only. The equipment supplier/ Contractor is responsible to verify the pipe sizing detail as given in drawings attached in accordance with their selected models of equipment being offered. The copper piping shall be nitrogen pressure tested and shall be made vacuum, the refrigerant piping shall run in 22 gauge GI trunking provided outside the building, the refrigerant piping shall be complete in all respects as per drawings, specifications and as approved by the Consultant. |  |  |  | 0 | 0 | 0 | 0 | 0
|  | REFRIGERANT PIPING FOR SPLIT SYSTEM |  |  |  | 0 | 0 | 0 | 0 | 0
| 5 | Supply, installation and testing of Gas & Liquid Copper Piping & Fittings (22 Gauge) Complete with 19mm thick O type Closed Cell Foam insulation of 40-55 Kg/m3 density, control wiring between Indoor Units & Outdoor Unit, duly wrapped with weather proof tape clamps/hangers/ supports and all other related material for installation purpose complete in all respect as specified. |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | 1 TR | Rft | 125 | 2000 | 353.9823 | 250000 | 44247.7876 | 294247.7876 | 313.2587
| b) | 2 TR | Rft | 75 | 2600 | 398.2301 | 195000 | 29867.2566 | 224867.2566 | 352.416
|  | CONDENSATE DRAIN PIPE |  |  |  | 0 | 0 | 0 | 0 | 0
| 6 | Supply and installation of E-Class UPVC piping & fittings along with 1/4" thick polyethylene insulation (Jumbolon) covered with PVC taping for condensate drain piping, including hangers, anchor bolts, rubber vibration mounts etc. |  |  |  | 0 | 0 | 0 | 0 | 0
| i) | Embedded in Ground & Wall |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | 1" | Rft | 350 | 300 | 88.4956 | 105000 | 30973.4513 | 135973.4513 | 78.3147
| ii) | Above Ceiling |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | 1" | Rft | 1195 | 415 | 70.7965 | 495925 | 84601.7699 | 580526.7699 | 62.6517
| b) | 1 1/4" | Rft | 250 | 475 | 88.4956 | 118750 | 22123.8938 | 140873.8938 | 78.3147
| c) | 1 1/2" | Rft | 275 | 515 | 88.4956 | 141625 | 24336.2832 | 165961.2832 | 78.3147
|  | Y JOINTS |  |  |  | 0 | 0 | 0 | 0 | 0
| 7 | Suppy and Installation of Y Joints with all fittings complete in all respect for Refrigerant pipes. | Lot | 1 | 1150000 | 44247.7876 | 1150000 | 44247.7876 | 1194247.7876 | 39157.3342
|  | VENTILATION FANS |  |  |  | 0 | 0 | 0 | 0 | 0
| 8 | Supply, installation testing & commissioning of following type of exhaust/supply fans with hanger, supports, nut bolts, sound attenuators (so the noise level should not exceed from 60 dBA at full load). including electrical connections, safety devices, motor starter if required as recommended by the manufacturer. Complete in all respects as shown on drawings and as per the equipment schedule. IP55, F Class, IE2 Motor for upto 2hp Motors, IE3 Motor for greater than 2hp. |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | EAF-01 | Each | 1 | 112500 | 7079.646 | 112500 | 7079.646 | 119579.646 | 6265.1735
| b) | EAF-02 | Each | 1 | 121250 | 7079.646 | 121250 | 7079.646 | 128329.646 | 6265.1735
| c) | EAF-03 | Each | 1 | 183500 | 7079.646 | 183500 | 7079.646 | 190579.646 | 6265.1735
| d) | EAF-04 | Each | 2 | 243650 | 8849.5575 | 487300 | 17699.115 | 504999.115 | 7831.4668
| e) | EAF-05 | Each | 1 | 862000 | 8849.5575 | 862000 | 8849.5575 | 870849.5575 | 7831.4668
| f) | FAF-01 | Each | 4 | 121250 | 8849.5575 | 485000 | 35398.2301 | 520398.2301 | 7831.4668
| g) | FAF-02 | Each | 1 | 121250 | 8849.5575 | 121250 | 8849.5575 | 130099.5575 | 7831.4668
| h) | FAF-03 | Each | 2 | 211500 | 8849.5575 | 423000 | 17699.115 | 440699.115 | 7831.4668
|  | DUCT WORK |  |  |  | 0 | 0 | 0 | 0 | 0
| 9 | Supply, fabrication and installation as per specifications and as shown on drawings Galvanized Iron Sheet-metal (of Grade G-60 & zinc Coating of Class Z-180) work including all bends, tees, connection to grilles, volume control dampers, splitter dampers, access doors, hangers, supports, rods and wooden frames (for ducts crossing walls). All duct work shall be constructed comply to SMACNA standards and all accessories necessary to complete the work. |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | U.S GAGE 26 | Per Sft | 2509.5 | 425 | 70.7965 | 1066537.5 | 177663.7168 | 1244201.2168 | 62.6517
| b) | U.S GAGE 24 | Per Sft | 14285 | 480 | 70.7965 | 6856800 | 1011327.4336 | 7868127.4336 | 62.6517
| c) | U.S GAGE 22 | Per Sft | 2200 | 525 | 70.7965 | 1155000 | 155752.2124 | 1310752.2124 | 62.6517
| d) | 10'' Dia Inulated Flexible duct | Per Rft | 300 | 800 | 176.9912 | 240000 | 53097.3451 | 293097.3451 | 156.6293
| e) | VCD (Volume Control Damper) | Per Sft | 93 | 5050 | 265.4867 | 469650 | 24690.2655 | 494340.2655 | 234.944
| f) | Flexible Duct Connector (6'' wide) | Per Rft | 250 | 700 | 88.4956 | 175000 | 22123.8938 | 197123.8938 | 78.3147
| 10 | Supply & installation of 1" thick fiber glass blanket insulation for supply and return duct of density 24kg/m3, having factory applied Aluminum foil facing protected with 8oz canvas cloth complete with adhesives, sealers and protections | Per Sft | 8915 | 125 | 44.2478 | 1114375 | 394469.0265 | 1508844.0265 | 39.1573
| 11 | Supply & installation of 1"thick bonded fiber glass Blanket sound liner (Acoustic Liner) having density of 24 kg/m3 with NRC (Noise Reduction Coefficient of 0.6) inducts, fire retardant type with 100% surface applied with adhesive as well as mechanical fasteners (Gripnails) complete in all respect as aprroved and directed by Engineer Incharge. | Per Sft | 350 | 125 | 44.2478 | 43750 | 15486.7257 | 59236.7257 | 39.1573
| 12 | Supply & installation of 2" thick washable aluminum filter installed in Fresh air supply ducts fabricated with min. 12 mesh layers | Per Sft | 8.5 | 3000 | 265.4867 | 25500 | 2256.6372 | 27756.6372 | 234.944
|  | AIR DEVICES |  |  |  | 0 | 0 | 0 | 0 | 0
| 13 | Supply, installation and testing of air inlet/outlet devices including fittings, fixing with all necessary items to complete the work complete in all respects as shown on drawings. |  |  |  | 0 | 0 | 0 | 0 | 0
| i) | Supply/Return/Fresh Air Register |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | Single Deflection type (Extruded Aluminum ) | Sqft | 22.5 | 4300 | 442.4779 | 96750 | 9955.7522 | 106705.7522 | 391.5733
| ii) | Fresh/Exhuast air Louver insect screen |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | Extruded Aluminum | Sqft | 21 | 4500 | 442.4779 | 94500 | 9292.0354 | 103792.0354 | 391.5733
| iii) | Supply/Return/Fresh Air Diffuser |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | 4-Way Square (Extruded Aluminum ) | Sqft | 35 | 5000 | 442.4779 | 175000 | 15486.7257 | 190486.7257 | 391.5733
| iv) | Supply/Return/Fresh Air Diffuser |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | Round 14'' Dia (Extruded Aluminum ) | Each | 20 | 9000 | 884.9558 | 180000 | 17699.115 | 197699.115 | 783.1467
| v) | Linear Slot Diffuser |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | 3 Slot 3/4''x6''xLength as per drawing | Per Rft | 950 | 1600 | 88.4956 | 1520000 | 84070.7965 | 1604070.7965 | 78.3147
| vi) | Side wall Linear Slot Diffuser |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | 3 Slot 3/4''x6''xLength as per drawing | Per Rft | 40 | 1600 | 88.4956 | 64000 | 3539.823 | 67539.823 | 78.3147
| vii) | WireMesh |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | Galvanized Iron | Sqft | 27 | 2000 | 176.9912 | 54000 | 4778.7611 | 58778.7611 | 156.6293
|  | AIR CURTAIN |  |  |  | 0 | 0 | 0 | 0 | 0
| 14 | Supply, Installation, testing and commissioning of air curtain (remote control operated), along with all fitting, connections, control, stand for hanging etc. complete in all respects ready to operate as per drawings and as per instruction of Engineer. ''10ft throw'' |  |  |  | 0 | 0 | 0 | 0 | 0
| a) | 1500mm | Each | 2 | 125000 | 2654.8673 | 250000 | 5309.7345 | 255309.7345 | 2349.4401
| 15 | Supply & Installation of all type of Electrical Control wiring from outdoor to indoor units and from thermostats to indoor units or as required as per site complete in all respects. | Job | 1 | 1990000 | 265486.7257 | 1990000 | 265486.7257 | 2255486.7257 | 234944.005
| 16 | Supply & Installation of all type of M.C.C. AND A.C.Ps complete in all respect. | Lot | 1 | 1780000 | 88495.5752 | 1780000 | 88495.5752 | 1868495.5752 | 78314.6683
| 17 | Air Balancing, Shop drawings and As-built drawings. | Job | 1 | 0 | 176991.1504 | 0 | 176991.1504 | 176991.1504 | 156629.3367
| 18 | Opening / dismantling of brick masonry walls for HVAC duct and repair of wall, plastering, and paint complete same as before dismantling as per instruction of the engineer in charge. | Job | 1 | 0 | 132743.3628 | 0 | 132743.3628 | 132743.3628 | 117472.0025
| 19 | Construction of RCC Pad for HVAC equipment i-e Condensing Units Etc. work complete per instruction of the engineer in charge. | Job | 1 | 450000 | 88495.5752 | 450000 | 88495.5752 | 538495.5752 | 78314.6683
| 20 | Operation & Maintenance period for one year after issuing completion certificate on monthly basis as specified | Months | 12 | 0 | 132743.3628 | 0 | 1592920.354 | 1592920.354 | 117472.0025
SUB TOTAL SECTION = 02 | TOTAL AMOUNT (PKR.) | [5 empty] | 140045430.7 | 7379433.6283 | 147424864.3283
Notes:
| 1 | Prices should be inclusive of all applicable taxes and duties.
| 2 | Payment will be paid on actual quantities after verification and as per quoted unit rates.
| 3 | The Bidder shall provide the Technical Literature for approval of Consultant
| 4 | The Bidder shall specify the Country of Origin of the Quoted Items.
| 5 | The Bidder shall be fully responsible to complete the Works for the completion and operation of all systems and shall include price of all such items of systems and equipment or work, whether mentioned in the BOQ, which are required to make the systems operationally complete in all respects. Also include price, at this stage, as foreseen by Bidder as per his Detailed Engineering / Site Works / Commissioning etc.

## Plumbing
MEEZAN BANK LIMITED MAKKAH TOWER, GUJRANWALA
BILL OF QUANTITIES
PLUMBING & FIREFIGHTING SYSTEMS
Sr. No. | Description | Unit | Qty | Unit Rate (Rs.) | Amount (Rs.)
Part-1: PLUMBING FIXTURES
INDIAN W.C
1.1 | Providing and fixing Indian W.C ceramics ware including muslim shower, tee stop cock, double bibcock with flushing cistern of best quality including hockey pipe. Fixing connection pipes and all joints to services and drains. Plugging and screwing the structure as necessary and make good the same, complete in all respect as per specifications and drawings as well as directed by the Engineer. | Nos. | 3 | 52000 | 156000
EUROPEAN W.C
1.2 | Providing and fixing European W.C ceramics ware including muslim shower, tee stop cock with double bibcock, flushing cistern with hinged double seat and cover of best quality. Fixing connection pipes and all joints to services and drains. Plugging and screwing the structure as necessary and make good the same, complete in all respect as per specifications and drawings as well as directed by the Engineer.
Items Included
European type W.C With Seat Cover.
W.C Thimble
Muslim Shower
Double Bibcock
| Tee Stop Cock | Nos. | 27 | 88500 | 2389500
CORE CUTTING
1.3 | Cutting of R.C.C slab via core cutter of suitable diameter by using proper technique and equipment for the crossing of utility pipes and its water proof refilling with useful materials complete in all respect as per specifications and drawings as well as directed by the Engineer. | Nos. | 42 | 2000 | 84000
WASH HAND BASIN VANITY
1.4 | Providing and fixing wash hand basin vanity Under counter including basin mixer with waste coupling & bottle trap and fixing connection pipes, connections to water lines, nuts, washers, etc. complete in all respect as per specifications and drawings as well as directed by the Engineer.
Items Included
Wash Hand Basin Vanity.
Basin Mixer
Bottle Trap
Waste Coupling
| Tee Stop Cock | Nos. | 36 | 68000 | 2448000
KITCHEN SINK
1.5 | Providing and fixing kitchen sink with mixer, waste coupling and tee stop cock including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer.
Items Included
Kitchen Sink
Kitchen Sink Mixer
Waste Coupling
| Tee Stop Cock | Nos. | 5 | 110250 | 551250
SOAP DISPENSER
1.6 | Providing and fixing soap dispenser including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer.
Items Included
| Soap Dispenser | Nos. | 16 | 9100 | 145600
TOILET PAPER HOLDER
1.7 | Providing and fixing chromium plated toilet paper holder including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer.
Items Included
| Toilet Paper Holder | Nos. | 30 | 6250 | 187500
HAND DRYER
1.8 | Providing and fixing electrical hand dryer with automatic sensor having fastest drying time of 12 seconds, temperature of 104 Fahrenheit. hand dryer must have noise Level of 81dB and automatic shut off including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer.
Items Included
| Hand Dryer | Nos. | 9 | 24500 | 220500
LOOKING GLASS
1.9 | Providing and fixing looking glass 5mm thick first quality complete with fixing clamps including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer.
Items Included
Looking Glass
| Looking Glass Clamp | Sft. | 216 | 2700 | 583200
TOWEL ROD
2 | Providing and fixing towel rod including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer.
Items Included
| Towel Rod | Nos. | 8 | 9500 | 76000
TAP
1.1 | Providing and fixing tap 3/4 inch dia including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer.
Items Included
| Tap 3/4 inch dia | Nos. | 25 | 9900 | 247500
Total Amount (Rs.) Part - 1
Part-2: INTERNAL WATER SUPPLY SYSTEM
2.1 | Providing, fixing, jointing and testing Polypropylene Random (PPR) PN16 pressure pipe for cold, hot and hot water return water as per DIN 8077-8078 for pipes and DIN 16962,PN20 for fittings (polyfusion welded joints) inside building including fittings and specials (sockets, tees, elbows, bends, crosses, reducers, adaptor, plugs and union etc.) supported on walls or suspended from roof slab or run in chases including pipe hangers, supports, walls cutting for pipelines, complete in all respect as per specifications and drawings as well as directed by the Engineer.
| 25 mm dia | Rft. | 880 | 350 | 308000
| 32 mm dia | Rft. | 374 | 525 | 196350
| 40 mm dia | Rft. | 207 | 750 | 155250
| 50 mm dia | Rft. | 55 | 1100 | 60500
| 75 mm dia | Rft. | 208 | 1980 | 411840
GATE / BALL VALVE
2.2 | Providing and installing gate/ball valves of following nominal dia, of approved equivalent make ,including jointing ,fitting, painting, testing, complete in all respects to match with following PPR pipe diameters.
| 25 mm dia | Each | 8 | 11500 | 92000
| 32 mm dia | Each | 10 | 14600 | 146000
| 40 mm dia | Each | 11 | 16250 | 178750
| 75 mm dia | Each | 4 | 65000 | 260000
Total Amount (Rs.) Part - 2
Part-3: INTERNAL SEWERAGE , VENTS & ROOF DRAINAGE
3.1 | Providing, fixing, jointing and testing uPVC pipe including all fittings such as tees, bends and reducers. Also it includes the cost of joint solutions & clamping to walls, ceiling hangers, supports, cutting through walls for pipelines and pipe fittings of the following diameters, complete in all respect as per specifications and drawings as well as directed by the Engineer.
BSEN 1329
| 50 mm dia | Rft. | 308 | 550 | 169400
| 75 mm dia | Rft. | 48 | 900 | 43200
| 100 mm dia | Rft. | 1256 | 1450 | 1821200
| 200 mm dia | Rft. | 225 | 3150 | 708750
CLASS :D: BS 3505/PS 3051 (For Pressure Pipe)
| 2 inch dia pipe | Rft. | 130 | 700 | 91000
FLOOR DRAIN
3.2 | Providing and fixing 4" dia Floor Drain with P-trap including Stainless Steel grating and cover of approved make including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer. | Nos. | 22 | 8500 | 187000
CLEAN-OUT
3.3 | Providing and fixing 4" dia Clean-out for uPVC Pipes including Stainless Steel Cover Plate of approved make, core cutting of Slab concrete and its water proofed refilling as approved by Engineer In charge and complete in all respect. | Nos. | 8 | 8500 | 68000
Total Amount (Rs.) Part - 3.
Part-4: FIRE FIGHTING SYSTEM
4.1 | Providing and fixing Mild Steel Schedule 40 Seamless Pipes including all fittings such as tees, bends and reducers with cost of clamping to walls and ceiling hangers, supports, cutting through walls and concrete in slabs with core cutter for pipelines and pipe fittings of the following diameters complete in all respect.
| 2-1/2" dia (63mm) | Rft. | 576 | 2150 | 1238400
| 4" dia (100mm) | Rft. | 612 | 3950 | 2417400
GATE / BALL VALVE
4.2 | Providing and installing gate/ball valves of following nominal dia, of approved make, including jointing, fitting, painting, testing, complete in all respects to match with following pipe dia meters.
| 2-1/2" dia (63mm) | Nos. | 12 | 92300 | 1107600
LANDING VALVE
4.3 | Providing, Installing, testing and commissioning Landing valves in Stair hall on intermediate landings with reducing tee of size 4"x2-1/2" as required by NFPA codes for including jointing, fitting, testing, including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer. | Nos. | 7 | 67000 | 469000
HOSE REEL CABINET
4.4 | Providing, Installing, testing and commission fire hose reel cabinets, swing type hose reel in cabinet, Dia 1" x 100' long, swing type with imported high pressure PE pipe house, and imported jet/spray/shut nozzle, in steel cabinet (34" x 32" x 10.5") where indicated on drawings including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer. | Nos. | 12 | 175000 | 2100000
ALARM CHECK ASSEMBLY
4.5 | Installing and fixing Alarm Check Valve Wt type 4" Flanged End Complete set with Basic trim, Pressure switch, Retard chamber and water motor alarm Gong, UL Listed and FM Approved | Nos. | 1 | 482500 | 482500
PILLAR TYPE FIRE HYDRANT
4.6 | Providing, Installing, testing and commissiong Pillar type fire hydrants with inlet flanged 4" size with double deliveries 2 1/2" female instantaneous coupling with blank cap and chain, including all necessary accessories required for installation, complete in all respect as per specifications and drawings as well as directed by the Engineer. | Nos. | 2 | 210250 | 420500
BREACHING INLET
4.7 | Providing, Installation, testing and commissioning of Interconnection with Municipal Fire Brigade (Siamese connection), consisting of breach inlet valve and casing, flang 4" dia, complete in all respect as per specifications and drawings as well as directed by the Engineer. | Nos. | 1 | 99000 | 99000
Total Amount (Rs.) Part - 4.
Part-5: MISCELLANEOUS
UNDERGROUND WATER TANK
5.1 | Providing, placing sleeves and puddle flange in R.C.C. under ground water tank walls, pipe connection (G.I) with inlet / outlet pipe work, manhole covers, floating ball valve etc, including all necessary accessories required for sleeces placing, complete in all respects. | Job | 1 | 85000 | 85000
OVERHEAD WATER TANK
5.2 | Providing, placing sleeves and puddle flange in R.C.C. over head water tank walls, pipe connection (G.I) with inlet / outlet pipe work, manhole covers, floating ball valve etc, including all necessary accessories required for sleeves placing, complete in all respects. | Job | 1 | 45000 | 45000
SEPTIC TANK
5.3 | Providing, placing sleeves and puddle flange in R.C.C. over head water tank walls, pipe connection (G.I) with inlet / outlet pipe work, manhole covers, floating ball valve etc, including all necessary accessories required for sleeves placing, complete in all respects. | Job | 1 | 45000 | 45000
STORAGE GEYSER
5.4 | Providing, installing, testing and commission of storage type electric geyser of approved make 25 Liters capacity complete with inlet, outlet, safety valves complete in all respects. | Nos. | 14 | 95000 | 1330000
Total Amount (Rs.) Part - 5.
Part-6: GI PIPES
6.1 | Providing, fixing, jointing and testing G.I pipes and fittings inside building including fittings and specials (sockets, tees, elbows, bends, crosses, reducers, adaptor, plugs and union etc.) supported on walls or suspended from roof slab or run in chases including pipe hangers, supports, walls cutting and core cutter for cutting of concrete slab with sealing and water proofing with epoxy grouting for pipelines complete in all respects.
| 1-1/2 inch dia | Rft | 165 | 1450 | 239250
| 2 inch dia | Rft | 12 | 1700 | 20400
| 2-1/2 inch dia | Rft | 126 | 1980 | 249480
| 3 inch dia | Rft | 290 | 2450 | 710500
GATE / BALL VALVE
6.2 | Providing and installing gate/ball valves of following nominal dia, of approved make ,including jointing ,fitting, painting, testing, complete in all respects to match with following G.I pipe diameters.
| 1-1/2 inch dia | Nos. | 4 | 18500 | 74000
| 2 inch dia | Nos. | 1 | 28900 | 28900
| 2-1/2 inch dia | Nos. | 7 | 42500 | 297500
| 3 inch dia | Nos. | 1 | 68000 | 68000
Total Amount (Rs.) Part - 6.
Part-07:- PLUMBING EQUIPMENT
FIRE FIGHTING PUMP SET
7.1 | Providing, Fixing ,testing & installing pump set for fire fighting of following capacities. Pump set shall be Standard Firefighting Pump:
a) Horizontal centrifugal pump set (50Hz x 380V, 3 phase Motor) 350 GPM @ 5 bar complete with automatic control panel , Pressure switch & Pressure gauge. It should be capable of operating 1 remotest 21/2" hydrants 200 GPM each @ min. 4.5 bar pressure
b) Horizontal centrifugal engine driven pump set 350 GPM @ 5 bar complete with automatic control panel , Pressure switch, Pressure gauge & diesel tank. It should be capable of operating 1 remotest 21/2" hydrants 200 GPM each @ min. 4.5 bar pressure
c) Jockey electric motor driven pump set (50Hz x 380 V ,3Ph Motor) 25 GPM @ 5.5 bar complete with automatic control panel, pressure switch and pressure gauge.
d) Pump control cabinet for above mentioned pump.
| e) Pump room's fitting and controls i.e. gate valves, NRV, expansion joints, headers, pressure reducing/ relief valve, test return line to reservoir, supports and painting. | Set | 1 | 6550500 | 6550500
WATER TRANSFER PUMP
7.2 | Providing, Installing, fixing, testing and commission, centrifugal pumps of make KSB, Grundfos or approved equivalent (2 Nos. - 1 running + 1 standby) of capacity 75 gpm each with stainless steel impeller capable of pumping against a total pumping head of 110 ft. coupled with water cooled electric motor of , 440 volts, 3 - phase, 50 Hz. The pump shall be provided with control panel having auto / manual switches, dry running protection, low / high level water controls with alternative standby duty operation system, complete in all respects. | Set. | 1 | 1440000 | 1440000
SUMP PUMP
7.3 | Providing, Installing, testing and commissioning non-clogging, centrifugal submersible Drainage pumps 30 gpm against a total pumping head of 35 ft (one running one standby). coupled with water cooled IP Class 68 electric motor of 2 HP, 400 volts, 3 - phase, 50 Hz. of approved make with auto / manual switches, dry running protection, low / high level water controls, gate valves, NRV, flexible Joints, Strainer, with alternative standby duty operation system),All accesorries/consumables to be provided by contractor. | Set. | 1 | 750000 | 750000
WATER SUPPLY BOOSTER (MINI)
7.4 | Supply, Installing, fixing, testing and commissioning of Water Pressure Booster Pump (1 working + 1 standby) with a capacity of 25 USGPM against a total head of 40 feet. The pump shall be provided with control panel having auto / manual switches, dry running protection, low / high level water controls with alternative standby duty operation system, complete in all respects. | Set | 1 | 650000 | 650000 | `
Total Amount (Rs.) Part - 7.
SUMMARY
Sub-Total (Plumbing Fixtures)
Sub-Total (Internal Water Supply)
Sub-Total (Internal Sewerage, Vents & Roof Drainage)
Sub-Total (Fire Fighting System)
Sub-Total (Miscellaneous)
Sub-Total (GI Pipes)
Sub-Total (Plumbing Equipment)
Sub-Total ( 0.25 Cusec Tube Well)
| Grand Total |  |  |  | 32904220
Note:
It should be clearly understood by the contractor / bidder that the above mentioned items shall be complete in all respects, including cost of all necessary materials / accessories whether mentioned or not but are required for proper functioning of the system shall be deemed to be included in the cost of each above mentioned items, no extra charge shall be paid or claimed by the contractor / bidder.

## Tube well
MEEZAN BANK LIMITED MAKKAH TOWER, GUJRANWALA
BILL OF QUANTITIES
DRILLING AND INSTALLATION OF 0.25 CUSEC TUBE WELL
Sr. No. | Description | Unit. | Qty | Rate(Rs) | Amount (Rs.)
1 | Mobilization Demobilization of drilling equipment, materials and crew. | Job | 1 | 50000 | 50000
2 | SITE PREPARATION
| Excavation of drilling Pit and Supply well. | Job | 1 | 400000 | 400000
3 | TUBEWELL BORING
Drilling of bore dia 16" (408 mm) i/d for tubewell in all type of soils except shingle and rock.
| From ground level to 100 ft depth. | Rft | 100 | 650 | 65000
| From 100 ft to 200 ft depth | Rft | 100 | 700 | 70000
| From 200 ft to 300 ft depth | Rft | 100 | 750 | 75000
| From 300 ft to 400 ft depth | Rft | 100 | 800 | 80000
| From 400 ft to 500 ft depth | Rft | 100 | 850 | 85000
| From 500 ft to 600 ft depth | Rft | 100 | 900 | 90000
| From 600 ft to 700 ft depth | Rft | 100 | 950 | 95000
4 | TUBEWELL MATERIALS
4.1 | Housing
| Supply and installation of Fiberglass, Dia: 8", wall thickness: 6mm, including welding etc. | Rft | 220 | 3010.5 | 662310
4.2 | Strainer
Providing and installing Fiberglass Reinforced Polypropelene (FRP) strainer of specifid wall thickness having slot size of 0.9 mm to 1.10 mm in Tubewell borehole i/c the cost of male/female coupling with Nylone Strip,studs complete in all respect as approved and directed by the Engineer Incharge.
| 6" inch dia (5 mm thickness) | Rft | 90 | 2524.5 | 227205
4.3 | Blind Pipe
| Supply & installing fiberglass pipes, Dia:6", wall thickness: 5mm, including nylon sticks etc. | Rft | 380 | 2430 | 923400
4.4 | Bail Plug
| Supply and installing of fiberglass bail plug, Dia:6", wall thickness: 5mm, Slot Size: 1mm, including nylon sticks etc. | Rft | 10 | 2430 | 24300
4.5 | Reducer
| Supply and installation of MS Reducer Dia: 8"/6", Wall thickness: 6mm, including welding etc | Each | 1 | 22950 | 22950
4.6 | Pea Gravels (Shrouding)
| Supply of Pea Gravels of gradation appropriate to 1 mm slot size from Attock quarry, including sieving, washing and lowering in the annular space of the borehole | Cft | 865 | 310.5 | 268582.5
4.7 | GI Pipe
| Providing, fixing, cutting, jointing and testing 2 inch dia GI medium gauge piping for pea gravels (Shrouding) including GI fittings with welding, complete in all respects. | Rft | 100 | 742.5 | 74250
5 | M.S PLATE
| Providing and fixing, M.S bore cover plate 2'-6'' x 2'-6'' including paint complete in all respect | Kgs | 120 |  | 56700
6 | AIR VALVE
Providing and fixing, air valve 2½ (65mm) dia of B.S.S.quality and weight (complete with jointing material).
| 2 1/2 inch dia | No. | 1 | 33750 | 33750
7 | GATE VALVE
Providing and fixing, Cast Iron flanged Gate Valve (B.S. 5163) quality and weight with jointing material complete in all respect and directed by the Engineer-in-charge:-
| 4 inch dia | No. | 1 | 81000 | 81000
8 | NON-RETURN VALVE/ CHECK VALVE
Providing and fixing, Cast Iron flanged Non Return Valve (B.S. 5153) quality and weight with jointing material complete in all respect and directed by the Engineer-in-charge:-
| 4 inch dia | No. | 1 | 87750 | 87750
9 | FLOW METER
| Providing and fixing, analog and recordable flow meter / water meter complete in all respect and directed by the Engineer-in-charge. | No. | 1 | 60750 | 60750
10 | PRESSURE GUAGE
| Providing and installing Pressure guages made up of stainless steel body having pressure of 0-16 bars. | No. | 1 | 16200 | 16200
11 | SOIL SAMPLING
| Taking soil samples at every 5 ft interval or at change of strata, which ever is less, Sieve analyses. | Job | 140 | 0 | 25650
12 | ELECTRICAL LOGGING
| Electrical Logging for analysing water quality and tubewell designing | Job | 1 | 65475 | 65475
13 | DEVELOPMENT
| Development of tubewell for 24 - 48 hrs till pumped water is sand free and the formation around well has stabilized to the satisfaction of Engineer | Job | 1 | 81000 | 81000
14 | CONCRETE BLOCK
| Construction of cement concrete block RCC ratio 1:2:4 around house pipe, complete in all respect . | Job | 1 | 74250 | 74250
15 | PUMPING MACHINERY
Submersible Pump with Submersible Motor)
PUMP PARAMETERS AND SCOPE OF SUPPLY
| Discharge: 0.25 Cusec | Set | 1 | 2632500 | 2632500
Head: 330ft
Pump Setting: 230ft
Pump Type: Deep Well Submersible Pump KSB or Grundfoss OR Approved Equivalent Submersible Pumps.
Motor Submersible Motor,
Colum Pipe: ERW,
Bowl Assembly: Impellors: SS , Bowls: SS, Shaft SS
MCU with all protection devices, such as over/under current relay, starting method Y/D of metallic box magnetic contactor, circuit breakers on/off switch controle wire under and over voltage protection relay and indication lamps. Ampere and volt meters for each phase, emergency stop button, Suitable size submerssible cable from MCU to motor, complete in all respect as per satisfaction of the engineer in charge.
Accessories: Gate Valve, Non Return Valve, Set of Lowering Clamp, Top Plate, Discharge Bend etc
|  |  | Total Amount Rs. : |  | 6428022.5
NOTE:
After the selection of contractor and before the start of drilling process the contractor must provide shop drawings to the consultant for approval.